## Sheet1
Date | Production Unit I (MWh) | Production Unit II (MWh) | Total HPP | Auxiliaries Consumptions Unit I (MWh) | Auxiliaries Consumptions Unit II (MWh) | Auxiliaries Consumptions Grid (MWh) | Net Production (MWh) | Peak (MW) | Hours of Operation Unit I | Hours of Operation Unit II | Unit I Maintenance Plant | Unit I Maintenance Outside | Unit I Failure Plant | Unit I Failure Outside | Unit II Maintenance Plant | Unit II Maintenance Outside | Unit II Failure Plant | Unit II Failure Outside | Number of Starts Unit I | Number of Starts Unit II | Comments | Date | Asomata Reservoir Water Level (m) | Asomata Reservoir Water Content (m3 x 1000) | Regulating lake Water Level (m) | Regulating lake Water Content (m3 x 1000) | Water saved in lake | Catchment water inflow | Production Water Consumption (m3 x 1000) | Specific Consumption | Turbine Efficiency | HPP Sfikia Water Production (m3 x 1000) | HPP Sfikia Water Pumped upstream (m3 x 1000) | Lake natural inflow (m3 x 1000) | Losses (m3 x 1000) | B | Regulating lake Water flow (m3/s) | Regulating lake Total Water (m3 x 1000) | Year | Month | SourceFile
1 | 590 | 160 | 750 | 0 | 0 | 5 | 745 | 105 | 13.19999999999709 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.55 | 8120 | 42.001 | 3803.6699999999937 | -600 | 10024.340425531915 | 7752 | 10.336 | 83.44080720914751 | 9840.4 | 2872.3404255319147 | 243.94042553191503 | 60 |  | 89.72222222222223 | 7752 | 2014 | 1 | 2014_01_Asomata_english.xlsx
2 | 600 | 0 | 600 | 0 | 0 | 5 | 595 | 55 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.5 | 8000.000000000007 | 41.151 | 2809.17 | -119.99999999999272 | 7780.425531914901 | 6060 | 10.1 | 85.49097262667443 | 7784 | 1840.4255319148936 | 56.4255319149006 | 60 |  | 70.13888888888889 | 6060 | 2014 | 1 | 2014_01_Asomata_english.xlsx
3 | 235 | 0 | 235 | 0 | 0 | 4 | 231 | 54 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.6 | 8239.999999999993 | 40.865 | 2474.55 | 239.99999999998545 | 2754.4999999999854 | 2514.5 | 10.7 | 80.50765653108684 | 2628 | 0 | 156.49999999998545 | 30 |  | 29.10300925925926 | 2514.5 | 2014 | 1 | 2014_01_Asomata_english.xlsx
4 | 355 | 0 | 355 | 0 | 0 | 5 | 350 | 54 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 83.55 | 5720 | 41.3 | 2983.5 | -2519.9999999999927 | 3465.1929787234117 | 3628.81 | 10.222 | 86.40197248048793 | 3268.8 | 2356.3829787234044 | 256.3929787234115 | 60 |  | 42.00011574074074 | 3628.81 | 2014 | 1 | 2014_01_Asomata_english.xlsx
5 | 195 | 0 | 195 | 0 | 0 | 5 | 190 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 83.6 | 5839.999999999993 | 40.452 | 1991.34 | 119.99999999999272 | 2206.4999999999927 | 2086.5 | 10.7 | 82.44293673616106 | 2275.2 | 0 | 81.29999999999245 | 150 |  | 24.149305555555557 | 2086.5 | 2014 | 1 | 2014_01_Asomata_english.xlsx
6 | 145 | 0 | 145 | 0 | 0 | 0 | 145 | 40 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 83.65 | 5960.00000000002 | 40.6725 | 2249.325 | 120.00000000002728 | 1657.0000000000273 | 1537 | 10.6 | 83.12079548800651 | 1470 | 0 | 187.00000000002728 | 0 |  | 17.78935185185185 | 1537 | 2014 | 1 | 2014_01_Asomata_english.xlsx
7 | 270 | 0 | 270 | 0 | 0 | 5 | 265 | 54 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 83.7 | 6080.000000000014 | 41.1015 | 2751.2550000000065 | 119.99999999999363 | 2900.9999999999936 | 2781 | 10.3 | 85.43922143838327 | 2686.4 | 0 | 214.59999999999354 | 0 |  | 32.1875 | 2781 | 2014 | 1 | 2014_01_Asomata_english.xlsx
8 | 285 | 0 | 285 | 0 | 0 | 6 | 279 | 54 | 5.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.7 | 8480.000000000015 | 40.76 | 2351.7 | 2400 | 5178.75 | 2778.75 | 9.75 | 88.1450789647511 | 4819.5 | 0 | 359.2500000000009 | 0 |  | 32.161458333333336 | 2778.75 | 2014 | 1 | 2014_01_Asomata_english.xlsx
9 | 205 | 0 | 205 | 0 | 0 | 7 | 198 | 55 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.4 | 7760.00000000002 | 40.858 | 2466.36 | -719.9999999999945 | 3316.182432432438 | 2203.75 | 10.75 | 80.51118911803421 | 3218.4 | 1832.4324324324325 | 197.78243243243742 | 100 |  | 25.50636574074074 | 2203.75 | 2014 | 1 | 2014_01_Asomata_english.xlsx
10 | 180 | 0 | 180 | 0 | 0 | 5 | 175 | 55 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84 | 6800.000000000007 | 40.85 | 2457 | -960.0000000000127 | 3355.531914893604 | 1890 | 10.5 | 83.21315192743764 | 3322.6 | 2425.531914893617 | 32.931914893604244 | 0 |  | 21.875 | 1890 | 2014 | 1 | 2014_01_Asomata_english.xlsx
11 | 85 | 0 | 85 | 0 | 0 | 5 | 80 | 55 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.55 | 5720 | 40.93 | 2550.6 | -1080.0000000000073 | 2225.228723404248 | 922.25 | 10.85 | 81.40101038668642 | 2022.1 | 2382.978723404255 | 203.12872340424792 | 0 |  | 10.674189814814815 | 922.25 | 2014 | 1 | 2014_01_Asomata_english.xlsx
12 | 65 | 0 | 65 | 0 | 0 | 5 | 60 | 35 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.1 | 7039.999999999993 | 39.781 | 1206.27 | 1319.9999999999927 | 1960.2499999999927 | 640.25 | 9.85 | 88.49367592268831 | 1530 | 0 | 430.2499999999927 | 0 |  | 7.410300925925926 | 640.25 | 2014 | 1 | 2014_01_Asomata_english.xlsx
13 | 305 | 165 | 470 | 0 | 0 | 5 | 465 | 109 | 5.900000000001455 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.4 | 7760.00000000002 | 41.95 | 3744 | 720.0000000000273 | 5467.000000000027 | 4747 | 10.1 | 85.69260227909582 | 5439 | 0 | 88.00000000002728 | 60 |  | 54.942129629629626 | 4747 | 2014 | 1 | 2014_01_Asomata_english.xlsx
14 | 165 | 0 | 165 | 0 | 0 | 4 | 161 | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.8 | 8720 | 40.707 | 2289.69 | 959.99999999998 | 4459.138601036249 | 1773.75 | 10.75 | 79.75874809823952 | 4123.35 | 1725.3886010362694 | 335.788601036249 | 0 |  | 20.52951388888889 | 1773.75 | 2014 | 1 | 2014_01_Asomata_english.xlsx
15 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.8 | 8720 | 40.6 | 2164.5 | 0 | 3057.833333333333 | 724.5 | 10.35 | 82.84121179285748 | 2945.2 | 2333.333333333333 | 112.63333333333276 | 0 |  | 8.385416666666666 | 724.5 | 2014 | 1 | 2014_01_Asomata_english.xlsx
16 | 0 | 125 | 125 | 0 | 0 | 4 | 121 | 40 | 0 | 3.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.35 | 7639.999999999993 | 40.41 | 1942.1999999999946 | -1080.0000000000073 | 2441.7783505154566 | 1212.5 | 9.7 | 89.3316617777724 | 2443 | 2309.278350515464 | 98.77835051545662 | 100 |  | 14.033564814814815 | 1212.5 | 2014 | 1 | 2014_01_Asomata_english.xlsx
17 | 70 | 0 | 70 | 0 | 0 | 6 | 64 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.6 | 8239.999999999993 | 40.032 | 1499.94 | 600 | 1307 | 707 | 10.1 | 85.29028959233953 | 1226.4 | 0 | 140.6 | 60 |  | 8.18287037037037 | 707 | 2014 | 1 | 2014_01_Asomata_english.xlsx
18 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.55 | 8120 | 39.9279 | 1378.1429999999996 | -119.99999999999272 | 3012.531914893624 | 707 | 10.1 | 85.39051319938106 | 3022.2 | 2425.531914893617 | 50.331914893624344 | 60 |  | 8.18287037037037 | 707 | 2014 | 1 | 2014_01_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 6 | 64 | 35 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.7 | 8480.000000000015 | 39.848 | 1284.66 | 360.00000000001455 | 1046.0000000000146 | 686 | 9.8 | 87.6953591741146 | 766.5 | 0 | 279.50000000001455 | 0 |  | 7.939814814814815 | 686 | 2014 | 1 | 2014_01_Asomata_english.xlsx
20 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 83.05 | 4520 | 39.853 | 1290.51 | -3960.0000000000146 | 1443.923884514421 | 795 | 10.6 | 84.33571576310528 | 1576.8 | 4608.9238845144355 | 37.12388451442098 | 170 |  | 9.20138888888889 | 795 | 2014 | 1 | 2014_01_Asomata_english.xlsx
21 | 75 | 0 | 75 | 0 | 0 | 5 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 83.45 | 5480.000000000014 | 39.9101 | 1357.3170000000025 | 960.0000000000136 | 1766.2500000000136 | 806.25 | 10.75 | 82.35643953207843 | 1361.6 | 0 | 404.6500000000135 | 0 |  | 9.331597222222221 | 806.25 | 2014 | 1 | 2014_01_Asomata_english.xlsx
22 | 80 | 0 | 80 | 0 | 0 | 4 | 76 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 83.5 | 5600.000000000007 | 41.15 | 2808 | 119.99999999999363 | 927.9999999999936 | 808 | 10.1 | 87.55099606346177 | 795 | 0 | 132.99999999999363 | 0 |  | 9.351851851851851 | 808 | 2014 | 1 | 2014_01_Asomata_english.xlsx
23 | 85 | 0 | 85 | 0 | 0 | 4 | 81 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.8 | 6320 | 40.547 | 2102.49 | 719.9999999999927 | 1633.7499999999927 | 913.75 | 10.75 | 81.6668521197285 | 1372 | 0 | 261.7499999999927 | 0 |  | 10.575810185185185 | 913.75 | 2014 | 1 | 2014_01_Asomata_english.xlsx
24 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 83.9 | 6560.00000000002 | 40.36 | 1883.7 | 240.00000000002 | 999.50000000002 | 759.5 | 10.85 | 80.72104967939904 | 737.3 | 0 | 262.20000000002005 | 0 |  | 8.79050925925926 | 759.5 | 2014 | 1 | 2014_01_Asomata_english.xlsx
25 | 180 | 0 | 180 | 0 | 0 | 4 | 176 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.2 | 7280.000000000014 | 41.24 | 2913.3 | 719.9999999999936 | 2537.9999999999936 | 1818 | 10.1 | 86.09872835624795 | 2401.7 | 0 | 196.29999999999382 | 60 |  | 21.041666666666668 | 1818 | 2014 | 1 | 2014_01_Asomata_english.xlsx
26 | 95 | 0 | 95 | 0 | 0 | 5 | 90 | 35 | 2.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.3 | 7520 | 40.815 | 2416.05 | 239.99999999998636 | 2346.35638297871 | 1021.25 | 10.75 | 80.70152289845511 | 2160 | 1085.1063829787233 | 186.35638297870992 | 0 |  | 11.820023148148149 | 1021.25 | 2014 | 1 | 2014_01_Asomata_english.xlsx
27 | 90 | 0 | 90 | 0 | 0 | 5 | 85 | 40 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.4 | 7760.00000000002 | 41.001 | 2633.6699999999937 | 240.00000000002 | 1167.00000000002 | 927 | 10.3 | 84.028668254259 | 967.5 | 0 | 199.50000000002 | 0 |  | 10.729166666666668 | 927 | 2014 | 1 | 2014_01_Asomata_english.xlsx
28 | 0 | 415 | 415 | 0 | 0 | 5 | 410 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.55 | 8120 | 41.1385 | 2794.545000000004 | 359.99999999998 | 6967.74999999998 | 4295.25 | 10.35 | 83.32794041678731 | 6832.8 | 2312.5 | 194.9499999999798 | 60 |  | 49.713541666666664 | 4295.25 | 2014 | 1 | 2014_01_Asomata_english.xlsx
29 | 0 | 200 | 200 | 0 | 0 | 4 | 196 | 35 | 0 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.3 | 7520 | 41.601 | 3335.67 | -600 | 1390 | 1990 | 9.95 | 87.1900875536073 | 1323.45 | 0 | 66.54999999999973 | 0 |  | 23.032407407407405 | 1990 | 2014 | 1 | 2014_01_Asomata_english.xlsx
30 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.65 | 8360.00000000002 | 40.5455 | 2100.735 | 840.00000000002 | 1526.00000000002 | 686 | 9.8 | 87.79816733258366 | 1211.8 | 0 | 314.20000000002005 | 0 |  | 7.939814814814815 | 686 | 2014 | 1 | 2014_01_Asomata_english.xlsx
31 | 85 | 0 | 85 | 0 | 0 | 4 | 81 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 85 | 9200.000000000007 | 40.6 | 2164.5 | 839.9999999999873 | 1698.4999999999873 | 858.5 | 10.1 | 84.49689154962007 | 1472.6 | 0 | 225.89999999998713 | 0 |  | 9.936342592592593 | 858.5 | 2014 | 1 | 2014_01_Asomata_english.xlsx
1 | 115 | 0 | 115 | 0 | 0 | 0 | 115 | 35 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.8 | 8720 | 41 | 2632.5 | -480.0000000000073 | 2884.285714285707 | 1150 | 10 | 85.74065420560747 | 2829.6 | 2214.285714285714 | 54.68571428570658 | 0 |  | 13.310185185185185 | 1150 | 2014 | 2 | 2014_02_Asomata_english.xlsx
2 | 85 | 0 | 85 | 0 | 0 | 10 | 75 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.05 | 6920 | 41.199 | 2865.33 | -1800 | 2381.9736842105262 | 892.5 | 10.5 | 83.11420644357625 | 2450 | 3289.4736842105262 | 31.973684210526244 | 100 |  | 10.32986111111111 | 892.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
3 | 70 | 0 | 70 | 0 | 0 | 6 | 64 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.25 | 7400.000000000007 | 41.189 | 2853.63 | 480.0000000000073 | 1162.5000000000073 | 682.5 | 9.75 | 89.08390229100289 | 825 | 0 | 337.5000000000073 | 0 |  | 7.899305555555555 | 682.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
4 | 65 | 0 | 65 | 0 | 0 | 5 | 60 | 35 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.4 | 7760.00000000002 | 40.618 | 2185.56 | 360.00000000001273 | 1016.5000000000127 | 656.5 | 10.1 | 85.69260227909582 | 915 | 0 | 161.50000000001273 | 60 |  | 7.59837962962963 | 656.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
5 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.6 | 8239.999999999993 | 40.63 | 2199.6 | 479.9999999999727 | 1267.4999999999727 | 787.5 | 10.5 | 82.04113570310754 | 1087.5 | 0 | 179.99999999997272 | 0 |  | 9.114583333333334 | 787.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
6 | 70 | 0 | 70 | 0 | 0 | 5 | 65 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 84.6 | 8239.999999999993 | 40.56 | 2117.7 | 0 | 2446.3617021276596 | 707 | 10.1 | 85.29028959233953 | 2204.6 | 1739.3617021276596 | 241.76170212765965 | 0 |  | 8.18287037037037 | 707 | 2014 | 2 | 2014_02_Asomata_english.xlsx
7 | 90 | 0 | 90 | 0 | 0 | 5 | 85 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.75 | 8600.000000000007 | 40.704 | 2286.18 | 360.00000000001455 | 3715.79787234044 | 967.5 | 10.75 | 79.85203318373453 | 3598.9 | 2388.2978723404253 | 116.89787234043979 | 0 |  | 11.197916666666666 | 967.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
8 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 85.15 | 9560.00000000002 | 40.9 | 2515.5 | 960.0000000000127 | 1705.5000000000127 | 745.5 | 10.65 | 79.85463961832018 | 1445.4 | 0 | 260.10000000001287 | 0 |  | 8.628472222222221 | 745.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
9 | 75 | 0 | 75 | 0 | 0 | 5 | 70 | 55 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.65 | 8360.00000000002 | 41 | 2632.5 | -1200 | 1389.7340425531916 | 802.5 | 10.7 | 80.41327475320747 | 1416.2 | 1787.2340425531916 | 33.53404255319151 | 60 |  | 9.288194444444445 | 802.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
10 | 0 | 70 | 70 | 0 | 0 | 0 | 70 | 36 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.65 | 8360.00000000002 | 41.002 | 2634.84 | 0 | 3080.6243386243386 | 742 | 10.6 | 81.17189055276603 | 2989.1 | 2338.6243386243386 | 151.52433862433872 | 60 |  | 8.587962962962964 | 742 | 2014 | 2 | 2014_02_Asomata_english.xlsx
11 | 95 | 0 | 95 | 0 | 0 | 4 | 91 | 40 | 1.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84 | 6800.000000000007 | 41.157 | 2816.19 | -1560.0000000000127 | 1193.2087628865852 | 1021.25 | 10.75 | 81.27796234772978 | 1065 | 1731.958762886598 | 128.2087628865852 | 0 |  | 11.820023148148149 | 1021.25 | 2014 | 2 | 2014_02_Asomata_english.xlsx
12 | 70 | 0 | 70 | 0 | 0 | 8 | 62 | 35 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.05 | 6920 | 41.211 | 2879.3699999999935 | 119.99999999999272 | 2642.1335078533957 | 752.5 | 10.75 | 81.18131792163261 | 2555 | 1769.6335078534032 | 147.1335078533957 | 60 |  | 8.70949074074074 | 752.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
13 | 80 | 0 | 80 | 0 | 0 | 7 | 73 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.5 | 8000.000000000007 | 40.689 | 2268.63 | 1080.0000000000073 | 3074.1702127659646 | 808 | 10.1 | 85.49097262667443 | 2920 | 1186.1702127659573 | 154.1702127659646 | 0 |  | 9.351851851851851 | 808 | 2014 | 2 | 2014_02_Asomata_english.xlsx
14 | 145 | 0 | 145 | 0 | 0 | 5 | 140 | 54 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.6 | 8239.999999999993 | 40.999 | 2631.3300000000063 | 239.99999999998545 | 1791.4999999999854 | 1551.5 | 10.7 | 80.50765653108684 | 1687.5 | 0 | 163.99999999998545 | 60 |  | 17.957175925925927 | 1551.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
15 | 85 | 0 | 85 | 0 | 0 | 5 | 80 | 54 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.7 | 8480.000000000015 | 41.05 | 2691 | 240.00000000002183 | 2942.0531914893836 | 909.5 | 10.7 | 80.31911400993675 | 2693.7 | 1792.5531914893618 | 248.3531914893838 | 0 |  | 10.526620370370368 | 909.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
16 | 75 | 0 | 75 | 0 | 0 | 5 | 70 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 85.05 | 9320 | 41.02 | 2655.9 | 839.9999999999854 | 1594.8749999999854 | 754.875 | 10.065 | 84.69224142954651 | 1554.9 | 0 | 99.97499999998558 | 60 |  | 8.736979166666666 | 754.875 | 2014 | 2 | 2014_02_Asomata_english.xlsx
17 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 54 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.3 | 7520 | 41 | 2632.5 | -1800 | 894.0159574468084 | 731.25 | 9.75 | 88.97860217009155 | 846.8 | 1962.7659574468084 | 107.21595744680849 | 60 |  | 8.463541666666666 | 731.25 | 2014 | 2 | 2014_02_Asomata_english.xlsx
18 | 90 | 0 | 90 | 0 | 0 | 4 | 86 | 55 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.35 | 7639.999999999993 | 41.101 | 2750.67 | 119.99999999999272 | 3937.1666666666592 | 963 | 10.7 | 80.98290834059739 | 3890.9 | 2854.1666666666665 | 46.2666666666596 | 0 |  | 11.145833333333332 | 963 | 2014 | 2 | 2014_02_Asomata_english.xlsx
19 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85.2 | 9680.000000000015 | 41.04 | 2679.3 | 2040.0000000000218 | 3950.7474226804343 | 802.5 | 10.7 | 79.38949463482173 | 3916.8 | 1108.2474226804122 | 33.9474226804341 | 0 |  | 9.288194444444445 | 802.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
20 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 54 | 1.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 85.05 | 9320 | 40.953 | 2577.51 | -360.00000000001455 | 2708.70212765956 | 707 | 10.1 | 84.3987534641966 | 2569.6 | 2361.7021276595747 | 139.1021276595602 | 0 |  | 8.18287037037037 | 707 | 2014 | 2 | 2014_02_Asomata_english.xlsx
21 | 120 | 0 | 120 | 0 | 0 | 5 | 115 | 54 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.9 | 8960.00000000002 | 41.28 | 2960.1 | -359.99999999998 | 4354.59067357515 | 1212 | 10.1 | 84.6938540007847 | 4161 | 3502.5906735751296 | 193.5906735751496 | 0 |  | 14.027777777777779 | 1212 | 2014 | 2 | 2014_02_Asomata_english.xlsx
22 | 70 | 0 | 70 | 0 | 0 | 5 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.9 | 8960.00000000002 | 40.92 | 2538.9 | 0 | 2518.876595744681 | 747.6 | 10.68 | 80.09437503819525 | 2489.3 | 1771.276595744681 | 89.57659574468107 | 60 |  | 8.652777777777779 | 747.6 | 2014 | 2 | 2014_02_Asomata_english.xlsx
23 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 55 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.9 | 6560.00000000002 | 41.08 | 2726.1 | -2400 | 1900.8870967741937 | 752.5 | 10.75 | 81.4719431647888 | 1967 | 3548.3870967741937 | 13.887096774193651 | 80 |  | 8.70949074074074 | 752.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
24 | 155 | 0 | 155 | 0 | 0 | 4 | 151 | 55 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 83.65 | 5960.00000000002 | 41.671 | 3417.57 | -600 | 4491.63829787234 | 1581 | 10.2 | 86.38043452675187 | 4438 | 3510.6382978723404 | 53.638297872340445 | 0 |  | 18.29861111111111 | 1581 | 2014 | 2 | 2014_02_Asomata_english.xlsx
25 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.95 | 6680.000000000014 | 40.52 | 2070.9000000000055 | 719.9999999999936 | 2649.403553299486 | 802.5 | 10.7 | 81.7550934022479 | 2569.6 | 1126.9035532994924 | 79.80355329948588 | 0 |  | 9.288194444444445 | 802.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
26 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 2.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.05 | 6920 | 40.555 | 2111.85 | 239.99999999998636 | 989.9999999999864 | 750 | 10 | 87.26991676575506 | 876 | 0 | 173.99999999998636 | 60 |  | 8.680555555555555 | 750 | 2014 | 2 | 2014_02_Asomata_english.xlsx
27 | 145 | 0 | 145 | 0 | 0 | 4 | 141 | 55 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.15 | 7160.00000000002 | 41.03 | 2667.6 | 240.00000000002 | 2847.357142857163 | 1464.5 | 10.1 | 86.20086207909047 | 2671.8 | 1142.857142857143 | 235.5571428571634 | 60 |  | 16.95023148148148 | 1464.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
28 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.053 | 6927.2 | 40.297 | 1809.99 | -232.80000000001928 | 1690.1893617021083 | 731.5 | 10.45 | 83.50592445600375 | 1444 | 1191.4893617021276 | 306.1893617021083 | 60 |  | 8.466435185185185 | 731.5 | 2014 | 2 | 2014_02_Asomata_english.xlsx
1 | 240 | 0 | 240 | 0 | 0 | 4 | 236 | 54 | 4.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.25 | 7400.000000000007 | 40.802 | 2400.84 | 472.80000000000655 | 2872.8000000000065 | 2400 | 10 | 86.85680473372781 | 2774 | 0 | 98.80000000000655 | 0 |  | 27.77777777777778 | 2400 | 2014 | 3 | 2014_03_Asomata_english.xlsx
2 | 85 | 0 | 85 | 0 | 0 | 4 | 81 | 35 | 2.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.6 | 8239.999999999993 | 40.851 | 2458.17 | 839.9999999999854 | 1677.2499999999854 | 837.25 | 9.85 | 87.45501775458165 | 1489.2 | 0 | 188.0499999999854 | 0 |  | 9.690393518518519 | 837.25 | 2014 | 3 | 2014_03_Asomata_english.xlsx
3 | 95 | 0 | 95 | 0 | 0 | 4 | 91 | 35 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.85 | 8839.999999999993 | 40.998 | 2630.16 | 600 | 3263.9842931937173 | 931 | 9.8 | 87.38837425285168 | 3124.4 | 1732.9842931937173 | 139.58429319371726 | 0 |  | 10.775462962962964 | 931 | 2014 | 3 | 2014_03_Asomata_english.xlsx
4 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 55 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.9 | 8960.00000000002 | 40.978 | 2606.76 | 120.00000000002728 | 2548.9305912596674 | 686 | 9.8 | 87.2865230008087 | 2416.3 | 1742.93059125964 | 132.63059125966765 | 0 |  | 7.939814814814815 | 686 | 2014 | 3 | 2014_03_Asomata_english.xlsx
5 | 160 | 0 | 160 | 0 | 0 | 4 | 156 | 55 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.7 | 8480.000000000015 | 41.551 | 3277.17 | -480.00000000000546 | 4586.321243523311 | 1600 | 10 | 85.94145199063232 | 4628.2 | 3466.3212435233163 | 18.121243523311023 | 60 |  | 18.51851851851852 | 1600 | 2014 | 3 | 2014_03_Asomata_english.xlsx
6 | 120 | 0 | 120 | 0 | 0 | 4 | 116 | 55 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 84 | 6800.000000000007 | 40.9 | 2515.5 | -1680.0000000000073 | 2484.1276595744607 | 1212 | 10.1 | 86.50872230080151 | 2467.4 | 2952.127659574468 | 76.72765957446109 | 60 |  | 14.027777777777779 | 1212 | 2014 | 3 | 2014_03_Asomata_english.xlsx
7 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84 | 6800.000000000007 | 40.75 | 2340 | 0 | 2427.344559585492 | 717.5 | 10.25 | 85.24274099883856 | 2197.3 | 1709.844559585492 | 230.04455958549215 | 0 |  | 8.304398148148149 | 717.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
8 | 85 | 0 | 85 | 0 | 0 | 4 | 81 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.2 | 7280.000000000014 | 40.8 | 2398.5 | 480.00000000000637 | 2529.989361702134 | 858.5 | 10.1 | 86.09872835624795 | 2452.8 | 1191.4893617021276 | 137.18936170213374 | 60 |  | 9.936342592592593 | 858.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
9 | 75 | 0 | 75 | 0 | 0 | 3 | 72 | 54 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.35 | 7639.999999999993 | 40.758 | 2349.36 | 359.9999999999791 | 1109.999999999979 | 750 | 10 | 86.65171192443921 | 905.2 | 0 | 204.79999999997915 | 0 |  | 8.680555555555555 | 750 | 2014 | 3 | 2014_03_Asomata_english.xlsx
10 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 54 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.45 | 7880.000000000014 | 40.67 | 2246.4 | 240.00000000002092 | 2637.4358974359184 | 700 | 10 | 86.44758539458186 | 2343.3 | 1697.4358974358975 | 294.13589743591865 | 0 |  | 8.101851851851851 | 700 | 2014 | 3 | 2014_03_Asomata_english.xlsx
11 | 80 | 0 | 80 | 0 | 0 | 4 | 76 | 50 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.9 | 8960.00000000002 | 40.72 | 2304.9 | 1080.0000000000064 | 3675.234042553198 | 808 | 10.1 | 84.6938540007847 | 3650 | 1787.2340425531916 | 25.234042553197924 | 0 |  | 9.351851851851851 | 808 | 2014 | 3 | 2014_03_Asomata_english.xlsx
12 | 0 | 110 | 110 | 0 | 0 | 5 | 105 | 54 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.5 | 8000.000000000007 | 40.9489 | 2572.713000000004 | -960.0000000000127 | 1896.2959183673343 | 1116.5 | 10.15 | 85.06983483048391 | 1749.3 | 1739.795918367347 | 146.9959183673343 | 0 |  | 12.922453703703704 | 1116.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
13 | 120 | 15 | 135 | 0 | 0 | 4 | 131 | 110 | 2.1999999999970896 | 0.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.1 | 7039.999999999993 | 41.35 | 3042 | -960.0000000000146 | 2761.012953367861 | 1363.5 | 10.1 | 86.3032383998495 | 2664 | 2357.5129533678755 | 97.01295336786097 | 0 |  | 15.78125 | 1363.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
14 | 110 | 0 | 110 | 0 | 0 | 3 | 107 | 54 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.35 | 7639.999999999993 | 41.482 | 3196.44 | 600 | 1683.5 | 1083.5 | 9.85 | 87.97128114156266 | 1594.95 | 0 | 88.55000000000018 | 0 |  | 12.54050925925926 | 1083.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
15 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.35 | 7639.999999999993 | 41 | 2632.5 | 0 | 1822.4489795918366 | 700 | 10 | 86.65171192443921 | 1719.9 | 1122.4489795918366 | 102.54897959183677 | 0 |  | 8.101851851851851 | 700 | 2014 | 3 | 2014_03_Asomata_english.xlsx
16 | 80 | 0 | 80 | 0 | 0 | 3 | 77 | 55 | 1.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16 | 84.35 | 7639.999999999993 | 40.979 | 2607.93 | 0 | 3048.704663212435 | 800 | 10 | 86.65171192443921 | 2844 | 2248.704663212435 | 204.7046632124352 | 0 |  | 9.25925925925926 | 800 | 2014 | 3 | 2014_03_Asomata_english.xlsx
17 | 70 | 0 | 70 | 0 | 0 | 5 | 65 | 55 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.35 | 7639.999999999993 | 40.922 | 2541.24 | 0 | 3111.255319148936 | 707 | 10.1 | 85.79377418261309 | 2993 | 2404.255319148936 | 118.255319148936 | 0 |  | 8.18287037037037 | 707 | 2014 | 3 | 2014_03_Asomata_english.xlsx
18 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 54 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.35 | 7639.999999999993 | 40.8611 | 2469.9870000000014 | 0 | 757.5 | 757.5 | 10.1 | 85.79377418261309 | 791 | 0 | 26.5 | 60 |  | 8.76736111111111 | 757.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.3 | 7520 | 40.799 | 2397.33 | -119.99999999999272 | 2305.7500000000073 | 707 | 10.1 | 85.89518526320718 | 2241.1 | 1718.75 | 64.65000000000737 | 0 |  | 8.18287037037037 | 707 | 2014 | 3 | 2014_03_Asomata_english.xlsx
20 | 80 | 0 | 80 | 0 | 0 | 4 | 76 | 54 | 1.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 84.5 | 8000.000000000007 | 40.772 | 2365.74 | 480.0000000000073 | 2969.4358974359047 | 792 | 9.9 | 87.21806298276887 | 2664 | 1697.4358974358975 | 305.43589743590474 | 0 |  | 9.166666666666666 | 792 | 2014 | 3 | 2014_03_Asomata_english.xlsx
21 | 170 | 0 | 170 | 0 | 0 | 3 | 167 | 54 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.75 | 8600.000000000007 | 41.399 | 3099.33 | 600 | 2283 | 1683 | 9.9 | 86.70801583082284 | 2226.8 | 0 | 56.20000000000027 | 0 |  | 19.479166666666668 | 1683 | 2014 | 3 | 2014_03_Asomata_english.xlsx
22 | 130 | 85 | 215 | 0 | 0 | 4 | 211 | 108 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.4 | 7760.00000000002 | 41.231 | 2902.77 | -839.9999999999873 | 3689.8421052631707 | 2193 | 10.2 | 84.85247872733999 | 3733.8 | 2336.842105263158 | 16.042105263170924 | 60 |  | 25.381944444444443 | 2193 | 2014 | 3 | 2014_03_Asomata_english.xlsx
23 | 70 | 0 | 70 | 0 | 0 | 3 | 67 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.35 | 7639.999999999993 | 41.137 | 2792.79 | -120.00000000002728 | 2293.98979591834 | 689.5 | 9.85 | 87.97128114156266 | 2073.2 | 1724.4897959183672 | 220.78979591834013 | 0 |  | 7.980324074074074 | 689.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
24 | 125 | 0 | 125 | 0 | 0 | 4 | 121 | 54 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 83.9 | 6560.00000000002 | 40.999 | 2631.3300000000063 | -1079.9999999999727 | 1315.4787234042826 | 1262.5 | 10.1 | 86.71518703182966 | 1245 | 1132.9787234042553 | 130.47872340428262 | 60 |  | 14.612268518518519 | 1262.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 55 | 1.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.65 | 8360.00000000002 | 40.2 | 1696.5000000000055 | 1800 | 4875.702127659575 | 714 | 10.2 | 84.35510194699215 | 4777.5 | 2361.7021276595747 | 158.20212765957513 | 60 |  | 8.26388888888889 | 714 | 2014 | 3 | 2014_03_Asomata_english.xlsx
26 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 55 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.8 | 8720 | 40.211 | 1709.37 | 359.99999999998 | 1066.99999999998 | 707 | 10.1 | 84.89173683723513 | 1014.7 | 0 | 52.29999999998006 | 0 |  | 8.18287037037037 | 707 | 2014 | 3 | 2014_03_Asomata_english.xlsx
27 | 0 | 75 | 75 | 0 | 0 | 4 | 71 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.3 | 7520 | 40.295 | 1807.65 | -1200 | 1908.5638297872342 | 757.5 | 10.1 | 85.89518526320718 | 1890.7 | 2351.063829787234 | 77.86382978723418 | 60 |  | 8.76736111111111 | 757.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
28 | 125 | 0 | 125 | 0 | 0 | 4 | 121 | 55 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84 | 6800.000000000007 | 40.822 | 2424.24 | -719.9999999999927 | 5183.698979591843 | 1281.25 | 10.25 | 85.24274099883856 | 5112 | 4622.448979591836 | 131.69897959184345 | 60 |  | 14.829282407407407 | 1281.25 | 2014 | 3 | 2014_03_Asomata_english.xlsx
29 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.1 | 7039.999999999993 | 40.881 | 2493.27 | 239.99999999998545 | 997.4999999999854 | 757.5 | 10.1 | 86.3032383998495 | 1007.4 | 0 | 50.09999999998547 | 60 |  | 8.76736111111111 | 757.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
30 | 175 | 0 | 175 | 0 | 0 | 3 | 172 | 45 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.1 | 7039.999999999993 | 41.803 | 3572.0099999999916 | 0 | 1767.5 | 1767.5 | 10.1 | 86.3032383998495 | 1576.8 | 0 | 250.7 | 60 |  | 20.457175925925927 | 1767.5 | 2014 | 3 | 2014_03_Asomata_english.xlsx
31 | 170 | 0 | 170 | 0 | 0 | 4 | 166 | 54 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.05 | 6920 | 41.301 | 2984.67 | -119.99999999999272 | 3317.9302325581466 | 1717 | 10.1 | 86.4058581839159 | 3342.25 | 1720.9302325581396 | 35.6802325581466 | 60 |  | 19.872685185185187 | 1717 | 2014 | 3 | 2014_03_Asomata_english.xlsx
1 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 54 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.5 | 8000.000000000007 | 41.468 | 3180.06 | 1080.0000000000073 | 3197.7551020408237 | 980 | 9.8 | 88.1080432172869 | 2956.5 | 1137.7551020408164 | 241.25510204082366 | 0 |  | 11.342592592592593 | 980 | 2014 | 4 | 2014_04_Asomata_english.xlsx
2 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.5 | 8000.000000000007 | 41.38 | 3077.1 | 0 | 1824.4615384615383 | 686 | 9.8 | 88.1080432172869 | 1554.9 | 1138.4615384615383 | 269.5615384615385 | 0 |  | 7.939814814814815 | 686 | 2014 | 4 | 2014_04_Asomata_english.xlsx
3 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 50 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.8 | 8720 | 41.32 | 3006.9 | 719.9999999999927 | 3744.4642857142785 | 738.75 | 9.85 | 87.04634944731724 | 3679.2 | 2285.714285714286 | 65.26428571427869 | 0 |  | 8.550347222222221 | 738.75 | 2014 | 4 | 2014_04_Asomata_english.xlsx
4 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.9 | 8960.00000000002 | 41.29 | 2971.8 | 240.00000000002 | 929.50000000002 | 689.5 | 9.85 | 86.84344420385028 | 795.7 | 0 | 133.80000000002008 | 0 |  | 7.980324074074074 | 689.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
5 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 54 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.6 | 8239.999999999993 | 41.241 | 2914.47 | -720.0000000000273 | 2885.9361702127385 | 707 | 10.1 | 85.29028959233953 | 2934.6 | 2898.936170212766 | 11.33617021273858 | 60 |  | 8.18287037037037 | 707 | 2014 | 4 | 2014_04_Asomata_english.xlsx
6 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 84.7 | 8480.000000000015 | 41.22 | 2889.9 | 240.00000000002183 | 4530.6735751295555 | 700 | 10 | 85.94145199063232 | 4343.5 | 3590.6735751295337 | 247.1735751295555 | 60 |  | 8.101851851851851 | 700 | 2014 | 4 | 2014_04_Asomata_english.xlsx
7 | 230 | 0 | 230 | 0 | 0 | 3 | 230 | 55 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.25 | 7400.000000000007 | 41.202 | 2868.84 | -1080.0000000000073 | 1242.9999999999927 | 2323 | 10.1 | 85.99683637002754 | 1169 | 0 | 73.99999999999272 | 0 |  | 26.886574074074073 | 2323 | 2014 | 4 | 2014_04_Asomata_english.xlsx
8 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 54 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.35 | 7639.999999999993 | 41.302 | 2985.84 | 239.99999999998545 | 1130.9999999999854 | 891 | 9.9 | 87.52698174185778 | 1043.9 | 0 | 87.09999999998558 | 0 |  | 10.3125 | 891 | 2014 | 4 | 2014_04_Asomata_english.xlsx
9 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 45 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.45 | 7880.000000000014 | 41.228 | 2899.26 | 240.00000000002092 | 933.0000000000209 | 693 | 9.9 | 87.32079332786046 | 664.3 | 0 | 268.70000000002096 | 0 |  | 8.020833333333334 | 693 | 2014 | 4 | 2014_04_Asomata_english.xlsx
10 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 54 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.4 | 7760.00000000002 | 41.4 | 3100.5 | -119.99999999999363 | 740.0000000000064 | 860 | 10.75 | 80.51118911803421 | 635.1 | 0 | 104.90000000000634 | 0 |  | 9.953703703703704 | 860 | 2014 | 4 | 2014_04_Asomata_english.xlsx
11 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.65 | 8360.00000000002 | 41.31 | 2995.2 | 600 | 1392 | 792 | 9.9 | 86.91131715750706 | 992.8 | 0 | 399.2 | 0 |  | 9.166666666666666 | 792 | 2014 | 4 | 2014_04_Asomata_english.xlsx
12 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.9 | 8960.00000000002 | 41.3995 | 3099.9150000000086 | 600 | 1531 | 931 | 9.8 | 87.2865230008087 | 1416.2 | 0 | 114.8 | 0 |  | 10.775462962962964 | 931 | 2014 | 4 | 2014_04_Asomata_english.xlsx
13 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 55 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.5 | 8000.000000000007 | 41.65 | 3393 | -960.0000000000127 | 1964.5962566844792 | 1138.5 | 9.9 | 87.21806298276887 | 1800 | 1786.096256684492 | 164.59625668447916 | 0 |  | 13.177083333333334 | 1138.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
14 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 83.75 | 6200.000000000007 | 40.662 | 2237.04 | -1800 | 1270.6595744680849 | 693 | 9.9 | 88.78485453335753 | 1123.2 | 2377.659574468085 | 147.45957446808484 | 0 |  | 8.020833333333334 | 693 | 2014 | 4 | 2014_04_Asomata_english.xlsx
15 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 83.8 | 6320 | 40.6176 | 2185.0920000000024 | 119.99999999999272 | 927.9999999999927 | 808 | 10.1 | 86.9226396323843 | 770.4 | 0 | 157.59999999999275 | 0 |  | 9.351851851851851 | 808 | 2014 | 4 | 2014_04_Asomata_english.xlsx
16 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 54 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 83.95 | 6680.000000000014 | 40.578 | 2138.76 | 360.00000000001364 | 1053.0000000000136 | 693 | 9.9 | 88.36156559636892 | 919.8 | 0 | 133.2000000000137 | 0 |  | 8.020833333333334 | 693 | 2014 | 4 | 2014_04_Asomata_english.xlsx
17 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 45 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.35 | 7639.999999999993 | 40.67 | 2246.4 | 959.9999999999791 | 1642.499999999979 | 682.5 | 9.75 | 88.87355069173252 | 1321.3 | 0 | 321.1999999999791 | 0 |  | 7.899305555555555 | 682.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
18 | 105 | 0 | 105 | 0 | 0 | 4 | 105 | 35 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.6 | 8239.999999999993 | 40.89 | 2503.8 | 600 | 1623.75 | 1023.75 | 9.75 | 88.35199229565427 | 1452.7 | 0 | 171.05 | 0 |  | 11.848958333333334 | 1023.75 | 2014 | 4 | 2014_04_Asomata_english.xlsx
19 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 54 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85 | 9200.000000000007 | 41.09 | 2737.8 | 960.0000000000146 | 2247.0000000000146 | 1287 | 9.9 | 86.20389945971341 | 2109.7 | 0 | 137.30000000001473 | 0 |  | 14.895833333333334 | 1287 | 2014 | 4 | 2014_04_Asomata_english.xlsx
20 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 84.7 | 8480.000000000015 | 40.892 | 2506.14 | -719.9999999999927 | 1462.5000000000073 | 682.5 | 9.75 | 88.1450789647511 | 1387 | 1500 | 135.50000000000728 | 60 |  | 7.899305555555555 | 682.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
21 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.45 | 7880.000000000014 | 40.75 | 2340 | -600.0000000000009 | 142.4999999999991 | 742.5 | 9.9 | 87.32079332786046 | 0 | 0 | 142.4999999999991 | 0 |  | 8.59375 | 742.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
22 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 50 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.6 | 8239.999999999993 | 40.901 | 2516.67 | 359.9999999999791 | 1481.249999999979 | 1121.25 | 9.75 | 88.35199229565427 | 1337.6 | 0 | 143.64999999997917 | 0 |  | 12.977430555555555 | 1121.25 | 2014 | 4 | 2014_04_Asomata_english.xlsx
23 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.65 | 8360.00000000002 | 41.152 | 2810.34 | 120.00000000002728 | 1357.5000000000273 | 1237.5 | 9.9 | 86.91131715750706 | 1116.9 | 0 | 240.60000000002742 | 0 |  | 14.322916666666666 | 1237.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
24 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 55 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.75 | 8600.000000000007 | 41.01 | 2644.2 | 239.99999999998727 | 978.7499999999873 | 738.75 | 9.85 | 87.14815804316206 | 852.6 | 0 | 126.14999999998736 | 0 |  | 8.550347222222221 | 738.75 | 2014 | 4 | 2014_04_Asomata_english.xlsx
25 | 215 | 30 | 245 | 0 | 0 | 3 | 245 | 90 | 5.099999999998545 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.6 | 8239.999999999993 | 41.637 | 3377.79 | -360.00000000001455 | 2053.2499999999854 | 2413.25 | 9.85 | 87.45501775458165 | 1956.4 | 0 | 96.84999999998558 | 0 |  | 27.93113425925926 | 2413.25 | 2014 | 4 | 2014_04_Asomata_english.xlsx
26 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.5 | 8000.000000000007 | 40.55 | 2106 | -239.99999999998545 | 1159.202127659589 | 787.5 | 10.5 | 82.2341736694678 | 890.6 | 611.7021276595744 | 268.602127659589 | 0 |  | 9.114583333333334 | 787.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
27 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.6 | 8239.999999999993 | 40.488 | 2033.46 | 239.99999999998545 | 946.9999999999854 | 707 | 10.1 | 85.29028959233953 | 905.2 | 0 | 101.79999999998552 | 60 |  | 8.18287037037037 | 707 | 2014 | 4 | 2014_04_Asomata_english.xlsx
28 | 95 | 115 | 210 | 0 | 0 | 4 | 210 | 70 | 2.3000000000029104 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.7 | 8480.000000000015 | 41.103 | 2753.01 | 240.00000000002183 | 2308.500000000022 | 2068.5 | 9.85 | 87.25020506663179 | 1919.9 | 0 | 388.60000000002196 | 0 |  | 23.94097222222222 | 2068.5 | 2014 | 4 | 2014_04_Asomata_english.xlsx
29 | 120 | 0 | 120 | 0 | 0 | 4 | 120 | 55 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.6 | 8239.999999999993 | 41.172 | 2833.74 | -240.00000000002183 | 959.9999999999782 | 1200 | 10 | 86.14319248826293 | 730 | 0 | 229.99999999997817 | 0 |  | 13.88888888888889 | 1200 | 2014 | 4 | 2014_04_Asomata_english.xlsx
30 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 55 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.7 | 8480.000000000015 | 41 | 2632.5 | 240.00000000002183 | 978.7500000000218 | 738.75 | 9.85 | 87.25020506663179 | 890.6 | 0 | 148.1500000000218 | 60 |  | 8.550347222222221 | 738.75 | 2014 | 4 | 2014_04_Asomata_english.xlsx
1 | 220 | 90 | 310 | 0 | 0 | 4 | 310 | 110 | 4 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.5 | 8000.000000000007 | 42.127 | 3951.09 | -480.0000000000073 | 3127.1489361702056 | 3038 | 9.8 | 88.1080432172869 | 2671.8 | 569.1489361702128 | 455.34893617020543 | 0 |  | 35.16203703703704 | 3038 | 2014 | 5 | 2014_05_Asomata_english.xlsx
2 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 55 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.4 | 7760.00000000002 | 41.079 | 2724.93 | -239.99999999998727 | 883.5000000000127 | 1123.5 | 10.7 | 80.88740962793158 | 912.5 | 0 | 71.00000000001273 | 100 |  | 13.003472222222221 | 1123.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
3 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 54 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.45 | 7880.000000000014 | 40.75 | 2340 | 119.99999999999363 | 809.4999999999936 | 689.5 | 9.85 | 87.76404608586991 | 788.4 | 0 | 81.09999999999366 | 60 |  | 7.980324074074074 | 689.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
4 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 54 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 83.6 | 5839.999999999993 | 40.502 | 2049.84 | -2040.000000000021 | 2569.712765957426 | 689.5 | 9.85 | 89.55730183522063 | 2438.2 | 3920.212765957447 | 131.51276595742638 | 0 |  | 7.980324074074074 | 689.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
5 | 80 | 0 | 80 | 0 | 0 | 6 | 80 | 55 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 16.45 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 5 | 84 | 6800.000000000007 | 40.518 | 2068.56 | 960.0000000000146 | 1748.0000000000146 | 788 | 9.85 | 88.70437515107567 | 1554.9 | 0 | 193.1000000000147 | 0 |  | 9.12037037037037 | 788 | 2014 | 5 | 2014_05_Asomata_english.xlsx
6 | 175 | 0 | 175 | 0 | 0 | 4 | 175 | 54 | 3.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 6 | 84.4 | 7760.00000000002 | 41.086 | 2733.1199999999935 | 960.0000000000127 | 2683.7500000000127 | 1723.75 | 9.85 | 87.86754142323531 | 2489.3 | 0 | 194.45000000001255 | 0 |  | 19.950810185185187 | 1723.75 | 2014 | 5 | 2014_05_Asomata_english.xlsx
7 | 290 | 0 | 290 | 0 | 0 | 4 | 290 | 55 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 7 | 84.6 | 8239.999999999993 | 41.6 | 3334.5 | 479.9999999999727 | 3379.9999999999727 | 2900 | 10 | 86.14319248826293 | 3248.5 | 0 | 131.49999999997272 | 0 |  | 33.56481481481482 | 2900 | 2014 | 5 | 2014_05_Asomata_english.xlsx
8 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 55 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 8 | 84.7 | 8480.000000000015 | 41.497 | 3213.99 | 240.00000000002183 | 2053.000000000022 | 1813 | 9.8 | 87.6953591741146 | 1693.6 | 0 | 359.4000000000219 | 0 |  | 20.983796296296298 | 1813 | 2014 | 5 | 2014_05_Asomata_english.xlsx
9 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 9 | 84.85 | 8839.999999999993 | 41.821 | 3593.0699999999933 | 359.9999999999782 | 2132.999999999978 | 1773 | 9.85 | 86.94477844446158 | 2044 | 0 | 88.99999999997817 | 0 |  | 20.520833333333332 | 1773 | 2014 | 5 | 2014_05_Asomata_english.xlsx
10 | 265 | 0 | 265 | 0 | 0 | 4 | 265 | 55 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 10 | 84.8 | 8720 | 41.852 | 3629.34 | -119.99999999999272 | 2490.2500000000073 | 2610.25 | 9.85 | 87.04634944731724 | 2336 | 0 | 154.25000000000728 | 0 |  | 30.21122685185185 | 2610.25 | 2014 | 5 | 2014_05_Asomata_english.xlsx
11 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 40 | 2.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 11 | 84.8 | 8720 | 40.953 | 2577.51 | 0 | 967.5 | 967.5 | 10.75 | 79.75874809823952 | 584 | 0 | 383.5 | 0 |  | 11.197916666666666 | 967.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
12 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 40 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 12 | 84.8 | 8720 | 41.597 | 3330.99 | 0 | 2142 | 2142 | 10.2 | 84.05946490745832 | 1898 | 0 | 244 | 0 |  | 24.791666666666668 | 2142 | 2014 | 5 | 2014_05_Asomata_english.xlsx
13 | 150 | 0 | 150 | 0 | 0 | 4 | 150 | 55 | 3.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 13 | 85 | 9200.000000000007 | 40.912 | 2529.54 | 480.0000000000073 | 2017.5000000000073 | 1537.5 | 10.25 | 83.26035167328418 | 1609.65 | 0 | 407.8500000000072 | 0 |  | 17.79513888888889 | 1537.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
14 | 185 | 0 | 185 | 0 | 0 | 2 | 185 | 55 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 14 | 84.8 | 8720 | 41.111 | 2762.3699999999935 | -480.0000000000073 | 1406.9999999999925 | 1887 | 10.2 | 84.05946490745832 | 1197.2 | 0 | 209.79999999999245 | 0 |  | 21.840277777777775 | 1887 | 2014 | 5 | 2014_05_Asomata_english.xlsx
15 | 190 | 0 | 190 | 0 | 0 | 3 | 190 | 54 | 4.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 15 | 84.75 | 8600.000000000007 | 41.29 | 2971.8 | -119.99999999999272 | 1799.0000000000073 | 1919 | 10.1 | 84.9910254183313 | 1560 | 0 | 239.00000000000728 | 0 |  | 22.21064814814815 | 1919 | 2014 | 5 | 2014_05_Asomata_english.xlsx
16 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 54 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 16 | 84.65 | 8360.00000000002 | 41.477 | 3190.59 | -239.99999999998727 | 2017.5000000000127 | 2257.5 | 10.5 | 81.9449561770781 | 1695 | 0 | 322.50000000001273 | 0 |  | 26.12847222222222 | 2257.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
17 | 75 | 170 | 245 | 0 | 0 | 4 | 245 | 108 | 1.5 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.4 | 7760.00000000002 | 41.702 | 3453.84 | -600 | 1972.5 | 2572.5 | 10.5 | 82.42812219227312 | 1687.5 | 0 | 285 | 0 |  | 29.774305555555557 | 2572.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
18 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 54 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.6 | 8239.999999999993 | 41.583 | 3314.61 | 479.9999999999727 | 2479.9999999999727 | 2000 | 10 | 86.14319248826293 | 2347.5 | 0 | 132.49999999997272 | 0 |  | 23.14814814814815 | 2000 | 2014 | 5 | 2014_05_Asomata_english.xlsx
19 | 0 | 220 | 220 | 0 | 0 | 4 | 220 | 54 | 0 | 4.19999999999709 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 19 | 84.7 | 8480.000000000015 | 41.755 | 3515.85 | 240.00000000002183 | 2561.000000000022 | 2321 | 10.55 | 81.46109193424863 | 2255.7 | 0 | 305.300000000022 | 0 |  | 26.863425925925927 | 2321 | 2014 | 5 | 2014_05_Asomata_english.xlsx
20 | 0 | 240 | 240 | 0 | 0 | 4 | 240 | 54 | 0 | 5.30000000000291 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 20 | 84.85 | 8839.999999999993 | 41.948 | 3741.66 | 359.9999999999782 | 2843.999999999978 | 2484 | 10.35 | 82.74454760173396 | 2416.3 | 0 | 427.69999999997844 | 0 |  | 28.75 | 2484 | 2014 | 5 | 2014_05_Asomata_english.xlsx
21 | 0 | 280 | 280 | 0 | 0 | 3 | 280 | 40 | 0 | 6.19999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 21 | 84.85 | 8839.999999999993 | 41.97 | 3767.4 | 0 | 2954 | 2954 | 10.55 | 81.17593058558732 | 2649.9 | 0 | 304.1 | 0 |  | 34.18981481481482 | 2954 | 2014 | 5 | 2014_05_Asomata_english.xlsx
22 | 0 | 370 | 370 | 0 | 0 | 3 | 370 | 53 | 0 | 8.30000000000291 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 22 | 84.6 | 8239.999999999993 | 41.887 | 3670.29 | -600 | 3192.5 | 3792.5 | 10.25 | 84.04213901293944 | 3021.75 | 0 | 170.75 | 0 |  | 43.894675925925924 | 3792.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
23 | 0 | 325 | 325 | 0 | 0 | 3 | 325 | 53 | 0 | 6.5 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 23 | 84.65 | 8360.00000000002 | 41.637 | 3377.79 | 120.00000000002728 | 3516.250000000027 | 3396.25 | 10.45 | 82.33703730711196 | 3217.5 | 0 | 298.75000000002683 | 0 |  | 39.30844907407407 | 3396.25 | 2014 | 5 | 2014_05_Asomata_english.xlsx
24 | 0 | 365 | 365 | 0 | 0 | 4 | 365 | 54 | 0 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 24 | 84.9 | 8960.00000000002 | 42.002 | 3804.84 | 600 | 4286.5 | 3686.5 | 10.1 | 84.6938540007847 | 3876.3 | 0 | 410.2 | 0 |  | 42.667824074074076 | 3686.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
25 | 0 | 305 | 305 | 0 | 0 | 0 | 305 | 49 | 0 | 7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 25 | 85.2 | 9680.000000000015 | 41.738 | 3495.96 | 719.9999999999945 | 3876.7499999999945 | 3156.75 | 10.35 | 82.07416353551619 | 3810.6 | 0 | 66.14999999999463 | 0 |  | 36.536458333333336 | 3156.75 | 2014 | 5 | 2014_05_Asomata_english.xlsx
26 | 0 | 350 | 350 | 0 | 0 | 5 | 350 | 55 | 0 | 6.900000000001455 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 26 | 85.4 | 10160 | 41.4544 | 3164.147999999995 | 480.00000000000546 | 3910.000000000006 | 3430 | 9.8 | 86.28091789711274 | 3592.5 | 0 | 317.5000000000059 | 0 |  | 39.699074074074076 | 3430 | 2014 | 5 | 2014_05_Asomata_english.xlsx
27 | 0 | 355 | 355 | 0 | 0 | 5 | 355 | 55 | 0 | 8.049999999995634 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 27 | 85 | 9200.000000000007 | 41.87 | 3650.4 | -960.0000000000127 | 2465.7499999999873 | 3425.75 | 9.65 | 88.43716110374744 | 2279.7 | 0 | 186.049999999987 | 0 |  | 39.64988425925926 | 3425.75 | 2014 | 5 | 2014_05_Asomata_english.xlsx
28 | 0 | 355 | 355 | 0 | 0 | 3 | 355 | 44 | 0 | 8.55000000000291 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 28 | 84.9 | 8960.00000000002 | 42.03 | 3837.6 | -239.99999999998727 | 3444.900000000013 | 3684.9 | 10.38 | 82.40924136877892 | 3175.2 | 0 | 269.700000000013 | 0 |  | 42.64930555555556 | 3684.9 | 2014 | 5 | 2014_05_Asomata_english.xlsx
29 | 0 | 380 | 380 | 0 | 0 | 3 | 380 | 55 | 0 | 8.599999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 29 | 84.95 | 9080.000000000015 | 42.08 | 3896.1 | 119.99999999999454 | 5622.974619289334 | 3838 | 10.1 | 84.59525812883966 | 5241.4 | 1664.9746192893401 | 381.5746192893348 | 0 |  | 44.4212962962963 | 3838 | 2014 | 5 | 2014_05_Asomata_english.xlsx
30 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 55 | 0 | 8.900000000001455 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 30 | 84.8 | 8720 | 41.997 | 3798.99 | -360.00000000001455 | 3986.9999999999854 | 4347 | 10.35 | 82.84121179285748 | 3788.7 | 0 | 198.29999999998563 | 0 |  | 50.3125 | 4347 | 2014 | 5 | 2014_05_Asomata_english.xlsx
31 | 0 | 250 | 250 | 0 | 0 | 3 | 250 | 45 | 0 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 31 | 84.85 | 8839.999999999993 | 42.004 | 3807.18 | 119.99999999999272 | 2557.4999999999927 | 2437.5 | 9.75 | 87.83651976184066 | 2212.35 | 0 | 345.1499999999928 | 0 |  | 28.211805555555557 | 2437.5 | 2014 | 5 | 2014_05_Asomata_english.xlsx
1 | 225 | 0 | 225 | 0 | 0 | 4 | 225 | 40 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.9 | 8960.00000000002 | 41.7 | 3451.5 | 120.00000000002728 | 2448.7500000000273 | 2328.75 | 10.35 | 82.64810873506525 | 2263 | 0 | 185.75000000002728 | 0 |  | 26.953125 | 2328.75 | 2014 | 6 | 2014_06_Asomata_english.xlsx
2 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 55 | 0 | 8.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.35 | 7639.999999999993 | 41.849 | 3625.83 | -1320.0000000000273 | 2103.699999999973 | 3423.7 | 10.22 | 84.78641088496987 | 2138.85 | 0 | 24.84999999997308 | 60 |  | 39.62615740740741 | 3423.7 | 2014 | 6 | 2014_06_Asomata_english.xlsx
3 | 260 | 0 | 260 | 0 | 0 | 4 | 260 | 55 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.45 | 7880.000000000014 | 41.428 | 3133.2599999999916 | 240.00000000002092 | 2931.000000000021 | 2691 | 10.35 | 83.52423709621435 | 2642.6 | 0 | 288.400000000021 | 0 |  | 31.145833333333332 | 2691 | 2014 | 6 | 2014_06_Asomata_english.xlsx
4 | 30 | 355 | 385 | 0 | 0 | 5 | 385 | 104 | 0.5500000000029104 | 7.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.1 | 7039.999999999993 | 41.761 | 3522.87 | -840.0000000000209 | 4803.819148936149 | 3888.5 | 10.1 | 86.3032383998495 | 4730.4 | 1755.3191489361702 | 133.4191489361492 | 60 |  | 45.00578703703704 | 3888.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
5 | 370 | 0 | 370 | 0 | 0 | 5 | 370 | 50 | 8.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.35 | 7639.999999999993 | 41.77 | 3533.4 | 600 | 4429.5 | 3829.5 | 10.35 | 83.72146079655963 | 4033 | 0 | 396.5 | 0 |  | 44.322916666666664 | 3829.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
6 | 380 | 0 | 380 | 0 | 0 | 3 | 380 | 55 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.5 | 8000.000000000007 | 41.88 | 3662.1 | 360.00000000001455 | 4198.000000000015 | 3838 | 10.1 | 85.49097262667443 | 4164.55 | 0 | 33.45000000001437 | 0 |  | 44.4212962962963 | 3838 | 2014 | 6 | 2014_06_Asomata_english.xlsx
7 | 350 | 0 | 350 | 0 | 0 | 3 | 350 | 55 | 7.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.1 | 9439.999999999993 | 41.84 | 3615.3 | 1439.9999999999854 | 5027.499999999985 | 3587.5 | 10.25 | 83.06717220304455 | 4817.4 | 0 | 210.0999999999849 | 0 |  | 41.52199074074074 | 3587.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
8 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 45 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.95 | 9080.000000000015 | 42.008 | 3811.86 | -359.9999999999782 | 3781.000000000022 | 4141 | 10.1 | 84.59525812883966 | 3587.2 | 0 | 193.800000000022 | 0 |  | 47.92824074074074 | 4141 | 2014 | 6 | 2014_06_Asomata_english.xlsx
9 | 435 | 0 | 435 | 0 | 0 | 3 | 435 | 55 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.95 | 9080.000000000015 | 42.12 | 3942.9 | 0 | 4284.75 | 4284.75 | 9.85 | 86.74234589860717 | 3912.8 | 0 | 371.95 | 0 |  | 49.592013888888886 | 4284.75 | 2014 | 6 | 2014_06_Asomata_english.xlsx
10 | 0 | 435 | 435 | 0 | 0 | 3 | 435 | 55 | 0 | 8.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.9 | 8960.00000000002 | 42.061 | 3873.87 | -119.99999999999454 | 4360.5000000000055 | 4480.5 | 10.3 | 83.04931314640051 | 4124.5 | 0 | 236.00000000000546 | 0 |  | 51.857638888888886 | 4480.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
11 | 0 | 420 | 420 | 0 | 0 | 3 | 420 | 55 | 0 | 8.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 85.1 | 9439.999999999993 | 42.079 | 3894.93 | 479.9999999999727 | 4679.999999999973 | 4200 | 10 | 85.14385150812066 | 4373.25 | 0 | 306.7499999999727 | 0 |  | 48.611111111111114 | 4200 | 2014 | 6 | 2014_06_Asomata_english.xlsx
12 | 420 | 40 | 460 | 0 | 0 | 4 | 460 | 55 | 8.400000000001455 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.9 | 8960.00000000002 | 41.982 | 3781.44 | -479.9999999999727 | 4166.000000000027 | 4646 | 10.1 | 84.6938540007847 | 4040.4 | 0 | 125.6000000000272 | 0 |  | 53.773148148148145 | 4646 | 2014 | 6 | 2014_06_Asomata_english.xlsx
13 | 445 | 0 | 445 | 0 | 0 | 4 | 445 | 54 | 9.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85 | 9200.000000000007 | 41.7 | 3451.5 | 239.99999999998727 | 4578.749999999987 | 4338.75 | 9.75 | 87.53011329755516 | 4277.8 | 0 | 300.949999999988 | 0 |  | 50.217013888888886 | 4338.75 | 2014 | 6 | 2014_06_Asomata_english.xlsx
14 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 55 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 85.15 | 9560.00000000002 | 41.68 | 3428.1 | 360.00000000001273 | 4385.500000000013 | 4025.5 | 9.7 | 87.67545483867114 | 4139.1 | 0 | 246.40000000001237 | 0 |  | 46.59143518518518 | 4025.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
15 | 390 | 0 | 390 | 0 | 0 | 4 | 390 | 54 | 9.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.9 | 8960.00000000002 | 42.101 | 3920.67 | -600 | 3436.5 | 4036.5 | 10.35 | 82.64810873506525 | 3219.3 | 0 | 217.2 | 0 |  | 46.71875 | 4036.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
16 | 400 | 0 | 400 | 0 | 0 | 3 | 400 | 45 | 8.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 85 | 9200.000000000007 | 41.066 | 2709.72 | 239.99999999998727 | 4119.999999999987 | 3880 | 9.7 | 87.9812994485735 | 3877.5 | 0 | 242.49999999998727 | 0 |  | 44.907407407407405 | 3880 | 2014 | 6 | 2014_06_Asomata_english.xlsx
17 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 55 | 9.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.6 | 8239.999999999993 | 41.881 | 3663.27 | -960.0000000000146 | 3742.4999999999854 | 4702.5 | 10.45 | 82.43367702226118 | 3489.4 | 0 | 253.09999999998536 | 0 |  | 54.427083333333336 | 4702.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
18 | 0 | 410 | 410 | 0 | 0 | 3 | 410 | 45 | 0 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.8 | 8720 | 41.92 | 3708.9 | 480.0000000000073 | 4559.500000000007 | 4079.5 | 9.95 | 86.17151176442964 | 4423.8 | 0 | 135.700000000008 | 0 |  | 47.21643518518518 | 4079.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
19 | 420 | 0 | 420 | 0 | 0 | 3 | 420 | 54 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.3 | 7520 | 41.87 | 3650.4 | -1200 | 3021 | 4221 | 10.05 | 86.32252449337238 | 2767.5 | 0 | 253.5 | 0 |  | 48.854166666666664 | 4221 | 2014 | 6 | 2014_06_Asomata_english.xlsx
20 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 54 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.4 | 7760.00000000002 | 41.749 | 3508.8300000000063 | 240.00000000002 | 4463.00000000002 | 4223 | 10.3 | 84.028668254259 | 4285.1 | 0 | 237.90000000002055 | 60 |  | 48.87731481481482 | 4223 | 2014 | 6 | 2014_06_Asomata_english.xlsx
21 | 485 | 0 | 485 | 0 | 0 | 5 | 485 | 54 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 42.083 | 3899.61 | -240.00000000002 | 4609.99999999998 | 4850 | 10 | 86.75413711583924 | 4474.9 | 0 | 135.09999999997945 | 0 |  | 56.13425925925926 | 4850 | 2014 | 6 | 2014_06_Asomata_english.xlsx
22 | 435 | 0 | 435 | 0 | 0 | 4 | 435 | 53 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.45 | 7880.000000000014 | 42.1175 | 3939.975 | 360.00000000001364 | 4710.000000000014 | 4350 | 10 | 86.44758539458186 | 4431.1 | 0 | 278.9000000000142 | 0 |  | 50.34722222222222 | 4350 | 2014 | 6 | 2014_06_Asomata_english.xlsx
23 | 440 | 0 | 440 | 0 | 0 | 4 | 440 | 44 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.5 | 8000.000000000007 | 42.062 | 3875.04 | 119.99999999999363 | 4563.999999999994 | 4444 | 10.1 | 85.49097262667443 | 4504.1 | 0 | 59.89999999999418 | 0 |  | 51.43518518518518 | 4444 | 2014 | 6 | 2014_06_Asomata_english.xlsx
24 | 515 | 40 | 555 | 0 | 0 | 4 | 555 | 107 | 10.400000000001455 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 24 | 84.6 | 8239.999999999993 | 41.901 | 3686.67 | 239.99999999998545 | 5845.499999999985 | 5605.5 | 10.1 | 85.29028959233953 | 5655 | 0 | 190.49999999998545 | 0 |  | 64.87847222222223 | 5605.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
25 | 525 | 0 | 525 | 0 | 0 | 3 | 525 | 53 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84 | 6800.000000000007 | 41.749 | 3508.8300000000063 | -1439.9999999999854 | 3862.5000000000146 | 5302.5 | 10.1 | 86.50872230080151 | 3956.6 | 0 | 25.900000000014643 | 120 |  | 61.37152777777778 | 5302.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
26 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 53 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84 | 6800.000000000007 | 41.978 | 3776.76 | 0 | 5252 | 5252 | 10.1 | 86.50872230080151 | 5219.5 | 0 | 132.5 | 100 |  | 60.78703703703704 | 5252 | 2014 | 6 | 2014_06_Asomata_english.xlsx
27 | 515 | 0 | 515 | 0 | 0 | 3 | 515 | 54 | 10.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84 | 6800.000000000007 | 41.941 | 3733.47 | 0 | 5201.5 | 5201.5 | 10.1 | 86.50872230080151 | 5161.1 | 0 | 40.400000000000546 | 0 |  | 60.2025462962963 | 5201.5 | 2014 | 6 | 2014_06_Asomata_english.xlsx
28 | 470 | 0 | 470 | 0 | 0 | 4 | 470 | 54 | 9.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.6 | 8239.999999999993 | 41.602 | 3336.84 | 1439.9999999999854 | 6186.999999999985 | 4747 | 10.1 | 85.29028959233953 | 6051.7 | 0 | 135.29999999998563 | 0 |  | 54.942129629629626 | 4747 | 2014 | 6 | 2014_06_Asomata_english.xlsx
29 | 560 | 0 | 560 | 0 | 0 | 4 | 560 | 44 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.4 | 7760.00000000002 | 41.871 | 3651.57 | -479.9999999999727 | 5064.000000000027 | 5544 | 9.9 | 87.4237659615018 | 4961.25 | 0 | 102.75000000002728 | 0 |  | 64.16666666666667 | 5544 | 2014 | 6 | 2014_06_Asomata_english.xlsx
30 | 250 | 285 | 535 | 0 | 0 | 5 | 535 | 53 | 5.099999999998545 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.65 | 8360.00000000002 | 41.961 | 3756.8699999999935 | 600 | 5950 | 5350 | 10 | 86.04220398593199 | 5731.55 | 0 | 218.45000000000073 | 0 |  | 61.9212962962963 | 5350 | 2014 | 6 | 2014_06_Asomata_english.xlsx
1 | 580 | 0 | 580 | 0 | 0 | 5 | 580 | 53 | 11.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.35 | 7639.999999999993 | 42.05 | 3861 | -720.0000000000273 | 5137.999999999973 | 5858 | 10.1 | 85.79377418261309 | 4978.6 | 0 | 159.39999999997235 | 0 |  | 67.80092592592592 | 5858 | 2014 | 7 | 2014_07_Asomata_english.xlsx
2 | 55 | 575 | 630 | 0 | 0 | 4 | 630 | 55 | 1 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.25 | 7400.000000000007 | 42.16 | 3989.7 | -239.99999999998545 | 6468.000000000015 | 6708 | 10.647619047619047 | 81.57392215600555 | 6497.2 | 0 | 10.800000000013824 | 40 |  | 77.63888888888889 | 6708 | 2014 | 7 | 2014_07_Asomata_english.xlsx
3 | 570 | 925 | 1495 | 0 | 0 | 3 | 1495 | 110 | 14.5 | 22.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.05 | 6920 | 41.7499 | 3509.8829999999975 | -480.0000000000073 | 14619.5 | 15099.5 | 10.1 | 86.4058581839159 | 14644.8 | 0 | 24.69999999999345 | 50 |  | 174.7627314814815 | 15099.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
4 | 360 | 165 | 525 | 0 | 0 | 3 | 525 | 44 | 8.099999999998545 | 4.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.4 | 7760.00000000002 | 41.832 | 3605.94 | 840.00000000002 | 6195.000000000019 | 5355 | 10.2 | 84.85247872734 | 5905.7 | 0 | 289.3000000000193 | 0 |  | 61.97916666666666 | 5355 | 2014 | 7 | 2014_07_Asomata_english.xlsx
5 | 830 | 300 | 1130 | 0 | 0 | 3 | 1130 | 108 | 16.19999999999709 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.3 | 7520 | 41.121 | 2774.07 | -240.00000000002 | 11173 | 11413 | 10.1 | 85.89518526320718 | 11143.25 | 0 | 29.74999999997999 | 0 |  | 132.09490740740742 | 11413 | 2014 | 7 | 2014_07_Asomata_english.xlsx
6 | 640 | 105 | 745 | 0 | 0 | 3 | 745 | 108 | 13.10000000000582 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 85.25 | 9800.000000000007 | 42.118 | 3940.56 | 2280.0000000000073 | 9655.500000000007 | 7375.5 | 9.9 | 85.7056110235301 | 9352.8 | 0 | 302.7000000000062 | 0 |  | 85.36458333333333 | 7375.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
7 | 655 | 190 | 845 | 0 | 0 | 4 | 845 | 100 | 13.299999999995634 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.25 | 7400.000000000007 | 42.148 | 3975.66 | -2400 | 6134.5 | 8534.5 | 10.1 | 85.99683637002754 | 6153.9 | 0 | 40.600000000000364 | 60 |  | 98.77893518518519 | 8534.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
8 | 440 | 435 | 875 | 0 | 0 | 4 | 875 | 108 | 8.400000000001455 | 8.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84 | 6800.000000000007 | 41.698 | 3449.16 | -600 | 8237.5 | 8837.5 | 10.1 | 86.50872230080151 | 8278.2 | 0 | 19.30000000000109 | 60 |  | 102.28587962962963 | 8837.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
9 | 305 | 295 | 600 | 0 | 0 | 4 | 600 | 55 | 4.69999999999709 | 6.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.15 | 7160.00000000002 | 41.951 | 3745.17 | 360.00000000001273 | 6420.000000000013 | 6060 | 10.1 | 86.20086207909047 | 6380.2 | 0 | 99.80000000001291 | 60 |  | 70.13888888888889 | 6060 | 2014 | 7 | 2014_07_Asomata_english.xlsx
10 | 635 | 0 | 635 | 0 | 0 | 4 | 635 | 53 | 14.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.25 | 7400.000000000007 | 41.899 | 3684.33 | 239.99999999998727 | 6653.499999999987 | 6413.5 | 10.1 | 85.99683637002754 | 6643 | 0 | 70.49999999998818 | 60 |  | 74.23032407407408 | 6413.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
11 | 680 | 0 | 680 | 0 | 0 | 3 | 680 | 55 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.2 | 7280.000000000014 | 42 | 3802.5 | -119.99999999999363 | 6748.000000000006 | 6868 | 10.1 | 86.09872835624795 | 6749.6 | 0 | 58.400000000006 | 60 |  | 79.49074074074075 | 6868 | 2014 | 7 | 2014_07_Asomata_english.xlsx
12 | 45 | 575 | 620 | 0 | 0 | 4 | 620 | 54 | 1.6500000000014552 | 11.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.95 | 9080.000000000015 | 41.699 | 3450.33 | 1800 | 8062 | 6262 | 10.1 | 84.59525812883966 | 8044.6 | 0 | 17.400000000000546 | 0 |  | 72.47685185185185 | 6262 | 2014 | 7 | 2014_07_Asomata_english.xlsx
13 | 255 | 495 | 750 | 0 | 0 | 4 | 750 | 100 | 5.400000000001455 | 10.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 13 | 84.45 | 7880.000000000014 | 42.061 | 3873.87 | -1200 | 6412.5 | 7612.5 | 10.15 | 85.17003487150922 | 6190.4 | 0 | 222.09999999999945 | 0 |  | 88.10763888888889 | 7612.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
14 | 670 | 10 | 680 | 0 | 0 | 5 | 680 | 100 | 12.44999999999709 | 0.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84 | 6800.000000000007 | 42.15 | 3978 | -1080.0000000000064 | 5787.999999999994 | 6868 | 10.1 | 86.50872230080151 | 5628.3 | 0 | 159.69999999999345 | 0 |  | 79.49074074074075 | 6868 | 2014 | 7 | 2014_07_Asomata_english.xlsx
15 | 280 | 350 | 630 | 0 | 0 | 2 | 630 | 50 | 6 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.7 | 8480.000000000015 | 41.97 | 3767.4 | 1680.0000000000073 | 8043.000000000007 | 6363 | 10.1 | 85.09054652537853 | 7818.3 | 0 | 224.700000000008 | 0 |  | 73.64583333333333 | 6363 | 2014 | 7 | 2014_07_Asomata_english.xlsx
16 | 0 | 655 | 655 | 0 | 0 | 4 | 655 | 50 | 0 | 13.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.9 | 8960.00000000002 | 42.099 | 3918.33 | 480.00000000000546 | 7095.5000000000055 | 6615.5 | 10.1 | 84.6938540007847 | 6664.9 | 0 | 430.6000000000058 | 0 |  | 76.56828703703704 | 6615.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
17 | 0 | 625 | 625 | 0 | 0 | 3 | 625 | 55 | 0 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.85 | 8839.999999999993 | 41.982 | 3781.44 | -120.00000000002728 | 6067.499999999973 | 6187.5 | 9.9 | 86.50566340181277 | 5876.5 | 0 | 190.99999999997272 | 0 |  | 71.61458333333333 | 6187.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
18 | 0 | 545 | 545 | 0 | 0 | 4 | 545 | 50 | 0 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.6 | 8239.999999999993 | 41.95 | 3744 | -600 | 5040.75 | 5640.75 | 10.35 | 83.23013766981926 | 4993.2 | 0 | 47.55000000000018 | 0 |  | 65.28645833333333 | 5640.75 | 2014 | 7 | 2014_07_Asomata_english.xlsx
19 | 0 | 605 | 605 | 0 | 0 | 4 | 605 | 50 | 0 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.55 | 8120 | 41.999 | 3801.3300000000063 | -119.99999999999272 | 6081.250000000007 | 6201.25 | 10.25 | 84.14089593304864 | 6124.7 | 0 | 16.550000000007458 | 60 |  | 71.77372685185185 | 6201.25 | 2014 | 7 | 2014_07_Asomata_english.xlsx
20 | 140 | 685 | 825 | 0 | 0 | 4 | 825 | 100 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.4 | 7760.00000000002 | 41.532 | 3254.94 | -359.99999999998 | 7807.50000000002 | 8167.5 | 9.9 | 87.4237659615018 | 7300 | 0 | 507.50000000002 | 0 |  | 94.53125 | 8167.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
21 | 0 | 675 | 675 | 0 | 0 | 3 | 675 | 50 | 0 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.5 | 8000.000000000007 | 41.88 | 3662.1 | 239.99999999998727 | 7192.499999999988 | 6952.5 | 10.3 | 83.83095374071958 | 7099.2 | 0 | 153.29999999998745 | 60 |  | 80.46875 | 6952.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
22 | 640 | 0 | 640 | 0 | 0 | 3 | 640 | 50 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.9 | 8960.00000000002 | 42.14 | 3966.3 | 960.0000000000127 | 7296.000000000013 | 6336 | 9.9 | 86.40484095029548 | 7000.7 | 0 | 295.3000000000138 | 0 |  | 73.33333333333333 | 6336 | 2014 | 7 | 2014_07_Asomata_english.xlsx
23 | 10 | 630 | 640 | 0 | 0 | 3 | 640 | 50 | 0.3000000000029104 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 84.9 | 8960.00000000002 | 42 | 3802.5 | 0 | 6336 | 6336 | 9.9 | 86.40484095029548 | 6241.5 | 0 | 94.5 | 0 |  | 73.33333333333333 | 6336 | 2014 | 7 | 2014_07_Asomata_english.xlsx
24 | 0 | 675 | 675 | 0 | 0 | 3 | 675 | 50 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.9 | 8960.00000000002 | 42.04 | 3849.3 | 0 | 6615 | 6615 | 9.8 | 87.2865230008087 | 6416.7 | 0 | 198.300000000002 | 0 |  | 76.5625 | 6615 | 2014 | 7 | 2014_07_Asomata_english.xlsx
25 | 745 | 0 | 745 | 0 | 0 | 3 | 745 | 53 | 14.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.1 | 7039.999999999993 | 42.07 | 3884.4 | -1920.0000000000273 | 5604.499999999973 | 7524.5 | 10.1 | 86.3032383998495 | 5641.35 | 0 | 53.14999999997235 | 90 |  | 87.08912037037037 | 7524.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
26 | 545 | 165 | 710 | 0 | 0 | 3 | 710 | 108 | 11 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84.05 | 6920 | 41.92 | 3708.9 | -119.99999999999272 | 6909.000000000007 | 7029 | 9.9 | 88.15143107652027 | 6628.4 | 0 | 280.60000000000764 | 0 |  | 81.35416666666667 | 7029 | 2014 | 7 | 2014_07_Asomata_english.xlsx
27 | 0 | 675 | 675 | 0 | 0 | 5 | 675 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 83.65 | 5960.00000000002 | 42.08 | 3896.1 | -959.99999999998 | 6060.00000000002 | 7020 | 10.4 | 84.71927232431433 | 6106.4 | 0 | 13.600000000020373 | 60 |  | 81.25 | 7020 | 2014 | 7 | 2014_07_Asomata_english.xlsx
28 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 54 | 0 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.5 | 8000.000000000007 | 41.98 | 3779.1 | 2039.9999999999873 | 8605.999999999989 | 6566 | 9.8 | 88.1080432172869 | 8244 | 0 | 361.9999999999891 | 0 |  | 75.99537037037038 | 6566 | 2014 | 7 | 2014_07_Asomata_english.xlsx
29 | 340 | 295 | 635 | 0 | 0 | 5 | 635 | 98 | 7.400000000001455 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 29 | 84.8 | 8720 | 41.64 | 3381.3 | 719.9999999999927 | 7006.499999999993 | 6286.5 | 9.9 | 86.60672141980554 | 6796.3 | 0 | 210.19999999999345 | 0 |  | 72.76041666666667 | 6286.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
30 | 360 | 300 | 660 | 0 | 0 | 5 | 660 | 49 | 7.599999999998545 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.3 | 7520 | 41.58 | 3311.1 | -1200 | 5598 | 6798 | 10.3 | 84.22731758819344 | 5582.8 | 0 | 15.199999999999818 | 0 |  | 78.68055555555556 | 6798 | 2014 | 7 | 2014_07_Asomata_english.xlsx
31 | 605 | 30 | 635 | 0 | 0 | 4 | 635 | 50 | 12.099999999998545 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 85.1 | 9439.999999999993 | 41.91 | 3697.2 | 1919.9999999999927 | 8206.499999999993 | 6286.5 | 9.9 | 86.0038904122431 | 7644.2 | 0 | 562.299999999992 | 0 |  | 72.76041666666667 | 6286.5 | 2014 | 7 | 2014_07_Asomata_english.xlsx
1 | 45 | 650 | 695 | 0 | 0 | 4 | 695 | 90 | 1.3000000000029104 | 14.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.9 | 8960.00000000002 | 41.95 | 3744 | -479.9999999999727 | 6539.500000000027 | 7019.5 | 10.1 | 84.6938540007847 | 6483.56 | 0 | 115.9400000000278 | 60 |  | 81.24421296296296 | 7019.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
2 | 0 | 660 | 660 | 0 | 0 | 4 | 660 | 50 | 0 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.7 | 8480.000000000015 | 41.93 | 3720.6 | -480.00000000000546 | 6185.9999999999945 | 6666 | 10.1 | 85.09054652537853 | 5982.9 | 0 | 203.0999999999949 | 0 |  | 77.15277777777777 | 6666 | 2014 | 8 | 2014_08_Asomata_english.xlsx
3 | 0 | 710 | 710 | 0 | 0 | 4 | 710 | 54 | 0 | 14.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 3 | 84.5 | 8000.000000000007 | 42.08 | 3896.1 | -480.0000000000073 | 6690.999999999993 | 7171 | 10.1 | 85.49097262667443 | 6657.6 | 0 | 63.39999999999236 | 30 |  | 82.99768518518519 | 7171 | 2014 | 8 | 2014_08_Asomata_english.xlsx
4 | 730 | 30 | 760 | 0 | 0 | 3 | 760 | 55 | 13.599999999998545 | 0.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.55 | 8120 | 42.12 | 3942.9 | 119.99999999999272 | 7795.999999999993 | 7676 | 10.1 | 85.39051319938106 | 7634.76 | 0 | 161.2399999999925 | 0 |  | 88.8425925925926 | 7676 | 2014 | 8 | 2014_08_Asomata_english.xlsx
5 | 380 | 315 | 695 | 0 | 0 | 3 | 695 | 50 | 7.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.5 | 8000.000000000007 | 42 | 3802.5 | -119.99999999999272 | 6899.500000000007 | 7019.5 | 10.1 | 85.49097262667443 | 6767.1 | 0 | 132.40000000000782 | 0 |  | 81.24421296296296 | 7019.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
6 | 365 | 260 | 625 | 0 | 0 | 4 | 625 | 50 | 7.30000000000291 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84 | 6800.000000000007 | 41.65 | 3393 | -1200 | 5050 | 6250 | 10 | 87.37380952380953 | 4898.3 | 0 | 151.7 | 0 |  | 72.33796296296296 | 6250 | 2014 | 8 | 2014_08_Asomata_english.xlsx
7 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 55 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 84 | 6800.000000000007 | 42 | 3802.5 | 0 | 6767 | 6767 | 10.1 | 86.50872230080151 | 6811.2 | 0 | 15.799999999999272 | 60 |  | 78.32175925925925 | 6767 | 2014 | 8 | 2014_08_Asomata_english.xlsx
8 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 50 | 0 | 14.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.7 | 8480.000000000015 | 42.05 | 3861 | 1680.0000000000073 | 8447.000000000007 | 6767 | 10.1 | 85.09054652537853 | 8312.85 | 0 | 134.15000000000873 | 0 |  | 78.32175925925925 | 6767 | 2014 | 8 | 2014_08_Asomata_english.xlsx
9 | 0 | 545 | 545 | 0 | 0 | 4 | 545 | 50 | 0 | 10.85000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 83.7 | 6080.000000000014 | 41.751 | 3511.1699999999937 | -2400 | 4314.177419354838 | 5504.5 | 10.1 | 87.13108720944037 | 4224.5 | 1209.6774193548388 | 149.6774193548381 | 60 |  | 63.70949074074074 | 5504.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
10 | 0 | 540 | 540 | 0 | 0 | 3 | 540 | 50 | 0 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.8 | 6320 | 41.849 | 3625.83 | 239.99999999998636 | 5693.999999999986 | 5454 | 10.1 | 86.9226396323843 | 5613.7 | 0 | 140.29999999998654 | 60 |  | 63.125 | 5454 | 2014 | 8 | 2014_08_Asomata_english.xlsx
11 | 590 | 0 | 590 | 0 | 0 | 4 | 590 | 55 | 11.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 83.65 | 5960.00000000002 | 42.101 | 3920.67 | -359.99999999998 | 5599.00000000002 | 5959 | 10.1 | 87.23568635374941 | 5482.3 | 0 | 116.70000000002074 | 0 |  | 68.9699074074074 | 5959 | 2014 | 8 | 2014_08_Asomata_english.xlsx
12 | 400 | 260 | 660 | 0 | 0 | 4 | 660 | 50 | 8.099999999998545 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.9 | 8960.00000000002 | 41.802 | 3570.84 | 3000 | 9699 | 6699 | 10.15 | 84.27664289733254 | 9627.6 | 0 | 71.40000000000146 | 0 |  | 77.53472222222223 | 6699 | 2014 | 8 | 2014_08_Asomata_english.xlsx
13 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 53 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.85 | 8839.999999999993 | 42 | 3802.5 | -120.00000000002728 | 6200.749999999973 | 6320.75 | 9.65 | 88.74674276455404 | 6150.85 | 0 | 49.89999999997235 | 0 |  | 73.15682870370371 | 6320.75 | 2014 | 8 | 2014_08_Asomata_english.xlsx
14 | 630 | 0 | 630 | 0 | 0 | 4 | 630 | 54 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.95 | 9080.000000000015 | 41.7 | 3451.5 | 240.00000000002183 | 6414.000000000022 | 6174 | 9.8 | 87.18490888788575 | 6399.55 | 0 | 14.450000000020736 | 0 |  | 71.45833333333333 | 6174 | 2014 | 8 | 2014_08_Asomata_english.xlsx
15 | 0 | 625 | 625 | 0 | 0 | 3 | 625 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.5 | 8000.000000000007 | 41.63 | 3369.6 | -1080.0000000000073 | 5232.499999999993 | 6312.5 | 10.1 | 85.49097262667443 | 5212.2 | 0 | 80.2999999999929 | 60 |  | 73.0613425925926 | 6312.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
16 | 540 | 135 | 675 | 0 | 0 | 5 | 675 | 107 | 10.80000000000291 | 2.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.6 | 8239.999999999993 | 41.781 | 3546.2699999999936 | 239.99999999998545 | 6821.249999999985 | 6581.25 | 9.75 | 88.35199229565427 | 6555.4 | 0 | 265.8499999999858 | 0 |  | 76.171875 | 6581.25 | 2014 | 8 | 2014_08_Asomata_english.xlsx
17 | 0 | 530 | 530 | 0 | 0 | 4 | 530 | 49 | 0 | 10.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 85.1 | 9439.999999999993 | 41.26 | 2936.7 | 1200 | 6314.5 | 5114.5 | 9.65 | 88.23197047473643 | 5913 | 0 | 401.5 | 0 |  | 59.195601851851855 | 5114.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
18 | 335 | 255 | 590 | 0 | 0 | 4 | 590 | 49 | 7.19999999999709 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 85.2 | 9680.000000000015 | 41.2 | 2866.5 | 240.00000000002183 | 6199.000000000022 | 5959 | 10.1 | 84.10570223689035 | 6000.6 | 0 | 198.40000000002146 | 0 |  | 68.9699074074074 | 5959 | 2014 | 8 | 2014_08_Asomata_english.xlsx
19 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 49 | 0 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 85.1 | 9439.999999999993 | 41.41 | 3112.2 | -240.00000000002183 | 5919.499999999978 | 6159.5 | 9.7 | 87.77716650321717 | 5854.6 | 0 | 64.89999999997781 | 0 |  | 71.29050925925925 | 6159.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
20 | 0 | 655 | 655 | 0 | 0 | 4 | 655 | 50 | 0 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.95 | 9080.000000000015 | 41.829 | 3602.43 | -359.9999999999782 | 6059.000000000023 | 6419 | 9.8 | 87.18490888788575 | 5855.85 | 0 | 203.15000000002237 | 0 |  | 74.2939814814815 | 6419 | 2014 | 8 | 2014_08_Asomata_english.xlsx
21 | 0 | 630 | 630 | 0 | 0 | 4 | 630 | 53 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.95 | 9080.000000000015 | 42.078 | 3893.76 | 0 | 6205.5 | 6205.5 | 9.85 | 86.74234589860717 | 6044.4 | 0 | 161.1 | 0 |  | 71.82291666666667 | 6205.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
22 | 0 | 655 | 655 | 0 | 0 | 4 | 655 | 55 | 0 | 12.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85 | 9200.000000000007 | 42.071 | 3885.5699999999933 | 119.99999999999272 | 6506.249999999993 | 6386.25 | 9.75 | 87.53011329755516 | 6379.8 | 0 | 186.44999999999345 | 60 |  | 73.91493055555556 | 6386.25 | 2014 | 8 | 2014_08_Asomata_english.xlsx
23 | 260 | 380 | 640 | 0 | 0 | 4 | 640 | 55 | 5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.6 | 8239.999999999993 | 41.705 | 3457.35 | -960.0000000000146 | 5375.999999999985 | 6336 | 9.9 | 87.01332574572012 | 5140.25 | 0 | 235.74999999998545 | 0 |  | 73.33333333333333 | 6336 | 2014 | 8 | 2014_08_Asomata_english.xlsx
24 | 290 | 355 | 645 | 0 | 0 | 3 | 645 | 53 | 5.30000000000291 | 7.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 1 | 1 | Ασυμφωνία θέσεως πόλων Δ/Κ Ρ25 Μον. ΝοΙΙ | 24 | 84.3 | 7520 | 41.979 | 3777.93 | -719.9999999999927 | 5794.500000000007 | 6514.5 | 10.1 | 85.89518526320718 | 5745.1 | 0 | 49.40000000000691 | 0 |  | 75.39930555555556 | 6514.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
25 | 645 | 0 | 645 | 0 | 0 | 4 | 645 | 55 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.55 | 2 | 0 | Ασυμφωνία θέσεως πόλων Δ/Κ Ρ25 Μον. ΝοΙΙ | 25 | 84.6 | 8239.999999999993 | 42.051 | 3862.17 | 719.9999999999927 | 7008.749999999993 | 6288.75 | 9.75 | 88.35199229565427 | 6921.05 | 0 | 147.69999999999254 | 60 |  | 72.78645833333333 | 6288.75 | 2014 | 8 | 2014_08_Asomata_english.xlsx
26 | 20 | 645 | 665 | 0 | 0 | 3 | 665 | 53 | 0.2999999999956344 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.3 | 7520 | 41.951 | 3745.17 | -719.9999999999927 | 6222.250000000006 | 6942.25 | 10.439473684210524 | 83.10202194106105 | 6156.15 | 0 | 66.10000000000582 | 0 |  | 80.35011574074073 | 6942.25 | 2014 | 8 | 2014_08_Asomata_english.xlsx
27 | 285 | 305 | 590 | 0 | 0 | 3 | 590 | 53 | 5.599999999998545 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.7 | 8480.000000000015 | 41.839 | 3614.13 | 960.0000000000146 | 6653.500000000015 | 5693.5 | 9.65 | 89.05849947215783 | 6421.1 | 0 | 232.4000000000142 | 0 |  | 65.89699074074075 | 5693.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
28 | 345 | 245 | 590 | 0 | 0 | 3 | 590 | 53 | 6.600000000005821 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.4 | 7760.00000000002 | 41.811 | 3581.37 | -719.9999999999945 | 5091.5000000000055 | 5811.5 | 9.85 | 87.86754142323531 | 4783.35 | 0 | 308.1500000000051 | 0 |  | 67.26273148148148 | 5811.5 | 2014 | 8 | 2014_08_Asomata_english.xlsx
29 | 0 | 595 | 595 | 0 | 0 | 3 | 595 | 50 | 0 | 11.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.55 | 8120 | 41.941 | 3733.47 | 359.99999999998 | 6190.99999999998 | 5831 | 9.8 | 88.00450850140291 | 6117.4 | 0 | 73.59999999998035 | 0 |  | 67.48842592592592 | 5831 | 2014 | 8 | 2014_08_Asomata_english.xlsx
30 | 0 | 490 | 490 | 0 | 0 | 5 | 490 | 50 | 0 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.5 | 8000.000000000007 | 41.74 | 3498.3 | -119.99999999999272 | 4829.000000000007 | 4949 | 10.1 | 85.49097262667443 | 4870.32 | 0 | 18.680000000007567 | 60 |  | 57.280092592592595 | 4949 | 2014 | 8 | 2014_08_Asomata_english.xlsx
31 | 0 | 475 | 475 | 0 | 0 | 6 | 475 | 50 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.85 | 8839.999999999993 | 41.468 | 3180.06 | 839.9999999999854 | 5471.249999999985 | 4631.25 | 9.75 | 87.83651976184066 | 5270.6 | 0 | 200.64999999998508 | 0 |  | 53.60243055555556 | 4631.25 | 2014 | 8 | 2014_08_Asomata_english.xlsx
1 | 460 | 0 | 460 | 0 | 0 | 3 | 460 | 53 | 9.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.25 | 9800.000000000007 | 41.48 | 3194.1 | 960.0000000000146 | 5468.000000000015 | 4508 | 9.8 | 86.5801580747906 | 5231.8 | 0 | 236.20000000001437 | 0 |  | 52.175925925925924 | 4508 | 2014 | 9 | 2014_09_Asomata_english.xlsx
2 | 245 | 105 | 350 | 0 | 0 | 4 | 350 | 49 | 4.900000000001455 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 85 | 9200.000000000007 | 41.48 | 3194.1 | -600 | 2760 | 3360 | 9.6 | 88.89777131782945 | 2416 | 0 | 344 | 0 |  | 38.888888888888886 | 3360 | 2014 | 9 | 2014_09_Asomata_english.xlsx
3 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 48 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85.1 | 9439.999999999993 | 40.451 | 1990.17 | 239.99999999998545 | 1464.9999999999854 | 1225 | 9.8 | 86.88148113073535 | 1306.7 | 0 | 158.2999999999854 | 0 |  | 14.17824074074074 | 1225 | 2014 | 9 | 2014_09_Asomata_english.xlsx
4 | 125 | 80 | 205 | 0 | 0 | 3 | 205 | 53 | 2.8000000000029104 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.9 | 8960.00000000002 | 40.698 | 2279.16 | -479.9999999999727 | 1508.5000000000273 | 1988.5 | 9.7 | 88.18638406267272 | 1315.65 | 0 | 192.85000000002742 | 0 |  | 23.015046296296298 | 1988.5 | 2014 | 9 | 2014_09_Asomata_english.xlsx
5 | 130 | 0 | 130 | 0 | 0 | 4 | 130 | 48 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85 | 9200.000000000007 | 40.618 | 2185.56 | 239.99999999998727 | 1500.9999999999873 | 1261 | 9.7 | 87.9812994485735 | 1376.4 | 0 | 124.59999999998718 | 0 |  | 14.594907407407407 | 1261 | 2014 | 9 | 2014_09_Asomata_english.xlsx
6 | 0 | 190 | 190 | 0 | 0 | 4 | 190 | 48 | 0 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.9 | 8960.00000000002 | 41.2515 | 2926.754999999996 | -239.99999999998727 | 1641.0000000000127 | 1881 | 9.9 | 86.40484095029548 | 1590 | 0 | 51.00000000001273 | 0 |  | 21.770833333333332 | 1881 | 2014 | 9 | 2014_09_Asomata_english.xlsx
7 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 53 | 3.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 85.15 | 9560.00000000002 | 41.57 | 3299.4 | 600 | 2111.25 | 1511.25 | 9.75 | 87.22583712154974 | 1801.2 | 0 | 310.05 | 0 |  | 17.491319444444443 | 1511.25 | 2014 | 9 | 2014_09_Asomata_english.xlsx
8 | 0 | 170 | 170 | 0 | 0 | 4 | 170 | 53 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.15 | 9560.00000000002 | 41.8 | 3568.5 | 0 | 1708.5 | 1708.5 | 10.05 | 84.62208078956317 | 1600.6 | 0 | 107.9 | 0 |  | 19.774305555555557 | 1708.5 | 2014 | 9 | 2014_09_Asomata_english.xlsx
9 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 48 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.15 | 9560.00000000002 | 41.681 | 3429.2699999999936 | 0 | 1480.25 | 1480.25 | 9.55 | 89.05255622357171 | 1200.8 | 0 | 279.45 | 0 |  | 17.13252314814815 | 1480.25 | 2014 | 9 | 2014_09_Asomata_english.xlsx
10 | 240 | 0 | 240 | 0 | 0 | 3 | 240 | 53 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.9 | 8960.00000000002 | 41.98 | 3779.1 | -600 | 1778.4 | 2378.4 | 9.91 | 86.31765140342334 | 1649.8 | 0 | 128.6 | 0 |  | 27.52777777777778 | 2378.4 | 2014 | 9 | 2014_09_Asomata_english.xlsx
11 | 265 | 0 | 265 | 0 | 0 | 3 | 265 | 55 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.7 | 8480.000000000015 | 41.622 | 3360.24 | -480.00000000000546 | 2169.9999999999945 | 2650 | 10 | 85.94145199063232 | 1992.9 | 0 | 177.09999999999445 | 0 |  | 30.671296296296298 | 2650 | 2014 | 9 | 2014_09_Asomata_english.xlsx
12 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 53 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.7 | 8480.000000000015 | 41.638 | 3378.96 | 0 | 2537.25 | 2537.25 | 9.95 | 86.37331858355007 | 2332.5 | 0 | 204.75 | 0 |  | 29.366319444444443 | 2537.25 | 2014 | 9 | 2014_09_Asomata_english.xlsx
13 | 0 | 55 | 55 | 0 | 0 | 5 | 55 | 35 | 0 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 84.95 | 9080.000000000015 | 40.78 | 2375.1 | 600 | 1155.5 | 555.5 | 10.1 | 84.59525812883966 | 1035 | 0 | 120.5 | 0 |  | 6.429398148148148 | 555.5 | 2014 | 9 | 2014_09_Asomata_english.xlsx
14 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 35 | 3.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 85.15 | 9560.00000000002 | 40.929 | 2549.43 | 480.00000000000546 | 1943.0000000000055 | 1463 | 10.45 | 81.38295807991484 | 1759.5 | 0 | 183.50000000000546 | 0 |  | 16.93287037037037 | 1463 | 2014 | 9 | 2014_09_Asomata_english.xlsx
15 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 55 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.05 | 9320 | 41.149 | 2806.83 | -240.00000000002 | 1541.99999999998 | 1782 | 9.9 | 86.10377878670562 | 1379.7 | 0 | 162.29999999997995 | 0 |  | 20.625 | 1782 | 2014 | 9 | 2014_09_Asomata_english.xlsx
16 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 53 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.85 | 8839.999999999993 | 41.252 | 2927.34 | -480.0000000000073 | 1549.4999999999927 | 2029.5 | 9.9 | 86.50566340181277 | 1460 | 0 | 89.49999999999272 | 0 |  | 23.489583333333332 | 2029.5 | 2014 | 9 | 2014_09_Asomata_english.xlsx
17 | 220 | 0 | 220 | 0 | 0 | 4 | 220 | 40 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.8 | 8720 | 41.298 | 2981.16 | -119.99999999999272 | 2003.0000000000073 | 2123 | 9.65 | 88.85041886591449 | 1736.5 | 0 | 266.5000000000073 | 0 |  | 24.57175925925926 | 2123 | 2014 | 9 | 2014_09_Asomata_english.xlsx
18 | 220 | 0 | 220 | 0 | 0 | 4 | 220 | 53 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.25 | 7400.000000000007 | 41.57 | 3299.4 | -1319.9999999999927 | 902.0000000000073 | 2222 | 10.1 | 85.99683637002754 | 846.8 | 0 | 55.20000000000732 | 0 |  | 25.71759259259259 | 2222 | 2014 | 9 | 2014_09_Asomata_english.xlsx
19 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 40 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.55 | 8120 | 41.303 | 2987.0099999999916 | 719.9999999999927 | 1881.4999999999927 | 1161.5 | 10.1 | 85.39051319938106 | 1755.6 | 0 | 125.89999999999281 | 0 |  | 13.443287037037036 | 1161.5 | 2014 | 9 | 2014_09_Asomata_english.xlsx
20 | 0 | 170 | 170 | 0 | 0 | 4 | 170 | 55 | 0 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.85 | 8839.999999999993 | 41.352 | 3044.34 | 719.9999999999927 | 2385.9999999999927 | 1666 | 9.8 | 87.38837425285168 | 2138.4 | 0 | 247.59999999999263 | 0 |  | 19.28240740740741 | 1666 | 2014 | 9 | 2014_09_Asomata_english.xlsx
21 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 54 | 0 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.3 | 9920 | 41.151 | 2809.17 | 1080.0000000000073 | 2274.0000000000073 | 1194 | 9.95 | 85.17645966553323 | 2095.1 | 0 | 178.90000000000737 | 0 |  | 13.819444444444445 | 1194 | 2014 | 9 | 2014_09_Asomata_english.xlsx
22 | 180 | 0 | 180 | 0 | 0 | 2 | 180 | 53 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 85.15 | 9560.00000000002 | 41.3 | 2983.5 | -359.99999999998 | 1458.00000000002 | 1818 | 10.1 | 84.20315959753565 | 1270.2 | 0 | 187.80000000001996 | 0 |  | 21.041666666666668 | 1818 | 2014 | 9 | 2014_09_Asomata_english.xlsx
23 | 0 | 190 | 190 | 0 | 0 | 3 | 190 | 35 | 0 | 5.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 85.15 | 9560.00000000002 | 41.602 | 3336.84 | 0 | 1952.25 | 1952.25 | 10.275 | 82.76904252409828 | 1854.2 | 0 | 98.05 | 0 |  | 22.59548611111111 | 1952.25 | 2014 | 9 | 2014_09_Asomata_english.xlsx
24 | 0 | 170 | 170 | 0 | 0 | 4 | 170 | 40 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.25 | 9800.000000000007 | 41.351 | 3043.17 | 239.99999999998727 | 2050.4999999999873 | 1810.5 | 10.65 | 79.67000461342235 | 1949.1 | 0 | 101.39999999998736 | 0 |  | 20.95486111111111 | 1810.5 | 2014 | 9 | 2014_09_Asomata_english.xlsx
25 | 0 | 190 | 190 | 0 | 0 | 4 | 190 | 54 | 0 | 3.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 85.15 | 9560.00000000002 | 41.451 | 3160.17 | -239.99999999998727 | 1631.5000000000127 | 1871.5 | 9.85 | 86.34029562792995 | 1598.7 | 0 | 32.80000000001269 | 0 |  | 21.66087962962963 | 1871.5 | 2014 | 9 | 2014_09_Asomata_english.xlsx
26 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 35 | 4.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.8 | 8720 | 41.942 | 3734.64 | -840.00000000002 | 963.74999999998 | 1803.75 | 9.75 | 87.93913251857178 | 715.4 | 0 | 248.34999999998 | 0 |  | 20.87673611111111 | 1803.75 | 2014 | 9 | 2014_09_Asomata_english.xlsx
27 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 35 | 0 | 3.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 85.15 | 9560.00000000002 | 42.002 | 3804.84 | 840.00000000002 | 2058.75000000002 | 1218.75 | 9.75 | 87.22583712154974 | 1867.5 | 0 | 191.25000000002 | 0 |  | 14.105902777777779 | 1218.75 | 2014 | 9 | 2014_09_Asomata_english.xlsx
28 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 53 | 0 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.55 | 8120 | 41.852 | 3629.34 | -1440.00000000002 | -26.00000000002001 | 1414 | 10.1 | 85.39051319938106 | 0 | 0 | 33.99999999997999 | 60 |  | 16.36574074074074 | 1414 | 2014 | 9 | 2014_09_Asomata_english.xlsx
29 | 35 | 190 | 225 | 0 | 0 | 3 | 225 | 53 | 0 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84 | 6800.000000000007 | 41.703 | 3455.01 | -1319.9999999999927 | 2096.489361702135 | 2225 | 9.88888888888889 | 88.35553772070625 | 1941.8 | 1191.4893617021276 | 154.68936170213487 | 0 |  | 25.752314814814813 | 2225 | 2014 | 9 | 2014_09_Asomata_english.xlsx
30 | 220 | 0 | 220 | 0 | 0 | 4 | 220 | 55 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.15 | 7160.00000000002 | 41.701 | 3452.67 | 360.00000000001273 | 2637.0000000000127 | 2277 | 10.35 | 84.1187156520593 | 2655.4 | 0 | 41.6000000000131 | 60 |  | 26.354166666666668 | 2277 | 2014 | 9 | 2014_09_Asomata_english.xlsx
1 | 0 | 195 | 195 | 0 | 0 | 4 | 195 | 55 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 1 | 84 | 6800.000000000007 | 41.801 | 3569.67 | -360.00000000001273 | 1716.7499999999873 | 2076.75 | 10.65 | 82.04113570310753 | 1750 | 0 | 26.749999999987267 | 60 |  | 24.036458333333332 | 2076.75 | 2014 | 10 | 2014_10_Asomata_english.xlsx
2 | 120 | 115 | 235 | 0 | 0 | 3 | 235 | 55 | 2.599999999998545 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.95 | 6680.000000000014 | 41.6415 | 3383.0549999999957 | -119.99999999999363 | 2183.0000000000064 | 2303 | 9.8 | 89.2632142249033 | 2092.5 | 0 | 90.50000000000637 | 0 |  | 26.65509259259259 | 2303 | 2014 | 10 | 2014_10_Asomata_english.xlsx
3 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 55 | 0 | 2.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 84.1 | 7039.999999999993 | 40.999 | 2631.3300000000063 | 359.9999999999791 | 1631.999999999979 | 1272 | 10.6 | 82.23233092815849 | 1511.1 | 0 | 180.89999999997917 | 60 |  | 14.722222222222221 | 1272 | 2014 | 10 | 2014_10_Asomata_english.xlsx
4 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 39 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 85 | 9200.000000000007 | 40.79 | 2386.8 | 2160.0000000000146 | 3624.5000000000146 | 1464.5 | 10.1 | 84.49689154962007 | 3620.8 | 0 | 13.70000000001437 | 10 |  | 16.95023148148148 | 1464.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
5 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 55 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480.000000000015 | 41.998 | 3800.16 | -719.9999999999927 | 4359.429487179495 | 3792.25 | 9.85 | 87.25020506663179 | 4314.3 | 1287.179487179487 | 45.12948717949439 | 0 |  | 43.891782407407405 | 3792.25 | 2014 | 10 | 2014_10_Asomata_english.xlsx
6 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 39 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.6 | 8239.999999999993 | 41.378 | 3074.76 | -240.00000000002183 | 3029.457446808489 | 1503.5 | 9.7 | 88.80741493635354 | 2839.7 | 1765.9574468085107 | 189.75744680848902 | 0 |  | 17.40162037037037 | 1503.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
7 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 54 | 5.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.55 | 8120 | 40.947 | 2570.49 | -119.99999999999272 | 2354.5000000000073 | 2474.5 | 10.1 | 85.39051319938106 | 2226.5 | 0 | 188.00000000000728 | 60 |  | 28.640046296296298 | 2474.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
8 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 40 | 4.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.6 | 8239.999999999993 | 40.85 | 2457 | 119.99999999999272 | 1735.9999999999927 | 1616 | 10.1 | 85.29028959233953 | 1635.2 | 0 | 100.79999999999268 | 0 |  | 18.703703703703702 | 1616 | 2014 | 10 | 2014_10_Asomata_english.xlsx
9 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 40 | 0 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.55 | 8120 | 40.71 | 2293.2 | -119.99999999999272 | 2079.6596858638814 | 985 | 9.85 | 87.55778510799479 | 2000.2 | 1214.6596858638743 | 79.4596858638813 | 0 |  | 11.400462962962964 | 985 | 2014 | 10 | 2014_10_Asomata_english.xlsx
10 | 160 | 0 | 160 | 0 | 0 | 4 | 160 | 53 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.55 | 8120 | 40.949 | 2572.83 | 0 | 1584 | 1584 | 9.9 | 87.11557407209581 | 1542.8 | 0 | 41.2 | 0 |  | 18.333333333333332 | 1584 | 2014 | 10 | 2014_10_Asomata_english.xlsx
11 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 53 | 4.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.85 | 8839.999999999993 | 41.501 | 3218.6699999999937 | 719.9999999999927 | 3600.8031088082826 | 1715 | 9.8 | 87.38837425285168 | 3436.5 | 1165.80310880829 | 164.30310880828256 | 0 |  | 19.849537037037038 | 1715 | 2014 | 10 | 2014_10_Asomata_english.xlsx
12 | 165 | 125 | 290 | 0 | 0 | 4 | 290 | 70 | 4.400000000001455 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.85 | 8839.999999999993 | 41.69 | 3439.8 | 0 | 4063.6363636363635 | 2900 | 10 | 85.64060676779464 | 3993.1 | 1163.6363636363635 | 70.53636363636315 | 0 |  | 33.56481481481482 | 2900 | 2014 | 10 | 2014_10_Asomata_english.xlsx
13 | 90 | 45 | 135 | 0 | 0 | 3 | 135 | 53 | 1.5999999999985448 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.8 | 8720 | 41.3 | 2983.5 | -119.99999999999272 | 2373.033678756484 | 1363.5 | 10.1 | 84.89173683723513 | 2255.7 | 1129.5336787564765 | 117.333678756484 | 0 |  | 15.78125 | 1363.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
14 | 375 | 105 | 480 | 0 | 0 | 4 | 480 | 107 | 7.94999999999709 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84.95 | 9080.000000000015 | 41.651 | 3394.17 | 360.00000000001455 | 5160.000000000015 | 4800 | 10 | 85.44121071012806 | 5088.1 | 0 | 71.90000000001419 | 0 |  | 55.55555555555556 | 4800 | 2014 | 10 | 2014_10_Asomata_english.xlsx
15 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 53 | 5.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 15 | 84.75 | 8600.000000000007 | 41.08 | 2726.1 | -480.0000000000073 | 2095.4999999999927 | 2575.5 | 10.1 | 84.9910254183313 | 2049.8 | 0 | 85.69999999999254 | 40 |  | 29.80902777777778 | 2575.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
16 | 45 | 115 | 160 | 0 | 0 | 0 | 160 | 80 | 1.2000000000043656 | 3.099999999998545 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | ΣΥΝΤΗΡΗΣΗ Κ.Γ. ΜΕΤΑΦ.150KV & Δ/Κ Ρ10 | 16 | 84.8 | 8720 | 41.329 | 3017.43 | 119.99999999999272 | 1695.9999999999927 | 1576 | 9.85 | 87.04634944731724 | 1547.6 | 0 | 148.39999999999281 | 0 |  | 18.24074074074074 | 1576 | 2014 | 10 | 2014_10_Asomata_english.xlsx
17 | 115 | 115 | 230 | 0 | 0 | 8 | 230 | 110 | 2.7999999999956344 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.8 | 8720 | 41.992 | 3793.14 | 0 | 2265.5 | 2265.5 | 9.85 | 87.04634944731724 | 2138.9 | 0 | 186.6 | 60 |  | 26.221064814814813 | 2265.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
18 | 0 | 115 | 115 | 0 | 0 | 4 | 115 | 35 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.85 | 8839.999999999993 | 41.228 | 2899.26 | 119.99999999999272 | 1235.4999999999927 | 1115.5 | 9.7 | 88.28928532762335 | 1175.3 | 0 | 60.19999999999277 | 0 |  | 12.91087962962963 | 1115.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
19 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 35 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 85.05 | 9320 | 41.269 | 2947.23 | 480.0000000000073 | 2656.126943005189 | 1072.5 | 9.75 | 87.4284523065011 | 2527.2 | 1103.6269430051814 | 128.9269430051886 | 0 |  | 12.413194444444445 | 1072.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
20 | 155 | 370 | 525 | 0 | 0 | 4 | 525 | 108 | 3.1000000000058208 | 7.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.6 | 8239.999999999993 | 41.502 | 3219.84 | -1080.0000000000073 | 5057.606382978716 | 5302.5 | 10.1 | 85.29028959233953 | 5026.45 | 835.1063829787234 | 31.156382978716465 | 0 |  | 61.37152777777778 | 5302.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
21 | 185 | 75 | 260 | 0 | 0 | 4 | 260 | 108 | 3.7999999999956344 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.5 | 8000.000000000007 | 41.6 | 3334.5 | -239.99999999998545 | 2334.0000000000146 | 2574 | 9.9 | 87.21806298276887 | 2299.5 | 0 | 94.50000000001455 | 60 |  | 29.791666666666668 | 2574 | 2014 | 10 | 2014_10_Asomata_english.xlsx
22 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 54 | 0 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.15 | 7160.00000000002 | 41.454 | 3163.68 | -839.9999999999873 | 1836.247422680425 | 1568 | 9.8 | 88.83966397947077 | 1730.1 | 1108.2474226804122 | 106.14742268042505 | 0 |  | 18.14814814814815 | 1568 | 2014 | 10 | 2014_10_Asomata_english.xlsx
23 | 0 | 135 | 135 | 0 | 0 | 4 | 135 | 40 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 84.55 | 8120 | 41.099 | 2748.33 | 959.99999999998 | 2384.24999999998 | 1424.25 | 10.55 | 81.7482638212084 | 2282.4 | 0 | 161.8499999999799 | 60 |  | 16.484375 | 1424.25 | 2014 | 10 | 2014_10_Asomata_english.xlsx
24 | 165 | 0 | 165 | 0 | 0 | 3 | 165 | 54 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.5 | 8000.000000000007 | 40.9 | 2515.5 | -119.99999999999272 | 1653.7500000000073 | 1773.75 | 10.75 | 80.32175102599179 | 970.9 | 0 | 682.8500000000073 | 0 |  | 20.52951388888889 | 1773.75 | 2014 | 10 | 2014_10_Asomata_english.xlsx
25 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 54 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.6 | 8239.999999999993 | 41.03 | 2667.6 | 239.99999999998545 | 2656.239361702113 | 1224.75 | 10.65 | 80.88562674954265 | 2255.7 | 1191.4893617021276 | 460.5393617021132 | 60 |  | 14.175347222222221 | 1224.75 | 2014 | 10 | 2014_10_Asomata_english.xlsx
26 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 55 | 0 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.9 | 8960.00000000002 | 40.85 | 2457 | 720.0000000000273 | 1578.5000000000273 | 858.5 | 10.1 | 84.6938540007847 | 1425 | 0 | 153.50000000002728 | 0 |  | 9.936342592592593 | 858.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
27 | 85 | 235 | 320 | 0 | 0 | 4 | 320 | 94 | 2.1999999999970896 | 5.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 84.7 | 8480.000000000015 | 41.699 | 3450.33 | -480.00000000000546 | 6092.042553191484 | 3088 | 9.65 | 89.05849947215783 | 6077.5 | 3484.0425531914893 | 74.54255319148433 | 60 |  | 35.74074074074074 | 3088 | 2014 | 10 | 2014_10_Asomata_english.xlsx
28 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 54 | 0 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.8 | 8720 | 40.569 | 2128.23 | 239.99999999998545 | 2257.9081632652915 | 997.5 | 10.5 | 81.65776591010237 | 2175.4 | 1020.408163265306 | 82.50816326529139 | 0 |  | 11.54513888888889 | 997.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
29 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 55 | 0 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 29 | 84.6 | 8239.999999999993 | 40.058 | 1530.36 | -480.0000000000073 | 2407.595744680844 | 1111 | 10.1 | 85.29028959233953 | 2394.4 | 1776.595744680851 | 13.195744680843745 | 0 |  | 12.858796296296296 | 1111 | 2014 | 10 | 2014_10_Asomata_english.xlsx
30 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 54 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.8 | 8720 | 40.3 | 1813.4999999999945 | 480.0000000000073 | 1812.5000000000073 | 1332.5 | 10.25 | 83.64941873717802 | 1380 | 0 | 432.5000000000073 | 0 |  | 15.422453703703704 | 1332.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
31 | 0 | 255 | 255 | 0 | 0 | 4 | 255 | 54 | 0 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 85 | 9200.000000000007 | 41.25 | 2925 | 480.0000000000073 | 3055.5000000000073 | 2575.5 | 10.1 | 84.49689154962007 | 2642.6 | 0 | 472.90000000000737 | 60 |  | 29.80902777777778 | 2575.5 | 2014 | 10 | 2014_10_Asomata_english.xlsx
1 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 54 | 0 | 1.3499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 84.6 | 8239.999999999993 | 41.15 | 2808 | -960.0000000000146 | 3341.88297872339 | 695.5 | 10.7 | 80.50765653108684 | 3164 | 3606.3829787234044 | 237.8829787233899 | 60 |  | 8.049768518518519 | 695.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
2 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 83.95 | 6680.000000000014 | 41.048 | 2688.66 | -1559.999999999979 | 2164.3617021276805 | 735 | 10.5 | 83.31233327657642 | 1971 | 2989.3617021276596 | 253.36170212768047 | 60 |  | 8.506944444444445 | 735 | 2014 | 11 | 2014_11_Asomata_english.xlsx
3 | 60 | 0 | 60 | 0 | 0 | 3 | 60 | 35 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.1 | 7039.999999999993 | 40.71 | 2293.2 | 359.9999999999791 | 938.9999999999791 | 579 | 9.65 | 90.32774174492019 | 938 | 0 | 60.99999999997908 | 60 |  | 6.701388888888889 | 579 | 2014 | 11 | 2014_11_Asomata_english.xlsx
4 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85.2 | 9680.000000000015 | 40.77 | 2363.400000000005 | 2640.000000000022 | 3549.000000000022 | 909 | 10.1 | 84.10570223689035 | 3124.4 | 0 | 484.6000000000222 | 60 |  | 10.520833333333334 | 909 | 2014 | 11 | 2014_11_Asomata_english.xlsx
5 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 55 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5 | 84.8 | 8720 | 40.7685 | 2361.645 | -960.0000000000146 | 1912.606382978709 | 787.5 | 10.5 | 81.65776591010237 | 1827 | 2085.1063829787236 | 145.606382978709 | 60 |  | 9.114583333333334 | 787.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
6 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.55 | 8120 | 40.8 | 2398.5 | -600 | 3573.502590673575 | 702 | 10.8 | 79.85594289942115 | 3430 | 3471.502590673575 | 203.502590673575 | 60 |  | 8.125 | 702 | 2014 | 11 | 2014_11_Asomata_english.xlsx
7 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 84.2 | 7280.000000000014 | 40.7 | 2281.5 | -839.9999999999864 | 2225.4787234042687 | 682.5 | 10.5 | 82.81877679981945 | 2117 | 2382.978723404255 | 168.47872340426875 | 60 |  | 7.899305555555555 | 682.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
8 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 54 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 85.2 | 9680.000000000015 | 40.67 | 2246.4 | 2400 | 4777.25 | 627.25 | 9.65 | 88.02772980234118 | 4693.9 | 1750 | 143.35000000000127 | 60 |  | 7.259837962962963 | 627.25 | 2014 | 11 | 2014_11_Asomata_english.xlsx
9 | 0 | 195 | 195 | 0 | 0 | 5 | 195 | 54 | 0 | 4.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 85.1 | 9439.999999999993 | 41.45 | 3159 | -240.00000000002183 | 3418.3457446808293 | 1881.75 | 9.65 | 88.23197047473643 | 3058.7 | 1776.595744680851 | 419.64574468082947 | 60 |  | 21.77951388888889 | 1881.75 | 2014 | 11 | 2014_11_Asomata_english.xlsx
10 | 180 | 0 | 180 | 0 | 0 | 2 | 180 | 54 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 85.2 | 9680.000000000015 | 41.1895 | 2854.214999999998 | 240.00000000002183 | 5589.106382978745 | 1764 | 9.8 | 86.68036659108087 | 5248.7 | 3585.106382978723 | 340.40638297874557 | 0 |  | 20.416666666666668 | 1764 | 2014 | 11 | 2014_11_Asomata_english.xlsx
11 | 0 | 110 | 110 | 0 | 0 | 4 | 110 | 40 | 0 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 11 | 85.05 | 9320 | 41.013 | 2647.71 | -360.00000000001455 | 4284.904255319135 | 1171.5 | 10.65 | 80.04013239327566 | 4219.4 | 3473.4042553191493 | 65.50425531913515 | 0 |  | 13.559027777777779 | 1171.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
12 | 205 | 80 | 285 | 0 | 0 | 4 | 285 | 110 | 3.900000000001455 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.7 | 8480.000000000015 | 41.1 | 2749.5 | -839.9999999999854 | 3304.6542553191634 | 2921.25 | 10.25 | 83.84531901525104 | 3343.4 | 1223.404255319149 | 21.254255319163804 | 60 |  | 33.810763888888886 | 2921.25 | 2014 | 11 | 2014_11_Asomata_english.xlsx
13 | 0 | 190 | 190 | 0 | 0 | 4 | 190 | 54 | 0 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 85 | 9200.000000000007 | 41.062 | 2705.04 | 719.9999999999927 | 3843.9583333333258 | 1900 | 10 | 85.34186046511628 | 3555 | 1223.9583333333333 | 288.95833333332575 | 0 |  | 21.99074074074074 | 1900 | 2014 | 11 | 2014_11_Asomata_english.xlsx
14 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 40 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.7 | 8480.000000000015 | 40.83 | 2433.6 | -719.9999999999927 | 1455.096153846161 | 1021.25 | 10.75 | 79.94553673547192 | 1468.8 | 1153.8461538461538 | 11.296153846160905 | 25 |  | 11.820023148148149 | 1021.25 | 2014 | 11 | 2014_11_Asomata_english.xlsx
15 | 170 | 375 | 545 | 0 | 0 | 4 | 545 | 109 | 3.599999999998545 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 15 | 85.2 | 9680.000000000015 | 41.429 | 3134.4300000000067 | 1200 | 8429.88860103627 | 5504.5 | 10.1 | 84.10570223689035 | 8343.9 | 1725.3886010362694 | 85.98860103626976 | 0 |  | 63.70949074074074 | 5504.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
16 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 54 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 85 | 9200.000000000007 | 41.35 | 3042 | -480.0000000000073 | 5260.648936170206 | 2171.5 | 10.1 | 84.49689154962007 | 5005.5 | 3569.148936170213 | 315.14893617020607 | 60 |  | 25.13310185185185 | 2171.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
17 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 54 | 2.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.2 | 9680.000000000015 | 40.95 | 2574 | 480.0000000000073 | 4776.373056994826 | 1400 | 10 | 84.94675925925925 | 4650.1 | 2896.3730569948184 | 126.27305699482622 | 0 |  | 16.203703703703702 | 1400 | 2014 | 11 | 2014_11_Asomata_english.xlsx
18 | 0 | 135 | 135 | 0 | 0 | 4 | 135 | 46 | 0 | 3.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.85 | 8839.999999999993 | 41.159 | 2818.53 | -840.0000000000218 | 2842.648936170191 | 1363.5 | 10.1 | 84.79267996811352 | 2766.7 | 2319.148936170213 | 75.94893617019125 | 0 |  | 15.78125 | 1363.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.9 | 8960.00000000002 | 40.7557 | 2346.6689999999967 | 120.00000000002728 | 4348.276595744708 | 707 | 10.1 | 84.6938540007847 | 4051.5 | 3521.276595744681 | 296.7765957447082 | 0 |  | 8.18287037037037 | 707 | 2014 | 11 | 2014_11_Asomata_english.xlsx
20 | 165 | 85 | 250 | 0 | 0 | 4 | 250 | 80 | 4.30000000000291 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 20 | 84.95 | 9080.000000000015 | 41.701 | 3452.67 | 119.99999999999454 | 5533.297872340419 | 2525 | 10.1 | 84.59525812883966 | 5453.1 | 2888.2978723404253 | 80.19787234041905 | 0 |  | 29.224537037037038 | 2525 | 2014 | 11 | 2014_11_Asomata_english.xlsx
21 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 55 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 85.2 | 9680.000000000015 | 41.639 | 3380.1300000000065 | 600 | 5040.148936170213 | 2121 | 10.1 | 84.10570223689035 | 4971.3 | 2319.148936170213 | 68.84893617021407 | 0 |  | 24.54861111111111 | 2121 | 2014 | 11 | 2014_11_Asomata_english.xlsx
22 | 185 | 115 | 300 | 0 | 0 | 4 | 300 | 55 | 3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 85.2 | 9680.000000000015 | 41.82 | 3591.9 | 0 | 6541.063829787234 | 2940 | 9.8 | 86.68036659108087 | 6445.9 | 3601.0638297872338 | 95.16382978723414 | 0 |  | 34.02777777777778 | 2940 | 2014 | 11 | 2014_11_Asomata_english.xlsx
23 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 53 | 0 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 84.6 | 8239.999999999993 | 41.53 | 3252.6 | -1440.0000000000218 | 5772.1595744680635 | 3584.5 | 10.7 | 80.50765653108684 | 5738.4 | 3627.6595744680853 | 93.75957446806297 | 60 |  | 41.48726851851851 | 3584.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
24 | 0 | 430 | 430 | 0 | 0 | 4 | 430 | 55 | 0 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.3 | 7520 | 41.6 | 3334.5 | -719.9999999999927 | 7125.163440860223 | 4291.4 | 9.98 | 86.92799310204333 | 7119 | 3553.7634408602153 | 66.16344086022309 | 60 |  | 49.668981481481495 | 4291.4 | 2014 | 11 | 2014_11_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.6 | 8239.999999999993 | 40.42 | 1953.9 | 719.9999999999927 | 3755.6554404145004 | 745.5 | 10.65 | 80.88562674954265 | 3591.6 | 2290.1554404145077 | 164.05544041450094 | 0 |  | 8.628472222222221 | 745.5 | 2014 | 11 | 2014_11_Asomata_english.xlsx
26 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 54 | 2.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.8 | 8720 | 40.58 | 2141.1 | 480.0000000000073 | 4497.771276595752 | 1650.75 | 10.65 | 80.50765653108684 | 4358.1 | 2367.021276595745 | 199.6712765957518 | 60 |  | 19.10590277777778 | 1650.75 | 2014 | 11 | 2014_11_Asomata_english.xlsx
27 | 0 | 110 | 110 | 0 | 0 | 4 | 110 | 54 | 0 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.7 | 8480.000000000015 | 40.53 | 2082.6 | -239.99999999998545 | 3458.2765957446954 | 1177 | 10.7 | 80.31911400993675 | 3346.2 | 2521.276595744681 | 172.07659574469517 | 60 |  | 13.622685185185185 | 1177 | 2014 | 11 | 2014_11_Asomata_english.xlsx
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.9 | 8960.00000000002 | 40.171 | 1662.57 | 480.00000000000546 | 2912.8461538461593 | 679 | 9.7 | 88.18638406267272 | 2876.2 | 1753.8461538461538 | 96.64615384615945 | 60 |  | 7.858796296296297 | 679 | 2014 | 11 | 2014_11_Asomata_english.xlsx
29 | 200 | 200 | 400 | 0 | 0 | 4 | 400 | 110 | 4.75 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.95 | 9080.000000000015 | 41.78 | 3545.1 | 119.99999999999454 | 4019.9999999999945 | 3900 | 9.75 | 87.63201098474671 | 3993.95 | 0 | 86.04999999999472 | 60 |  | 45.138888888888886 | 3900 | 2014 | 11 | 2014_11_Asomata_english.xlsx
30 | 250 | 0 | 250 | 0 | 0 | 4 | 250 | 54 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.8 | 8720 | 41.67 | 3416.4 | -360.00000000001455 | 3933.4210526315646 | 2525 | 10.1 | 84.89173683723513 | 3841.1 | 1768.421052631579 | 152.32105263156473 | 60 |  | 29.224537037037038 | 2525 | 2014 | 11 | 2014_11_Asomata_english.xlsx
1 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.9 | 8960.00000000002 | 41.047 | 2687.49 | 240.00000000002 | 4623.076923076943 | 860 | 10.75 | 79.57283027050468 | 4350.8 | 3523.076923076923 | 272.2769230769427 | 0 |  | 9.953703703703704 | 860 | 2014 | 12 | 2014_12_Asomata_english.xlsx
2 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.9 | 8960.00000000002 | 40.7 | 2281.5 | 0 | 3687.4111675126906 | 860 | 10.75 | 79.57283027050468 | 3542.4 | 2827.4111675126906 | 145.01116751269046 | 0 |  | 9.953703703703704 | 860 | 2014 | 12 | 2014_12_Asomata_english.xlsx
3 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 35 | 0 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 84.4 | 7760.00000000002 | 40.85 | 2457 | -1200 | 2680.718085106383 | 806.25 | 10.75 | 80.51118911803421 | 2664.5 | 3074.468085106383 | 76.21808510638311 | 60 |  | 9.331597222222221 | 806.25 | 2014 | 12 | 2014_12_Asomata_english.xlsx
4 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 54 | 3.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.8 | 8720 | 41.247 | 2921.49 | 959.99999999998 | 5048.607329842912 | 1764 | 9.8 | 87.49046347510966 | 4811.95 | 2324.607329842932 | 236.65732984291117 | 0 |  | 20.416666666666668 | 1764 | 2014 | 12 | 2014_12_Asomata_english.xlsx
5 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 54 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85 | 9200.000000000007 | 40.7 | 2281.5 | 480.0000000000073 | 3607.4935233160695 | 806.25 | 10.75 | 79.38777717685235 | 3445.6 | 2321.2435233160622 | 221.8935233160696 | 60 |  | 9.331597222222221 | 806.25 | 2014 | 12 | 2014_12_Asomata_english.xlsx
6 | 280 | 0 | 280 | 0 | 0 | 4 | 280 | 54 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 85 | 9200.000000000007 | 42.071 | 3885.5699999999933 | 0 | 5584.922279792746 | 2730 | 9.75 | 87.53011329755516 | 5305.3 | 2854.922279792746 | 339.62227979274576 | 60 |  | 31.59722222222222 | 2730 | 2014 | 12 | 2014_12_Asomata_english.xlsx
7 | 105 | 0 | 105 | 0 | 0 | 4 | 105 | 35 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.75 | 8600.000000000007 | 40.85 | 2457 | -600 | 2811.563829787234 | 1060.5 | 10.1 | 84.9910254183313 | 2530.25 | 2351.063829787234 | 341.3138297872342 | 60 |  | 12.274305555555555 | 1060.5 | 2014 | 12 | 2014_12_Asomata_english.xlsx
8 | 340 | 135 | 475 | 0 | 0 | 4 | 475 | 90 | 7.5 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 8 | 84.7 | 8480.000000000015 | 41.45 | 3159 | -119.99999999999272 | 6359.5512820512895 | 4797.5 | 10.1 | 85.09054652537853 | 6124.7 | 1682.051282051282 | 234.85128205128967 | 0 |  | 55.526620370370374 | 4797.5 | 2014 | 12 | 2014_12_Asomata_english.xlsx
9 | 420 | 470 | 890 | 0 | 0 | 4 | 890 | 108 | 8.80000000000291 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.85 | 8839.999999999993 | 40.78 | 2375.1 | 359.9999999999782 | 9348.999999999978 | 8989 | 10.1 | 84.79267996811352 | 8970 | 0 | 438.9999999999782 | 60 |  | 104.03935185185185 | 8989 | 2014 | 12 | 2014_12_Asomata_english.xlsx
10 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 54 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.95 | 9080.000000000015 | 40.701 | 2282.67 | 240.00000000002183 | 4426.765957446831 | 1224 | 10.2 | 83.76589285306673 | 4245.8 | 2962.7659574468084 | 240.96595744683145 | 60 |  | 14.166666666666666 | 1224 | 2014 | 12 | 2014_12_Asomata_english.xlsx
11 | 280 | 50 | 330 | 0 | 0 | 4 | 330 | 70 | 6.5 | 1.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 85.1 | 9439.999999999993 | 41.512 | 3231.54 | 359.9999999999782 | 6501.2085106382765 | 3194.4 | 9.68 | 87.95852428524863 | 6394.5 | 2946.808510638298 | 166.7085106382765 | 60 |  | 36.97222222222222 | 3194.4 | 2014 | 12 | 2014_12_Asomata_english.xlsx
12 | 0 | 295 | 295 | 0 | 0 | 4 | 295 | 55 | 0 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85 | 9200.000000000007 | 40.9107 | 2528.0189999999966 | -239.99999999998545 | 6888.436170212781 | 2979.5 | 10.1 | 84.49689154962007 | 6920.4 | 4148.936170212766 | 28.036170212781144 | 60 |  | 34.4849537037037 | 2979.5 | 2014 | 12 | 2014_12_Asomata_english.xlsx
13 | 0 | 205 | 205 | 0 | 0 | 4 | 205 | 55 | 0 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 13 | 85.15 | 9560.00000000002 | 40.5215 | 2072.655000000006 | 360.00000000001273 | 5938.148936170226 | 2009 | 9.8 | 86.78080734031734 | 5791.8 | 3569.148936170213 | 146.3489361702268 | 0 |  | 23.252314814814817 | 2009 | 2014 | 12 | 2014_12_Asomata_english.xlsx
14 | 280 | 90 | 370 | 0 | 0 | 5 | 370 | 108 | 6.19999999999709 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84.55 | 8120 | 41.4438 | 3151.7460000000015 | -1440.00000000002 | 6647.1276595744475 | 3885 | 10.5 | 82.13754126797606 | 6682.5 | 4202.1276595744675 | 24.627659574447534 | 60 |  | 44.96527777777778 | 3885 | 2014 | 12 | 2014_12_Asomata_english.xlsx
15 | 190 | 90 | 280 | 0 | 0 | 4 | 280 | 54 | 3.5 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.95 | 9080.000000000015 | 40.0718 | 1546.5060000000035 | 960.0000000000146 | 3788.0000000000146 | 2828 | 10.1 | 84.59525812883966 | 3685.2 | 0 | 162.80000000001428 | 60 |  | 32.73148148148148 | 2828 | 2014 | 12 | 2014_12_Asomata_english.xlsx
16 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 54 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 85.1 | 9439.999999999993 | 39.9987 | 1460.978999999999 | 359.9999999999782 | 3721.0638297872124 | 1010 | 10.1 | 84.30084307734718 | 3569.7 | 2351.063829787234 | 211.36382978721258 | 60 |  | 11.689814814814815 | 1010 | 2014 | 12 | 2014_12_Asomata_english.xlsx
17 | 75 | 130 | 205 | 0 | 0 | 4 | 205 | 80 | 1.9000000000014552 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.8 | 8720 | 40.583 | 2144.61 | -719.9999999999927 | 5697.021276595752 | 2050 | 10 | 85.74065420560747 | 5457.6 | 4367.021276595745 | 269.4212765957518 | 30 |  | 23.72685185185185 | 2050 | 2014 | 12 | 2014_12_Asomata_english.xlsx
18 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 85 | 9200.000000000007 | 40.019 | 1484.73 | 480.0000000000073 | 3075.7446808510713 | 750 | 10 | 85.34186046511628 | 2890.8 | 1845.7446808510638 | 214.94468085107155 | 30 |  | 8.680555555555555 | 750 | 2014 | 12 | 2014_12_Asomata_english.xlsx
19 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 35 | 3.7999999999956344 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | Εγκατάσταση Μετεο & Σταθμημέτρων από συνεργείο δυτών | 19 | 84.3 | 7520 | 40.55099 | 2107.1582999999964 | -1680.0000000000073 | 2132.9361702127585 | 1414 | 10.1 | 85.89518526320718 | 2073.2 | 2398.936170212766 | 119.73617021275868 | 60 |  | 16.36574074074074 | 1414 | 2014 | 12 | 2014_12_Asomata_english.xlsx
20 | 280 | 130 | 410 | 0 | 0 | 4 | 410 | 110 | 6.30000000000291 | 3.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 20 | 85.1 | 9439.999999999993 | 41.35 | 3042 | 1919.9999999999927 | 6019.999999999993 | 4100 | 10 | 85.14385150812066 | 5621 | 0 | 398.9999999999927 | 0 |  | 47.4537037037037 | 4100 | 2014 | 12 | 2014_12_Asomata_english.xlsx
21 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 55 | 0 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 21 | 84.9 | 8960.00000000002 | 40.1482 | 1635.8940000000018 | -479.9999999999727 | 3419.258064516156 | 867 | 10.2 | 83.8635220988162 | 3416 | 3032.258064516129 | 63.25806451615608 | 60 |  | 10.034722222222221 | 867 | 2014 | 12 | 2014_12_Asomata_english.xlsx
22 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 55 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.35 | 7639.999999999993 | 39.981 | 1440.27 | -1320.0000000000273 | 2812.3670212765683 | 1988.75 | 10.75 | 80.60624365064112 | 2529.6 | 2143.6170212765956 | 282.76702127656836 | 0 |  | 23.017939814814813 | 1988.75 | 2014 | 12 | 2014_12_Asomata_english.xlsx
23 | 115 | 0 | 115 | 0 | 0 | 5 | 115 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.9 | 8960.00000000002 | 40.65 | 2223 | 1320.0000000000273 | 4137.442307692335 | 1109.75 | 9.65 | 88.6433083324275 | 3920.1 | 1707.6923076923076 | 217.342307692335 | 0 |  | 12.844328703703704 | 1109.75 | 2014 | 12 | 2014_12_Asomata_english.xlsx
24 | 190 | 0 | 190 | 0 | 0 | 5 | 190 | 35 | 5.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.9 | 8960.00000000002 | 41.243 | 2916.81 | 0 | 3611.3076923076924 | 1919 | 10.1 | 84.6938540007847 | 3504 | 1692.3076923076922 | 167.30769230769238 | 60 |  | 22.21064814814815 | 1919 | 2014 | 12 | 2014_12_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.2 | 9680.000000000015 | 40.343 | 1863.81 | 719.9999999999945 | 5844.52577319587 | 707 | 10.1 | 84.10570223689035 | 5847.3 | 4417.525773195875 | 57.225773195870715 | 60 |  | 8.18287037037037 | 707 | 2014 | 12 | 2014_12_Asomata_english.xlsx
26 | 175 | 0 | 175 | 0 | 0 | 4 | 175 | 35 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.9 | 8960.00000000002 | 40.323 | 1840.41 | -719.9999999999945 | 2834.734042553197 | 1767.5 | 10.1 | 84.6938540007847 | 2701 | 1787.2340425531916 | 133.734042553197 | 0 |  | 20.457175925925927 | 1767.5 | 2014 | 12 | 2014_12_Asomata_english.xlsx
27 | 65 | 155 | 220 | 0 | 0 | 4 | 220 | 70 | 1.8000000000029104 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 85.15 | 9560.00000000002 | 41.02 | 2655.9 | 600 | 4561.7959183673465 | 2222 | 10.1 | 84.20315959753565 | 4569.8 | 1739.795918367347 | 11.995918367347258 | 20 |  | 25.71759259259259 | 2222 | 2014 | 12 | 2014_12_Asomata_english.xlsx
28 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 35 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.1 | 9439.999999999993 | 40.63 | 2199.6 | -120.00000000002728 | 4039.134615384588 | 1343.75 | 10.75 | 79.20358279825177 | 3934.7 | 2815.3846153846152 | 104.43461538458814 | 0 |  | 15.552662037037036 | 1343.75 | 2014 | 12 | 2014_12_Asomata_english.xlsx
29 | 0 | 185 | 185 | 0 | 0 | 4 | 185 | 35 | 0 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 85 | 9200.000000000007 | 41.65 | 3393 | -239.99999999998545 | 3352.8243243243387 | 1868.5 | 10.1 | 84.49689154962007 | 3150 | 1724.3243243243244 | 262.8243243243387 | 60 |  | 21.62615740740741 | 1868.5 | 2014 | 12 | 2014_12_Asomata_english.xlsx
30 | 260 | 450 | 710 | 0 | 0 | 4 | 710 | 70 | 7.19999999999709 | 12.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 30 | 83.6 | 5839.999999999993 | 41.35 | 3042 | -3360.0000000000146 | 7084.361702127645 | 7455 | 10.5 | 84.0132783882784 | 7070.4 | 2989.3617021276596 | 73.96170212764537 | 60 |  | 86.28472222222223 | 7455 | 2014 | 12 | 2014_12_Asomata_english.xlsx
31 | 125 | 90 | 215 | 0 | 0 | 4 | 215 | 70 | 3.3000000000029104 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.45 | 7880.000000000014 | 40.552 | 2108.34 | 2040.000000000021 | 7361.329787234064 | 2257.5 | 10.5 | 82.33103370912558 | 7132.1 | 3063.8297872340427 | 229.22978723406413 | 0 |  | 26.12847222222222 | 2257.5 | 2014 | 12 | 2014_12_Asomata_english.xlsx
1 | 370 | 115 | 485 | 0 | 0 | 4 | 485 | 80 | 8.94999999999709 | 2.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.9 | 8960.00000000002 | 41.598 | 3332.16 | 1080.0000000000064 | 8457.223404255325 | 4898.5 | 10.1 | 84.6938540007847 | 8373.1 | 2478.723404255319 | 84.12340425532602 | 0 |  | 56.695601851851855 | 4898.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
2 | 170 | 265 | 435 | 0 | 0 | 5 | 435 | 95 | 4.05000000000291 | 5.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.2 | 7280.000000000014 | 41.55 | 3276 | -1680.0000000000064 | 4266.673469387749 | 4263 | 9.8 | 88.73440371409225 | 4139.1 | 1683.673469387755 | 127.57346938774936 | 0 |  | 49.34027777777778 | 4263 | 2015 | 1 | 2015_01_Asomata_english.xlsx
3 | 210 | 625 | 835 | 0 | 0 | 5 | 835 | 110 | 3.8999999999941792 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 3 | 84.4 | 7760.00000000002 | 41.461 | 3171.8699999999935 | 480.00000000000637 | 8788.250000000007 | 8308.25 | 9.95 | 86.98445055466009 | 8789.2 | 0 | 59.05000000000655 | 60 |  | 96.16030092592592 | 8308.25 | 2015 | 1 | 2015_01_Asomata_english.xlsx
4 | 185 | 0 | 185 | 0 | 0 | 5 | 185 | 55 | 3.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 83.5 | 5600.000000000007 | 39.998 | 1460.16 | -2160.0000000000127 | 898.6424731182669 | 1988.75 | 10.75 | 82.25721490613617 | 847 | 1069.8924731182797 | 111.64247311826693 | 60 |  | 23.017939814814813 | 1988.75 | 2015 | 1 | 2015_01_Asomata_english.xlsx
5 | 0 | 245 | 245 | 0 | 0 | 4 | 245 | 54 | 0 | 4.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5 | 83.95 | 6680.000000000014 | 40.15 | 1638 | 1080.0000000000064 | 3493.2500000000064 | 2413.25 | 9.85 | 88.81010146234034 | 3486.1 | 0 | 67.15000000000646 | 60 |  | 27.93113425925926 | 2413.25 | 2015 | 1 | 2015_01_Asomata_english.xlsx
6 | 40 | 580 | 620 | 0 | 0 | 4 | 620 | 104 | 0.8999999999941792 | 12.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84 | 6800.000000000007 | 41.547 | 3272.49 | 119.99999999999363 | 6497.999999999994 | 6378 | 10.287096774193548 | 84.93534321850409 | 6387.75 | 0 | 170.24999999999363 | 60 |  | 73.81944444444444 | 6378 | 2015 | 1 | 2015_01_Asomata_english.xlsx
7 | 0 | 445 | 445 | 0 | 0 | 4 | 445 | 55 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 84.4 | 7760.00000000002 | 41.248 | 2922.66 | 960.0000000000127 | 5276.500000000013 | 4316.5 | 9.7 | 89.22631783699669 | 4995 | 0 | 281.50000000001273 | 0 |  | 49.95949074074074 | 4316.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
8 | 140 | 710 | 850 | 0 | 0 | 4 | 850 | 80 | 3.2000000000043656 | 14.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.3 | 7520 | 41.8 | 3568.5 | -240.00000000002 | 8344.99999999998 | 8585 | 10.1 | 85.89518526320718 | 8256.3 | 0 | 148.69999999998072 | 60 |  | 99.36342592592592 | 8585 | 2015 | 1 | 2015_01_Asomata_english.xlsx
9 | 350 | 265 | 615 | 0 | 0 | 4 | 615 | 100 | 6.849999999998545 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 84 | 6800.000000000007 | 41.7 | 3451.5 | -719.9999999999927 | 5491.500000000007 | 6211.5 | 10.1 | 86.50872230080151 | 5462.6 | 0 | 88.90000000000691 | 60 |  | 71.89236111111111 | 6211.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
10 | 130 | 0 | 130 | 0 | 0 | 4 | 130 | 55 | 3.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.2 | 7280.000000000014 | 40.7 | 2281.5 | 480.00000000000637 | 1747.5000000000064 | 1267.5 | 9.75 | 89.1894519382671 | 1641.6 | 0 | 105.90000000000646 | 0 |  | 14.67013888888889 | 1267.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
11 | 95 | 70 | 165 | 0 | 0 | 4 | 165 | 80 | 2.5 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.85 | 8839.999999999993 | 40.698 | 2279.16 | 1559.999999999979 | 3152.249999999979 | 1592.25 | 9.65 | 88.74674276455404 | 3056.2 | 0 | 96.04999999997881 | 0 |  | 18.428819444444443 | 1592.25 | 2015 | 1 | 2015_01_Asomata_english.xlsx
12 | 0 | 555 | 555 | 0 | 0 | 5 | 555 | 55 | 0 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.7 | 8480.000000000015 | 41.931 | 3721.7699999999936 | -359.9999999999782 | 8130.787234042575 | 5661 | 10.2 | 84.25632548101207 | 8092.8 | 2829.7872340425533 | 97.98723404257453 | 60 |  | 65.52083333333333 | 5661 | 2015 | 1 | 2015_01_Asomata_english.xlsx
13 | 145 | 175 | 320 | 0 | 0 | 5 | 320 | 110 | 2.7999999999956344 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.1 | 7039.999999999993 | 41.089 | 2736.63 | -1440.0000000000218 | 4829.518716577519 | 3200 | 10 | 87.16627078384799 | 4963 | 3069.51871657754 | 16.518716577518717 | 150 |  | 37.03703703703704 | 3200 | 2015 | 1 | 2015_01_Asomata_english.xlsx
14 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.85 | 8839.999999999993 | 39.09 | 397.8000000000053 | 1800 | 5511.530456852792 | 909.5 | 10.7 | 80.03795025027537 | 5270.4 | 2802.0304568527918 | 241.13045685279212 | 0 |  | 10.526620370370368 | 909.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
15 | 290 | 70 | 360 | 0 | 0 | 4 | 360 | 70 | 7 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | Βλάβη Απ/Ζ 26 | 15 | 84.6 | 8239.999999999993 | 40.982 | 2611.44 | -600 | 3072 | 3672 | 10.2 | 84.45411028261071 | 2937.8 | 0 | 134.2 | 0 |  | 42.5 | 3672 | 2015 | 1 | 2015_01_Asomata_english.xlsx
16 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85 | 9200.000000000007 | 40.4 | 1930.5 | 960.0000000000146 | 2112.0000000000146 | 1152 | 9.6 | 88.89777131782945 | 1959.35 | 0 | 152.65000000001442 | 0 |  | 13.333333333333334 | 1152 | 2015 | 1 | 2015_01_Asomata_english.xlsx
17 | 95 | 90 | 185 | 0 | 0 | 4 | 185 | 55 | 2.099999999998545 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.9 | 8960.00000000002 | 40.598 | 2162.16 | -239.99999999998727 | 1582.2500000000127 | 1822.25 | 9.85 | 86.84344420385028 | 1445.4 | 0 | 136.85000000001287 | 0 |  | 21.09085648148148 | 1822.25 | 2015 | 1 | 2015_01_Asomata_english.xlsx
18 | 300 | 70 | 370 | 0 | 0 | 5 | 370 | 70 | 7 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 84.7 | 8480.000000000015 | 41.8 | 3568.5 | -480.00000000000546 | 4908.888324873091 | 3663 | 9.9 | 86.80954746528516 | 4857.4 | 1725.8883248730963 | 51.48832487309119 | 0 |  | 42.395833333333336 | 3663 | 2015 | 1 | 2015_01_Asomata_english.xlsx
19 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 35 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.75 | 8600.000000000007 | 40.08 | 1556.1 | 119.99999999999272 | 2136.702127659567 | 1155 | 10.5 | 81.75327206906154 | 2102.4 | 861.7021276595744 | 84.30212765956685 | 50 |  | 13.368055555555555 | 1155 | 2015 | 1 | 2015_01_Asomata_english.xlsx
20 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 35 | 0 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.9 | 8960.00000000002 | 40.36 | 1883.7 | 360.00000000001273 | 2828.442211055289 | 780 | 9.75 | 87.73414619568464 | 2579.85 | 1688.4422110552764 | 248.59221105528923 | 0 |  | 9.027777777777779 | 780 | 2015 | 1 | 2015_01_Asomata_english.xlsx
21 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 54 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.75 | 8600.000000000007 | 40.018 | 1483.56 | -360.00000000001273 | 2189.9999999999873 | 2550 | 10 | 85.84093567251462 | 2051.3 | 0 | 138.69999999998754 | 0 |  | 29.51388888888889 | 2550 | 2015 | 1 | 2015_01_Asomata_english.xlsx
22 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.9 | 8960.00000000002 | 40.67 | 2246.4 | 360.00000000001273 | 1760.0000000000127 | 1400 | 10 | 85.54079254079252 | 1620.6 | 0 | 139.4000000000126 | 0 |  | 16.203703703703702 | 1400 | 2015 | 1 | 2015_01_Asomata_english.xlsx
23 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.95 | 9080.000000000015 | 39.698 | 1109.16 | 119.99999999999454 | 2733.0816326530557 | 909 | 10.1 | 84.59525812883966 | 2708.1 | 1704.0816326530612 | 24.98163265305584 | 0 |  | 10.520833333333334 | 909 | 2015 | 1 | 2015_01_Asomata_english.xlsx
24 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 55 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.35 | 7639.999999999993 | 41.192 | 2857.14 | -1440.0000000000218 | 5985.797872340404 | 3787.5 | 10.1 | 85.79377418261309 | 5978 | 3638.297872340426 | 67.79787234040396 | 60 |  | 43.83680555555556 | 3787.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
25 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.4 | 7760.00000000002 | 40.32 | 1836.9 | 120.00000000002728 | 3462.1595744681126 | 1464.5 | 10.1 | 85.69260227909582 | 3233.5 | 1877.659574468085 | 228.65957446811262 | 0 |  | 16.95023148148148 | 1464.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
26 | 0 | 420 | 420 | 0 | 0 | 5 | 420 | 55 | 0 | 8.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.85 | 8839.999999999993 | 40.921 | 2540.07 | 1079.9999999999727 | 5237.999999999973 | 4158 | 9.9 | 86.50566340181277 | 5002.4 | 0 | 235.59999999997217 | 0 |  | 48.125 | 4158 | 2015 | 1 | 2015_01_Asomata_english.xlsx
27 | 215 | 280 | 495 | 0 | 0 | 4 | 495 | 55 | 4 | 5.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84 | 6800.000000000007 | 41.467 | 3178.89 | -2039.9999999999854 | 4803.180851063844 | 5098.5 | 10.3 | 84.82894128525196 | 4746 | 1744.6808510638298 | 117.18085106384387 | 60 |  | 59.010416666666664 | 5098.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
28 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 55 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.75 | 8600.000000000007 | 39.555 | 941.85 | 1800 | 2624.5 | 824.5 | 9.7 | 88.49580997166457 | 2340 | 0 | 284.5 | 0 |  | 9.542824074074073 | 824.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
29 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.5 | 8000.000000000007 | 40.089 | 1566.63 | -600 | 3688.2659574468084 | 2575.5 | 10.1 | 85.49097262667443 | 3715.2 | 1712.7659574468084 | 3.065957446808625 | 30 |  | 29.80902777777778 | 2575.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
30 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 40 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.85 | 8839.999999999993 | 40.65 | 2223 | 839.9999999999854 | 3240.9999999999854 | 2401 | 9.8 | 87.38837425285168 | 3167.85 | 0 | 73.14999999998554 | 0 |  | 27.78935185185185 | 2401 | 2015 | 1 | 2015_01_Asomata_english.xlsx
31 | 475 | 280 | 755 | 0 | 0 | 5 | 755 | 110 | 10.30000000000291 | 6.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.8 | 8720 | 41.2679 | 2945.9429999999998 | -119.99999999999272 | 9172.457446808517 | 7776.5 | 10.3 | 83.24335359767717 | 9081.2 | 1515.9574468085107 | 151.25744680851858 | 60 |  | 90.00578703703704 | 7776.5 | 2015 | 1 | 2015_01_Asomata_english.xlsx
1 | 460 | 370 | 830 | 0 | 0 | 4 | 830 | 110 | 9.900000000001455 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.8 | 8720 | 42.028 | 3835.26 | 0 | 13843.589743589742 | 8300 | 10 | 85.74065420560747 | 13209 | 5543.589743589743 | 694.5897435897423 | 60 |  | 96.06481481481481 | 8300 | 2015 | 2 | 2015_02_Asomata_english.xlsx
2 | 100 | 430 | 530 | 0 | 0 | 4 | 530 | 70 | 2.6999999999970896 | 9.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84 | 6800.000000000007 | 40.3 | 1813.4999999999945 | -1919.9999999999927 | 8426.723404255326 | 5618 | 10.6 | 82.42812219227314 | 8431.5 | 4728.723404255319 | 55.223404255326386 | 60 |  | 65.02314814814815 | 5618 | 2015 | 2 | 2015_02_Asomata_english.xlsx
3 | 350 | 810 | 1160 | 0 | 0 | 5 | 1160 | 110 | 6.30000000000291 | 15.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 3 | 85.3 | 9920 | 41.808 | 3577.86 | 3119.9999999999927 | 17634.595744680842 | 12238 | 10.55 | 80.33230082199577 | 17191.5 | 2276.595744680851 | 503.0957446808425 | 60 |  | 141.6435185185185 | 12238 | 2015 | 2 | 2015_02_Asomata_english.xlsx
4 | 545 | 1135 | 1680 | 0 | 0 | 5 | 1680 | 110 | 11 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 85.1 | 9439.999999999993 | 41.0015 | 2634.254999999996 | -480.0000000000073 | 16488 | 16968 | 10.1 | 84.30084307734718 | 15946.6 | 0 | 601.3999999999924 | 60 |  | 196.38888888888889 | 16968 | 2015 | 2 | 2015_02_Asomata_english.xlsx
5 | 390 | 520 | 910 | 0 | 0 | 4 | 910 | 110 | 9.89999999999418 | 12.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 84.1 | 7039.999999999993 | 40.4385 | 1975.545 | -2400 | 6791 | 9191 | 10.1 | 86.3032383998495 | 6773.4 | 0 | 17.600000000000364 | 0 |  | 106.37731481481481 | 9191 | 2015 | 2 | 2015_02_Asomata_english.xlsx
6 | 760 | 870 | 1630 | 0 | 0 | 4 | 1630 | 110 | 15.80000000000291 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 83.5 | 5600.000000000007 | 41.158 | 2817.36 | -1439.9999999999854 | 17859.202702702718 | 17196.5 | 10.55 | 83.81659338776907 | 17906.9 | 2102.702702702703 | 12.302702702716488 | 60 |  | 199.0335648148148 | 17196.5 | 2015 | 2 | 2015_02_Asomata_english.xlsx
7 | 935 | 785 | 1720 | 0 | 0 | 4 | 1720 | 110 | 19.19999999999709 | 16.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.3 | 7520 | 41.901 | 3686.67 | 1919.9999999999927 | 19292 | 17372 | 10.1 | 85.89518526320718 | 19240 | 0 | 51.999999999992724 | 0 |  | 201.0648148148148 | 17372 | 2015 | 2 | 2015_02_Asomata_english.xlsx
8 | 695 | 800 | 1495 | 0 | 0 | 4 | 1495 | 110 | 15 | 17.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.5 | 8000.000000000007 | 41.018 | 2653.56 | 480.0000000000073 | 15205.75 | 14725.75 | 9.85 | 87.66079426694536 | 15157.5 | 0 | 48.250000000007276 | 0 |  | 170.4369212962963 | 14725.75 | 2015 | 2 | 2015_02_Asomata_english.xlsx
9 | 525 | 765 | 1290 | 0 | 0 | 4 | 1290 | 110 | 10.30000000000291 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 83.1 | 4639.999999999993 | 41.25 | 2925 | -3360.0000000000146 | 10249.5 | 13609.5 | 10.55 | 84.63232665674981 | 10205.1 | 0 | 104.39999999998508 | 60 |  | 157.51736111111111 | 13609.5 | 2015 | 2 | 2015_02_Asomata_english.xlsx
10 | 510 | 815 | 1325 | 0 | 0 | 4 | 1325 | 110 | 10 | 16.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 10 | 83 | 4400 | 41.6586 | 3403.0619999999963 | -239.99999999999272 | 15369.78723404256 | 13780 | 10.4 | 86.062382739212 | 15358.2 | 1829.787234042553 | 11.58723404255943 | 0 |  | 159.49074074074073 | 13780 | 2015 | 2 | 2015_02_Asomata_english.xlsx
11 | 810 | 925 | 1735 | 0 | 0 | 5 | 1735 | 110 | 14.900000000001455 | 16.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 82.6 | 3519.9999999999873 | 41.86 | 3638.7 | -880.0000000000127 | 16955.8 | 17835.8 | 10.28 | 87.92480496827741 | 16940 | 0 | 75.79999999998836 | 60 |  | 206.43287037037038 | 17835.8 | 2015 | 2 | 2015_02_Asomata_english.xlsx
12 | 930 | 845 | 1775 | 0 | 0 | 4 | 1775 | 108 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 83.15 | 4760.00000000002 | 41.57 | 3299.4 | 1240.0000000000327 | 19495.875000000033 | 18255.875 | 10.285 | 86.70745242957248 | 19469.45 | 0 | 86.42500000003201 | 60 |  | 211.29484953703704 | 18255.875 | 2015 | 2 | 2015_02_Asomata_english.xlsx
13 | 825 | 700 | 1525 | 0 | 0 | 5 | 1525 | 108 | 15.599999999998545 | 13.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 13 | 83.2 | 4880.000000000014 | 42 | 3802.5 | 119.99999999999363 | 15903.75 | 15783.75 | 10.35 | 86.05834623141503 | 15932 | 0 | 31.749999999992724 | 60 |  | 182.68229166666666 | 15783.75 | 2015 | 2 | 2015_02_Asomata_english.xlsx
14 | 920 | 865 | 1785 | 0 | 0 | 4 | 1785 | 110 | 17 | 16.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.5 | 5600.000000000007 | 41.5 | 3217.5 | 719.9999999999936 | 19819.5 | 19099.5 | 10.7 | 82.64159441504336 | 19856.34 | 0 | 23.159999999996217 | 60 |  | 221.05902777777777 | 19099.5 | 2015 | 2 | 2015_02_Asomata_english.xlsx
15 | 960 | 950 | 1910 | 0 | 0 | 5 | 1910 | 110 | 17.900000000001455 | 18.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 81.7 | 1540.0000000000064 | 41.448 | 3156.66 | -4060 | 16472.5 | 20532.5 | 10.75 | 85.98676117392068 | 16592.7 | 0 | 29.80000000000291 | 150 |  | 237.64467592592592 | 20532.5 | 2015 | 2 | 2015_02_Asomata_english.xlsx
16 | 910 | 815 | 1725 | 0 | 0 | 4 | 1725 | 110 | 16.900000000001455 | 15.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 82.7 | 3740.0000000000064 | 41.699 | 3450.33 | 2200 | 20640.25 | 18440.25 | 10.69 | 84.34482615960633 | 20650 | 0 | 50.25 | 60 |  | 213.42881944444446 | 18440.25 | 2015 | 2 | 2015_02_Asomata_english.xlsx
17 | 915 | 875 | 1790 | 0 | 0 | 4 | 1790 | 110 | 16.69999999999709 | 16.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 83.05 | 4520 | 42.008 | 3811.86 | 779.9999999999936 | 19843.5 | 19063.5 | 10.65 | 83.93977343557896 | 19821.5 | 0 | 81.99999999999272 | 60 |  | 220.64236111111111 | 19063.5 | 2015 | 2 | 2015_02_Asomata_english.xlsx
18 | 990 | 935 | 1925 | 0 | 0 | 4 | 1925 | 110 | 17.900000000001455 | 17.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 82.8 | 3959.9999999999936 | 41.9 | 3685.5 | -560.0000000000064 | 19267.5 | 19827.5 | 10.3 | 87.3239101465829 | 19236 | 0 | 91.49999999999272 | 60 |  | 229.4849537037037 | 19827.5 | 2015 | 2 | 2015_02_Asomata_english.xlsx
19 | 915 | 830 | 1745 | 0 | 0 | 4 | 1745 | 110 | 17 | 15.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 82.3 | 2859.9999999999936 | 41.398 | 3098.16 | -1100 | 17397 | 18497 | 10.6 | 85.90523900931693 | 17439.7 | 0 | 17.30000000000291 | 60 |  | 214.08564814814815 | 18497 | 2015 | 2 | 2015_02_Asomata_english.xlsx
20 | 690 | 945 | 1635 | 0 | 0 | 4 | 1635 | 110 | 12.599999999998545 | 18.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 20 | 83.1 | 4639.999999999993 | 41.57 | 3299.4 | 1780 | 19274.5 | 17494.5 | 10.7 | 83.44589217090754 | 19338.2 | 0 | 36.30000000000291 | 100 |  | 202.48263888888889 | 17494.5 | 2015 | 2 | 2015_02_Asomata_english.xlsx
21 | 920 | 570 | 1490 | 0 | 0 | 4 | 1490 | 110 | 16.900000000001455 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 83.8 | 6320 | 41.9675 | 3764.475 | 1680.0000000000073 | 17623 | 15943 | 10.7 | 82.0484729240263 | 17625.6 | 0 | 57.40000000000509 | 60 |  | 184.52546296296296 | 15943 | 2015 | 2 | 2015_02_Asomata_english.xlsx
22 | 990 | 965 | 1955 | 0 | 0 | 4 | 1955 | 110 | 17.900000000001455 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 82.75 | 3850 | 41.851 | 3628.17 | -2470 | 18644 | 21114 | 10.8 | 83.38332197227902 | 18711 | 0 | 13 | 80 |  | 244.375 | 21114 | 2015 | 2 | 2015_02_Asomata_english.xlsx
23 | 945 | 925 | 1870 | 0 | 0 | 4 | 1870 | 109 | 17.299999999995634 | 17.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.25 | 5000.000000000007 | 41.648 | 3390.66 | 1150.0000000000073 | 19850 | 18700 | 10 | 88.96242424242425 | 19688.1 | 0 | 161.90000000000873 | 0 |  | 216.4351851851852 | 18700 | 2015 | 2 | 2015_02_Asomata_english.xlsx
24 | 930 | 940 | 1870 | 0 | 0 | 4 | 1870 | 109 | 17 | 17.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83.8 | 6320 | 41.22 | 2889.9 | 1319.9999999999927 | 20207 | 18887 | 10.1 | 86.9226396323843 | 19823.98 | 0 | 443.0199999999968 | 60 |  | 218.59953703703704 | 18887 | 2015 | 2 | 2015_02_Asomata_english.xlsx
25 | 840 | 960 | 1800 | 0 | 0 | 4 | 1800 | 109 | 14.400000000001455 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.7 | 8480.000000000015 | 41.73 | 3486.6 | 2160.0000000000146 | 19980 | 17820 | 9.9 | 86.80954746528516 | 19869.15 | 0 | 170.8500000000131 | 60 |  | 206.25 | 17820 | 2015 | 2 | 2015_02_Asomata_english.xlsx
26 | 985 | 955 | 1940 | 0 | 0 | 4 | 1940 | 110 | 19 | 18.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.8 | 8720 | 41.619 | 3356.73 | 239.99999999998545 | 19349 | 19109 | 9.85 | 87.04634944731724 | 18915 | 0 | 433.99999999998545 | 0 |  | 221.1689814814815 | 19109 | 2015 | 2 | 2015_02_Asomata_english.xlsx
27 | 995 | 975 | 1970 | 0 | 0 | 4 | 1970 | 110 | 17.900000000001455 | 18.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.75 | 8600.000000000007 | 41.884 | 3666.78 | -119.99999999999272 | 19580 | 19700 | 10 | 85.84093567251462 | 19466.25 | 0 | 173.75000000000728 | 60 |  | 228.00925925925927 | 19700 | 2015 | 2 | 2015_02_Asomata_english.xlsx
28 | 860 | 660 | 1520 | 0 | 0 | 4 | 1520 | 109 | 16.599999999998545 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 83.5 | 5600.000000000007 | 41.382 | 3079.44 | -3000 | 12732 | 15732 | 10.35 | 85.43623770444096 | 12514.95 | 0 | 277.0500000000011 | 60 |  | 182.08333333333334 | 15732 | 2015 | 2 | 2015_02_Asomata_english.xlsx
1 | 755 | 560 | 1315 | 0 | 0 | 4 | 1315 | 109 | 13.5 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 83.1 | 4639.999999999993 | 41.603 | 3338.01 | -960.0000000000146 | 12387.25 | 13347.25 | 10.15 | 87.96759076144932 | 12295.2 | 0 | 152.04999999998654 | 60 |  | 154.4820601851852 | 13347.25 | 2015 | 3 | 2015_03_Asomata_english.xlsx
2 | 985 | 365 | 1350 | 0 | 0 | 4 | 1350 | 109 | 18 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.25 | 5000.000000000007 | 41.331 | 3019.77 | 360.00000000001455 | 13995 | 13635 | 10.1 | 88.08160816081609 | 13974 | 0 | 81.00000000001455 | 60 |  | 157.8125 | 13635 | 2015 | 3 | 2015_03_Asomata_english.xlsx
3 | 870 | 490 | 1360 | 0 | 0 | 4 | 1360 | 109 | 16.69999999999709 | 9.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 83.75 | 6200.000000000007 | 41.643 | 3384.81 | 1200 | 14936 | 13736 | 10.1 | 87.02673860200392 | 14891.32 | 0 | 104.68 | 60 |  | 158.9814814814815 | 13736 | 2015 | 3 | 2015_03_Asomata_english.xlsx
4 | 690 | 600 | 1290 | 0 | 0 | 4 | 1290 | 109 | 12.400000000001455 | 11.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84 | 6800.000000000007 | 41.418 | 3121.56 | 600 | 14016 | 13416 | 10.4 | 84.01327838827838 | 14008.3 | 0 | 47.70000000000073 | 40 |  | 155.27777777777777 | 13416 | 2015 | 3 | 2015_03_Asomata_english.xlsx
5 | 625 | 365 | 990 | 0 | 0 | 4 | 990 | 110 | 11.900000000001455 | 7.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.4 | 7760.00000000002 | 41.42 | 3123.9 | 960.0000000000127 | 10860 | 9900 | 10 | 86.54952830188678 | 10760.2 | 0 | 159.800000000012 | 60 |  | 114.58333333333333 | 9900 | 2015 | 3 | 2015_03_Asomata_english.xlsx
6 | 805 | 225 | 1030 | 0 | 0 | 4 | 1030 | 110 | 16 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 83.65 | 5960.00000000002 | 41.82 | 3591.9 | -1800 | 11882.734042553191 | 10145.5 | 9.85 | 89.44979006831157 | 11760.3 | 3537.2340425531916 | 122.43404255319183 | 0 |  | 117.42476851851852 | 10145.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
7 | 245 | 260 | 505 | 0 | 0 | 5 | 505 | 108 | 5 | 5.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 83.6 | 5839.999999999993 | 41.12 | 2772.9 | -120.00000000002728 | 6950.836021505349 | 5226.75 | 10.35 | 85.23086213303606 | 6913.8 | 1844.0860215053763 | 97.03602150534789 | 60 |  | 60.494791666666664 | 5226.75 | 2015 | 3 | 2015_03_Asomata_english.xlsx
8 | 620 | 565 | 1185 | 0 | 0 | 4 | 1185 | 110 | 13.099999999998545 | 12.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 83.35 | 5239.999999999993 | 41.5 | 3217.5 | -600 | 11368.5 | 11968.5 | 10.1 | 87.86859338896406 | 11316.9 | 0 | 111.6 | 60 |  | 138.52430555555554 | 11968.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
9 | 230 | 845 | 1075 | 0 | 0 | 4 | 1075 | 108 | 4.700000000004366 | 16.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84 | 6800.000000000007 | 41.96 | 3755.7 | 1560.0000000000146 | 12310 | 10750 | 10 | 87.37380952380953 | 12074.2 | 0 | 235.80000000001382 | 0 |  | 124.42129629629629 | 10750 | 2015 | 3 | 2015_03_Asomata_english.xlsx
10 | 605 | 790 | 1395 | 0 | 0 | 4 | 1395 | 109 | 13.799999999995634 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 83.6 | 5839.999999999993 | 41.669 | 3415.23 | -960.0000000000146 | 13129.5 | 14089.5 | 10.1 | 87.34053693830923 | 13032 | 0 | 157.49999999998545 | 60 |  | 163.07291666666666 | 14089.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
11 | 295 | 845 | 1140 | 0 | 0 | 4 | 1140 | 109 | 5.650000000001455 | 16.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.4 | 7760.00000000002 | 41.42 | 3123.9 | 1920.0000000000273 | 13320 | 11400 | 10 | 86.54952830188678 | 13329.8 | 0 | 50.20000000002801 | 60 |  | 131.94444444444446 | 11400 | 2015 | 3 | 2015_03_Asomata_english.xlsx
12 | 340 | 870 | 1210 | 0 | 0 | 4 | 1210 | 109 | 7.05000000000291 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.45 | 7880.000000000014 | 41.291 | 2972.9699999999934 | 119.99999999999363 | 12220 | 12100 | 10 | 86.44758539458186 | 12088.8 | 0 | 131.19999999999163 | 0 |  | 140.0462962962963 | 12100 | 2015 | 3 | 2015_03_Asomata_english.xlsx
13 | 755 | 685 | 1440 | 0 | 0 | 6 | 1440 | 109 | 14.5 | 13.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 83.65 | 5960.00000000002 | 41.2595 | 2936.1150000000084 | -1919.9999999999936 | 12480 | 14400 | 10 | 88.1080432172869 | 12296.55 | 0 | 243.450000000008 | 60 |  | 166.66666666666666 | 14400 | 2015 | 3 | 2015_03_Asomata_english.xlsx
14 | 145 | 695 | 840 | 0 | 0 | 6 | 840 | 90 | 3.2999999999956344 | 14.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.15 | 7160.00000000002 | 41.319 | 3005.7300000000064 | 1200 | 9768 | 8568 | 10.2 | 85.355755588119 | 9782 | 0 | 46 | 60 |  | 99.16666666666667 | 8568 | 2015 | 3 | 2015_03_Asomata_english.xlsx
15 | 490 | 215 | 705 | 0 | 0 | 7 | 705 | 110 | 10.400000000001455 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84 | 6800.000000000007 | 41.64 | 3381.3 | -360.00000000001273 | 9116.882978723392 | 7120.5 | 10.1 | 86.50872230080151 | 8856 | 2356.3829787234044 | 320.8829787233917 | 60 |  | 82.41319444444444 | 7120.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
16 | 375 | 355 | 730 | 0 | 0 | 4 | 730 | 110 | 6.900000000001455 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 82.6 | 3519.9999999999873 | 41.78 | 3545.1 | -3280.00000000002 | 7472.912087912067 | 7665 | 10.5 | 86.08257095941826 | 7507.6 | 3087.912087912088 | 65.31208791206791 | 100 |  | 88.71527777777777 | 7665 | 2015 | 3 | 2015_03_Asomata_english.xlsx
17 | 270 | 575 | 845 | 0 | 0 | 4 | 845 | 108 | 5.799999999995634 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 17 | 83 | 4400 | 41.802 | 3570.84 | 880.0000000000127 | 9752.500000000013 | 8872.5 | 10.5 | 85.24274099883856 | 9752.6 | 0 | 59.90000000001055 | 60 |  | 102.69097222222223 | 8872.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
18 | 250 | 610 | 860 | 0 | 0 | 5 | 860 | 109 | 4.80000000000291 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 83.4 | 5360.00000000002 | 41.451 | 3160.17 | 960.00000000002 | 9990.00000000002 | 9030 | 10.5 | 84.41913963653093 | 10026.75 | 0 | 63.25000000002001 | 100 |  | 104.51388888888889 | 9030 | 2015 | 3 | 2015_03_Asomata_english.xlsx
19 | 0 | 815 | 815 | 0 | 0 | 5 | 815 | 54 | 0 | 15.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 83.7 | 6080.000000000014 | 41.32 | 3006.9 | 719.9999999999936 | 8951.499999999993 | 8231.5 | 10.1 | 87.13108720944037 | 8856 | 0 | 155.49999999999272 | 60 |  | 95.27199074074075 | 8231.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
20 | 245 | 580 | 825 | 0 | 0 | 4 | 825 | 110 | 4.75 | 11.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 83.35 | 5239.999999999993 | 41.684 | 3432.78 | -840.0000000000209 | 7822.499999999979 | 8662.5 | 10.5 | 84.5212184027178 | 7830 | 0 | 12.499999999979082 | 20 |  | 100.26041666666667 | 8662.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
21 | 230 | 285 | 515 | 0 | 0 | 4 | 515 | 109 | 4.25 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 84 | 6800.000000000007 | 40.96 | 2585.7 | 1560.0000000000146 | 6761.500000000015 | 5201.5 | 10.1 | 86.50872230080151 | 6651.75 | 0 | 169.75000000001455 | 60 |  | 60.2025462962963 | 5201.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
22 | 220 | 380 | 600 | 0 | 0 | 4 | 600 | 109 | 4.099999999998545 | 8.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.85 | 8839.999999999993 | 41.4 | 3100.5 | 2039.9999999999854 | 7949.999999999985 | 5910 | 9.85 | 86.94477844446158 | 7803 | 0 | 146.99999999998545 | 0 |  | 68.40277777777777 | 5910 | 2015 | 3 | 2015_03_Asomata_english.xlsx
23 | 450 | 240 | 690 | 0 | 0 | 6 | 690 | 109 | 8.30000000000291 | 4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84 | 6800.000000000007 | 41.001 | 2633.6699999999937 | -2039.9999999999854 | 7878.393617021291 | 7003.5 | 10.15 | 86.08257095941825 | 7920.5 | 2914.8936170212764 | 17.893617021291902 | 60 |  | 81.05902777777777 | 7003.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
24 | 235 | 335 | 570 | 0 | 0 | 5 | 570 | 110 | 4.299999999995634 | 6.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.05 | 6920 | 41.53 | 3252.6 | 119.99999999999272 | 7853.717948717942 | 5985 | 10.5 | 83.11420644357625 | 7460.25 | 1748.7179487179487 | 393.4679487179419 | 0 |  | 69.27083333333333 | 5985 | 2015 | 3 | 2015_03_Asomata_english.xlsx
25 | 485 | 275 | 760 | 0 | 0 | 4 | 760 | 109 | 8.900000000001455 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.1 | 7039.999999999993 | 40.851 | 2458.17 | 119.99999999999272 | 9593.872340425525 | 7676 | 10.1 | 86.3032383998495 | 9453.5 | 1797.872340425532 | 200.37234042552518 | 60 |  | 88.8425925925926 | 7676 | 2015 | 3 | 2015_03_Asomata_english.xlsx
26 | 395 | 395 | 790 | 0 | 0 | 4 | 790 | 109 | 7.30000000000291 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.75 | 8600.000000000007 | 41.712 | 3465.5400000000086 | 1560.0000000000146 | 12485.808510638311 | 7979 | 10.1 | 84.9910254183313 | 12445.25 | 2946.808510638298 | 100.55851063831142 | 60 |  | 92.34953703703704 | 7979 | 2015 | 3 | 2015_03_Asomata_english.xlsx
27 | 550 | 365 | 915 | 0 | 0 | 4 | 915 | 110 | 11 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.5 | 8000.000000000007 | 41.103 | 2753.01 | -600 | 10997.882978723404 | 9241.5 | 10.1 | 85.49097262667443 | 10669.48 | 2356.3829787234044 | 388.4029787234049 | 60 |  | 106.96180555555556 | 9241.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
28 | 270 | 125 | 395 | 0 | 0 | 4 | 395 | 55 | 5.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 83.55 | 5720 | 39.7839 | 1209.6630000000036 | -2280.0000000000073 | 4570.111020185481 | 3989.5 | 10.1 | 87.44563987084629 | 4418.7 | 2860.611020185488 | 151.411020185481 | 0 |  | 46.17476851851852 | 3989.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
29 | 235 | 315 | 550 | 0 | 0 | 4 | 550 | 110 | 5.099999999998545 | 7.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 29 | 84 | 6800.000000000007 | 40.28 | 1790.1 | 1080.0000000000073 | 6635.000000000007 | 5555 | 10.1 | 86.50872230080151 | 6450 | 0 | 185.00000000000728 | 0 |  | 64.29398148148148 | 5555 | 2015 | 3 | 2015_03_Asomata_english.xlsx
30 | 465 | 0 | 465 | 0 | 0 | 5 | 465 | 44 | 10.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.4 | 7760.00000000002 | 39.932 | 1382.94 | 960.0000000000127 | 7958.489285714298 | 4712.775 | 10.135 | 85.39667321350447 | 7467.9 | 2285.7142857142853 | 490.58928571429806 | 0 |  | 54.54600694444444 | 4712.775000000001 | 2015 | 3 | 2015_03_Asomata_english.xlsx
31 | 95 | 60 | 155 | 0 | 0 | 4 | 155 | 70 | 2.599999999998545 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.2 | 7280.000000000014 | 41.3 | 2983.5 | -480.00000000000637 | 4005.7127659574403 | 1565.5 | 10.1 | 86.09872835624795 | 2825.1 | 2920.2127659574467 | 1240.6127659574404 | 60 |  | 18.119212962962962 | 1565.5 | 2015 | 3 | 2015_03_Asomata_english.xlsx
1 | 525 | 240 | 765 | 0 | 0 | 3 | 765 | 110 | 10 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 85.25 | 9800.000000000007 | 40.95 | 2574 | 1680.0000000000073 | 11378.545918367354 | 7458.75 | 9.75 | 87.02415888543057 | 11225.8 | 2239.795918367347 | 212.74591836735271 | 60 |  | 86.328125 | 7458.75 | 2015 | 4 | 2015_04_Asomata_english.xlsx
2 | 490 | 495 | 985 | 0 | 0 | 4 | 985 | 109 | 9.700000000004366 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 2 | 84.5 | 8000.000000000007 | 41.49 | 3205.8 | -1800 | 10717.27027027027 | 10047 | 10.2 | 84.65282583621685 | 10738 | 2470.2702702702704 | 39.270270270269975 | 60 |  | 116.28472222222223 | 10047 | 2015 | 4 | 2015_04_Asomata_english.xlsx
3 | 525 | 485 | 1010 | 0 | 0 | 4 | 1010 | 109 | 10.099999999998545 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.35 | 7639.999999999993 | 42.041 | 3850.4699999999934 | -360.00000000001455 | 9638.999999999985 | 9999 | 9.9 | 87.52698174185778 | 9446.2 | 0 | 252.79999999998472 | 60 |  | 115.72916666666667 | 9999 | 2015 | 4 | 2015_04_Asomata_english.xlsx
4 | 510 | 465 | 975 | 0 | 0 | 4 | 975 | 109 | 10.400000000001455 | 9.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84.6 | 8239.999999999993 | 41.9589 | 3754.4130000000036 | 600 | 10350 | 9750 | 10 | 86.14319248826293 | 10336.8 | 0 | 73.20000000000073 | 60 |  | 112.84722222222223 | 9750 | 2015 | 4 | 2015_04_Asomata_english.xlsx
5 | 470 | 525 | 995 | 0 | 0 | 4 | 995 | 109 | 9.599999999998545 | 10.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 84.3 | 7520 | 41.6485 | 3391.2449999999935 | -719.9999999999927 | 9203.875000000007 | 9923.875 | 9.973743718592965 | 86.98252087038587 | 9234.5 | 0 | 29.375000000007276 | 60 |  | 114.85966435185185 | 9923.875 | 2015 | 4 | 2015_04_Asomata_english.xlsx
6 | 455 | 470 | 925 | 0 | 0 | 4 | 925 | 109 | 8.650000000001455 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 6 | 84.25 | 7400.000000000007 | 41.13 | 2784.6 | -119.99999999999272 | 9222.500000000007 | 9342.5 | 10.1 | 85.99683637002754 | 9007.15 | 0 | 275.35000000000764 | 60 |  | 108.13078703703704 | 9342.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
7 | 520 | 460 | 980 | 0 | 0 | 4 | 980 | 109 | 9.5 | 9.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 7 | 84.3 | 7520 | 41.22 | 2889.9 | 119.99999999999272 | 12215.33678756476 | 9800 | 10 | 86.75413711583924 | 12054 | 2295.336787564767 | 221.33678756476183 | 60 |  | 113.42592592592592 | 9800 | 2015 | 4 | 2015_04_Asomata_english.xlsx
8 | 500 | 530 | 1030 | 0 | 0 | 4 | 1030 | 109 | 9.549999999995634 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 84.6 | 8239.999999999993 | 41.488 | 3203.46 | 719.9999999999927 | 10814 | 10094 | 9.8 | 87.90121682475808 | 10679.9 | 0 | 194.0999999999949 | 60 |  | 116.82870370370371 | 10094 | 2015 | 4 | 2015_04_Asomata_english.xlsx
9 | 760 | 270 | 1030 | 0 | 0 | 4 | 1030 | 110 | 15.5 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.95 | 9080.000000000015 | 41.98 | 3779.1 | 840.0000000000218 | 12903.157894736863 | 10300 | 10 | 85.44121071012806 | 12609.6 | 1763.157894736842 | 293.5578947368613 | 0 |  | 119.21296296296296 | 10300 | 2015 | 4 | 2015_04_Asomata_english.xlsx
10 | 420 | 340 | 760 | 0 | 0 | 4 | 760 | 110 | 8.30000000000291 | 6.5 | 0 | 0 | 1.15 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | ΒΛΑΒΗ ΦΡΕΝΩΝ | 10 | 83.7 | 6080.000000000014 | 41.63 | 3369.6 | -3000 | 8259.574468085106 | 7600 | 10 | 88.00239808153478 | 7976.4 | 3659.574468085106 | 343.1744680851052 | 60 |  | 87.96296296296296 | 7600 | 2015 | 4 | 2015_04_Asomata_english.xlsx
11 | 565 | 410 | 975 | 0 | 0 | 4 | 975 | 110 | 11.099999999998545 | 7.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 84.45 | 7880.000000000014 | 41.68 | 3428.1 | 1800 | 11647.5 | 9847.5 | 10.1 | 85.5916687075068 | 11598.9 | 0 | 108.59999999999854 | 60 |  | 113.97569444444444 | 9847.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
12 | 310 | 245 | 555 | 0 | 0 | 4 | 555 | 110 | 6.30000000000291 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 85.1 | 9439.999999999993 | 41.302 | 2985.84 | 1559.999999999979 | 11856.989361702108 | 5605.5 | 10.1 | 84.30084307734718 | 11736.12 | 4691.489361702128 | 180.8693617021072 | 60 |  | 64.87847222222223 | 5605.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
13 | 330 | 275 | 605 | 0 | 0 | 4 | 605 | 110 | 6.799999999995634 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.9 | 8960.00000000002 | 41.452 | 3161.34 | -479.9999999999727 | 9109.44736842108 | 6110.5 | 10.1 | 84.6938540007847 | 9125 | 3478.947368421053 | 44.44736842108068 | 60 |  | 70.72337962962963 | 6110.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
14 | 775 | 605 | 1380 | 0 | 0 | 4 | 1380 | 110 | 15.400000000001455 | 11.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.7 | 8480.000000000015 | 41.947 | 3740.4900000000084 | -480.00000000000546 | 13044 | 13524 | 9.8 | 87.6953591741146 | 12811.5 | 0 | 232.49999999999454 | 0 |  | 156.52777777777777 | 13524 | 2015 | 4 | 2015_04_Asomata_english.xlsx
15 | 570 | 595 | 1165 | 0 | 0 | 4 | 1165 | 110 | 12.200000000004366 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 84.8 | 8720 | 41.852 | 3629.34 | 239.99999999998545 | 11831.75 | 11591.75 | 9.95 | 86.17151176442964 | 11689.05 | 0 | 142.69999999998436 | 0 |  | 134.16377314814815 | 11591.75 | 2015 | 4 | 2015_04_Asomata_english.xlsx
16 | 610 | 485 | 1095 | 0 | 0 | 4 | 1095 | 109 | 12.599999999998545 | 11.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 16 | 84.05 | 6920 | 41.611 | 3347.3699999999935 | -1800 | 9259.5 | 11059.5 | 10.1 | 86.4058581839159 | 8957.76 | 0 | 361.7400000000016 | 60 |  | 128.00347222222223 | 11059.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
17 | 545 | 445 | 990 | 0 | 0 | 4 | 990 | 110 | 9.599999999998545 | 6.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 17 | 84.4 | 7760.00000000002 | 41.4 | 3100.5 | 840.00000000002 | 10839 | 9999 | 10.1 | 85.69260227909582 | 10855.9 | 0 | 43.10000000002037 | 60 |  | 115.72916666666667 | 9999 | 2015 | 4 | 2015_04_Asomata_english.xlsx
18 | 545 | 450 | 995 | 0 | 0 | 4 | 995 | 110 | 10.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.6 | 8239.999999999993 | 42.02 | 3825.9 | 479.9999999999727 | 10529.5 | 10049.5 | 10.1 | 85.29028959233953 | 10168.9 | 0 | 420.5999999999731 | 60 |  | 116.3136574074074 | 10049.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
19 | 650 | 385 | 1035 | 0 | 0 | 4 | 1035 | 110 | 13.30000000000291 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 83 | 4400 | 41.14 | 2796.3 | -3839.9999999999927 | 9478.085106382987 | 10350 | 10 | 89.50487804878048 | 9562 | 2968.0851063829787 | 16.08510638298685 | 100 |  | 119.79166666666667 | 10350 | 2015 | 4 | 2015_04_Asomata_english.xlsx
20 | 885 | 300 | 1185 | 0 | 0 | 4 | 1185 | 110 | 18.299999999995634 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 83.6 | 5839.999999999993 | 42.15 | 3978 | 1439.9999999999927 | 13764 | 12324 | 10.4 | 84.82109837278108 | 13859.2 | 0 | 14.799999999991996 | 110 |  | 142.63888888888889 | 12324 | 2015 | 4 | 2015_04_Asomata_english.xlsx
21 | 395 | 715 | 1110 | 0 | 0 | 4 | 1110 | 110 | 7.400000000001455 | 15.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 83.55 | 5720 | 42.1 | 3919.5 | -119.99999999999272 | 11313 | 11433 | 10.3 | 85.7476662811211 | 11343.6 | 0 | 29.40000000000873 | 60 |  | 132.3263888888889 | 11433 | 2015 | 4 | 2015_04_Asomata_english.xlsx
22 | 515 | 645 | 1160 | 0 | 0 | 4 | 1160 | 110 | 10.099999999998545 | 12.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84.5 | 8000.000000000007 | 41.65 | 3393 | 2280.0000000000073 | 13996 | 11716 | 10.1 | 85.49097262667443 | 13738.6 | 0 | 317.40000000000873 | 60 |  | 135.60185185185185 | 11716 | 2015 | 4 | 2015_04_Asomata_english.xlsx
23 | 460 | 530 | 990 | 0 | 0 | 4 | 990 | 110 | 8.30000000000291 | 10.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 23 | 84.6 | 8239.999999999993 | 41.25 | 2925 | 239.99999999998545 | 10041 | 9801 | 9.9 | 87.01332574572012 | 9954.2 | 0 | 146.79999999998654 | 60 |  | 113.4375 | 9801 | 2015 | 4 | 2015_04_Asomata_english.xlsx
24 | 585 | 535 | 1120 | 0 | 0 | 4 | 1120 | 110 | 11.849999999998545 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 85.05 | 9320 | 41.34 | 3030.3 | 1080.0000000000073 | 12280 | 11200 | 10 | 85.24274099883856 | 12293.2 | 0 | 46.80000000000837 | 60 |  | 129.62962962962962 | 11200 | 2015 | 4 | 2015_04_Asomata_english.xlsx
25 | 460 | 445 | 905 | 0 | 0 | 4 | 905 | 109 | 10.55000000000291 | 9.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 25 | 85 | 9200.000000000007 | 41.8008 | 3569.4359999999992 | -119.99999999999272 | 8839.500000000007 | 8959.5 | 9.9 | 86.20389945971341 | 8776.4 | 0 | 123.10000000000764 | 60 |  | 103.69791666666667 | 8959.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
26 | 240 | 295 | 535 | 0 | 0 | 4 | 535 | 109 | 3.9499999999970896 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.1 | 7039.999999999993 | 40.96 | 2585.7 | -2160.0000000000146 | 6328.29787234041 | 5350 | 10 | 87.16627078384799 | 6119.8 | 3138.2978723404253 | 268.49787234041014 | 60 |  | 61.9212962962963 | 5350 | 2015 | 4 | 2015_04_Asomata_english.xlsx
27 | 355 | 355 | 710 | 0 | 0 | 3 | 710 | 109 | 8.05000000000291 | 7.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 27 | 83.9 | 6560.00000000002 | 40.198 | 1694.16 | -479.9999999999727 | 7046.000000000027 | 7526 | 10.6 | 82.6248480208943 | 6962.4 | 0 | 143.60000000002583 | 60 |  | 87.10648148148148 | 7526 | 2015 | 4 | 2015_04_Asomata_english.xlsx
28 | 420 | 175 | 595 | 0 | 0 | 4 | 595 | 110 | 8.19999999999709 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84.05 | 6920 | 41.798 | 3566.16 | 359.99999999998 | 9020.228723404234 | 6277.25 | 10.55 | 82.72030025190053 | 9037.4 | 2382.978723404255 | 42.82872340423455 | 60 |  | 72.65335648148148 | 6277.25 | 2015 | 4 | 2015_04_Asomata_english.xlsx
29 | 220 | 535 | 755 | 0 | 0 | 4 | 755 | 110 | 3.900000000001455 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 29 | 84.3 | 7520 | 41.65 | 3393 | 600 | 9910.638297872341 | 7550 | 10 | 86.75413711583924 | 9792 | 1760.6382978723404 | 178.63829787234135 | 60 |  | 87.38425925925925 | 7550 | 2015 | 4 | 2015_04_Asomata_english.xlsx
30 | 330 | 305 | 635 | 0 | 0 | 4 | 635 | 103 | 7.099999999998545 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.95 | 9080.000000000015 | 40.85 | 2457 | 1560.0000000000146 | 7846.500000000015 | 6286.5 | 9.9 | 86.30425324255359 | 7540.6 | 0 | 365.9000000000142 | 60 |  | 72.76041666666667 | 6286.5 | 2015 | 4 | 2015_04_Asomata_english.xlsx
1 | 340 | 250 | 590 | 0 | 0 | 4 | 590 | 110 | 6.80000000000291 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.9 | 8960.00000000002 | 41.5 | 3217.5 | -119.99999999999454 | 6461.34042553192 | 5959 | 10.1 | 84.6938540007847 | 6307.2 | 622.3404255319149 | 214.1404255319203 | 60 |  | 68.9699074074074 | 5959 | 2015 | 5 | 2015_05_Asomata_english.xlsx
2 | 695 | 350 | 1045 | 0 | 0 | 4 | 1045 | 110 | 14.5 | 7.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.5 | 8000.000000000007 | 42.07 | 3884.4 | -960.0000000000127 | 9280.999999999989 | 10241 | 9.8 | 88.10804321728689 | 9108 | 0 | 232.9999999999891 | 60 |  | 118.53009259259261 | 10241 | 2015 | 5 | 2015_05_Asomata_english.xlsx
3 | 340 | 260 | 600 | 0 | 0 | 3 | 600 | 110 | 6.19999999999709 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.35 | 7639.999999999993 | 42.14989 | 3977.8712999999952 | -360.00000000001455 | 5879.999999999985 | 6240 | 10.4 | 83.31895377349925 | 5850.6 | 0 | 89.39999999998508 | 60 |  | 72.22222222222223 | 6240 | 2015 | 5 | 2015_05_Asomata_english.xlsx
4 | 60 | 665 | 725 | 0 | 0 | 3 | 725 | 110 | 1.4000000000014552 | 13.5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ Δ/Κ Ρ10 | 4 | 84.75 | 8600.000000000007 | 40.79 | 2386.8 | 960.0000000000146 | 8137.500000000015 | 7177.5 | 9.9 | 86.70801583082284 | 7866.8 | 0 | 270.7000000000153 | 0 |  | 83.07291666666667 | 7177.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
5 | 0 | 805 | 805 | 0 | 0 | 4 | 805 | 55 | 0 | 17.30000000000291 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 5 | 84.55 | 8120 | 40.97 | 2597.4 | -480.0000000000073 | 7650.499999999993 | 8130.5 | 10.1 | 85.39051319938106 | 7803.7 | 0 | 46.799999999993815 | 200 |  | 94.10300925925925 | 8130.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
6 | 0 | 865 | 865 | 0 | 0 | 4 | 865 | 54 | 0 | 16.799999999995634 | 0 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 6 | 84.4 | 7760.00000000002 | 40.901 | 2516.67 | -359.99999999998 | 8376.50000000002 | 8736.5 | 10.1 | 85.69260227909582 | 8006.4 | 0 | 430.10000000001946 | 60 |  | 101.11689814814815 | 8736.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
7 | 0 | 665 | 665 | 0 | 0 | 4 | 665 | 55 | 0 | 13.80000000000291 | 0 | 0 | 15.75 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ Δ/Κ Ρ10 | 7 | 83.55 | 5720 | 40.589 | 2151.63 | -2040.00000000002 | 4809.499999999981 | 6849.5 | 10.3 | 85.74766628112113 | 4886 | 0 | 23.4999999999809 | 100 |  | 79.27662037037038 | 6849.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
8 | 0 | 360 | 360 | 0 | 0 | 4 | 360 | 55 | 0 | 7.099999999998545 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 8 | 84.5 | 8000.000000000007 | 40.498 | 2045.16 | 2280.0000000000073 | 5808.000000000007 | 3528 | 9.8 | 88.1080432172869 | 5472 | 0 | 396.0000000000073 | 60 |  | 40.833333333333336 | 3528 | 2015 | 5 | 2015_05_Asomata_english.xlsx
9 | 0 | 585 | 585 | 0 | 0 | 4 | 585 | 55 | 0 | 12.099999999998545 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ Δ/Κ Ρ10 | 9 | 84.85 | 8839.999999999993 | 41.852 | 3629.34 | 839.9999999999854 | 6748.499999999985 | 5908.5 | 10.1 | 84.79267996811352 | 6600 | 0 | 208.49999999998545 | 60 |  | 68.38541666666667 | 5908.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
10 | 85 | 340 | 425 | 0 | 0 | 4 | 425 | 55 | 29.94999999999709 | 8.5 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 10 | 84.4 | 7760.00000000002 | 40.399 | 1929.33 | -1079.9999999999727 | 6338.154450261807 | 4292.5 | 10.1 | 85.69260227909582 | 6225.45 | 3125.65445026178 | 172.70445026180732 | 60 |  | 49.68171296296296 | 4292.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
11 | 655 | 20 | 675 | 0 | 0 | 4 | 675 | 100 | 13.75 | 0.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.15 | 7160.00000000002 | 41.08 | 2726.1 | -600 | 6285 | 6885 | 10.2 | 85.355755588119 | 6329.1 | 0 | 15.899999999999636 | 60 |  | 79.6875 | 6885 | 2015 | 5 | 2015_05_Asomata_english.xlsx
12 | 350 | 235 | 585 | 0 | 0 | 4 | 585 | 110 | 7.700000000004366 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 85.15 | 9560.00000000002 | 41.638 | 3378.96 | 2400 | 8103.75 | 5703.75 | 9.75 | 87.22583712154974 | 7871.85 | 0 | 231.9 | 0 |  | 66.015625 | 5703.75 | 2015 | 5 | 2015_05_Asomata_english.xlsx
13 | 400 | 120 | 520 | 0 | 0 | 0 | 520 | 109 | 8.099999999998545 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.75 | 8600.000000000007 | 40.41 | 1942.1999999999946 | -960.0000000000127 | 7846.382978723392 | 5200 | 10 | 85.84093567251462 | 7759.9 | 3606.3829787234044 | 146.48297872339208 | 60 |  | 60.18518518518518 | 5200 | 2015 | 5 | 2015_05_Asomata_english.xlsx
14 | 500 | 0 | 500 | 0 | 0 | 5 | 500 | 55 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 85.25 | 9800.000000000007 | 40.881 | 2493.27 | 1200 | 7845.20725388601 | 4925 | 9.85 | 86.14066488659371 | 7776.3 | 1720.2072538860102 | 128.90725388601095 | 60 |  | 57.00231481481482 | 4925 | 2015 | 5 | 2015_05_Asomata_english.xlsx
15 | 400 | 195 | 595 | 0 | 0 | 4 | 595 | 110 | 9.099999999998545 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 84.8 | 8720 | 41.381 | 3078.27 | -1080.0000000000073 | 7689.335106382971 | 5801.25 | 9.75 | 87.93913251857178 | 7465.8 | 2968.0851063829787 | 223.5351063829703 | 0 |  | 67.14409722222223 | 5801.25 | 2015 | 5 | 2015_05_Asomata_english.xlsx
16 | 420 | 115 | 535 | 0 | 0 | 3 | 535 | 110 | 8.60000000000582 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.4 | 7760.00000000002 | 41.88 | 3662.1 | -959.99999999998 | 5611.0675675675875 | 5403.5 | 10.1 | 85.69260227909582 | 5580.6 | 1167.5675675675675 | 30.46756756758805 | 0 |  | 62.54050925925926 | 5403.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
17 | 250 | 190 | 440 | 0 | 0 | 4 | 440 | 109 | 5.19999999999709 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.5 | 8000.000000000007 | 42.002 | 3804.84 | 239.99999999998727 | 4705.999999999987 | 4466 | 10.15 | 85.06983483048391 | 4630.5 | 0 | 75.49999999998727 | 0 |  | 51.68981481481482 | 4466 | 2015 | 5 | 2015_05_Asomata_english.xlsx
18 | 315 | 460 | 775 | 0 | 0 | 4 | 775 | 110 | 6.599999999998545 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.1 | 7039.999999999993 | 42 | 3802.5 | -960.0000000000146 | 6867.499999999985 | 7827.5 | 10.1 | 86.3032383998495 | 6792.5 | 0 | 134.99999999998545 | 60 |  | 90.59606481481481 | 7827.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
19 | 385 | 35 | 420 | 0 | 0 | 3 | 420 | 100 | 8.200000000004366 | 0.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.15 | 7160.00000000002 | 41.398 | 3098.16 | 120.00000000002728 | 4573.750000000027 | 4453.75 | 10.604166666666666 | 82.10251067965237 | 4494 | 0 | 79.75000000002728 | 0 |  | 51.548032407407405 | 4453.75 | 2015 | 5 | 2015_05_Asomata_english.xlsx
20 | 230 | 220 | 450 | 0 | 0 | 4 | 450 | 55 | 4.44999999999709 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.4 | 7760.00000000002 | 41.702 | 3453.84 | 600 | 4942.5 | 4342.5 | 9.65 | 89.68863036464951 | 4899.95 | 0 | 42.55000000000018 | 0 |  | 50.260416666666664 | 4342.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
21 | 340 | 115 | 455 | 0 | 0 | 4 | 455 | 108 | 7.05000000000291 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85.05 | 9320 | 41.8 | 3568.5 | 1559.99999999998 | 6109.99999999998 | 4550 | 10 | 85.24274099883856 | 5963.1 | 0 | 146.89999999997963 | 0 |  | 52.66203703703704 | 4550 | 2015 | 5 | 2015_05_Asomata_english.xlsx
22 | 470 | 380 | 850 | 0 | 0 | 3 | 850 | 109 | 9 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 83.8 | 6320 | 41.24 | 2913.3 | -3000 | 5415 | 8415 | 9.9 | 88.67865255425065 | 5340 | 0 | 75 | 0 |  | 97.39583333333333 | 8415 | 2015 | 5 | 2015_05_Asomata_english.xlsx
23 | 355 | 115 | 470 | 0 | 0 | 3 | 470 | 110 | 8.19999999999709 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.5 | 8000.000000000007 | 41.75 | 3510 | 1680.0000000000073 | 6215.500000000007 | 4535.5 | 9.65 | 89.47759829320329 | 6205.85 | 0 | 69.65000000000691 | 60 |  | 52.49421296296296 | 4535.5 | 2015 | 5 | 2015_05_Asomata_english.xlsx
24 | 255 | 145 | 400 | 0 | 0 | 4 | 400 | 108 | 5.099999999998545 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83 | 4400 | 41.538 | 3261.9599999999914 | -3600.0000000000073 | 3971.3513513513444 | 4220 | 10.55 | 84.8387469656687 | 3990 | 3351.3513513513517 | 41.35135135134442 | 60 |  | 48.842592592592595 | 4220 | 2015 | 5 | 2015_05_Asomata_english.xlsx
25 | 50 | 300 | 350 | 0 | 0 | 4 | 350 | 55 | 1 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 83.25 | 5000.000000000007 | 41.192 | 2857.14 | 600.0000000000073 | 4310.000000000007 | 3710 | 10.6 | 83.92681532304174 | 4416 | 0 | 14.000000000007276 | 120 |  | 42.93981481481482 | 3710 | 2015 | 5 | 2015_05_Asomata_english.xlsx
26 | 0 | 485 | 485 | 0 | 0 | 4 | 485 | 55 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 83.05 | 4520 | 41.499 | 3216.3300000000063 | -480.0000000000073 | 4491.249999999993 | 4971.25 | 10.25 | 87.21547191111375 | 4406.4 | 0 | 84.84999999999218 | 0 |  | 57.53761574074074 | 4971.25 | 2015 | 5 | 2015_05_Asomata_english.xlsx
27 | 370 | 85 | 455 | 0 | 0 | 4 | 455 | 105 | 7.200000000004366 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 83.75 | 6200.000000000007 | 41.399 | 3099.33 | 1680.0000000000073 | 6116.250000000007 | 4436.25 | 9.75 | 90.15077537233226 | 6066.3 | 0 | 49.950000000008004 | 0 |  | 51.345486111111114 | 4436.25 | 2015 | 5 | 2015_05_Asomata_english.xlsx
28 | 485 | 0 | 485 | 0 | 0 | 4 | 485 | 55 | 9.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.9 | 8960.00000000002 | 41.662 | 3407.04 | 2760.0000000000127 | 7513.000000000013 | 4753 | 9.8 | 87.2865230008087 | 7286.1 | 0 | 226.90000000001237 | 0 |  | 55.011574074074076 | 4753 | 2015 | 5 | 2015_05_Asomata_english.xlsx
29 | 440 | 100 | 540 | 0 | 0 | 4 | 540 | 70 | 9.599999999998545 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.7 | 8480.000000000015 | 42.05 | 3861 | -480.00000000000546 | 4838.9999999999945 | 5319 | 9.85 | 87.25020506663179 | 4773 | 0 | 125.99999999999454 | 60 |  | 61.5625 | 5319 | 2015 | 5 | 2015_05_Asomata_english.xlsx
30 | 365 | 115 | 480 | 0 | 0 | 4 | 480 | 109 | 6.900000000001455 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 30 | 85 | 9200.000000000007 | 42.05 | 3861 | 719.9999999999927 | 5399.999999999993 | 4680 | 9.75 | 87.53011329755516 | 5357.6 | 0 | 42.39999999999236 | 0 |  | 54.166666666666664 | 4680 | 2015 | 5 | 2015_05_Asomata_english.xlsx
31 | 0 | 385 | 385 | 0 | 0 | 3 | 385 | 55 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 31 | 85.2 | 9680.000000000015 | 41.25 | 2925 | 480.0000000000073 | 4195.250000000007 | 3715.25 | 9.65 | 88.02772980234118 | 3572.55 | 0 | 622.7000000000071 | 0 |  | 43.0005787037037 | 3715.25 | 2015 | 5 | 2015_05_Asomata_english.xlsx
1 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 54 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 85.3 | 9920 | 41.3 | 2983.5 | 239.99999999998545 | 4481.999999999985 | 4242 | 10.1 | 83.91146273980748 | 4097.5 | 0 | 384.49999999998545 | 0 |  | 49.09722222222222 | 4242 | 2015 | 6 | 2015_06_Asomata_english.xlsx
2 | 460 | 0 | 460 | 0 | 0 | 3 | 460 | 54 | 9.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 85.15 | 9560.00000000002 | 41.448 | 3156.66 | -359.99999999998 | 4079.00000000002 | 4439 | 9.65 | 88.12973180674715 | 3775 | 0 | 304.00000000002 | 0 |  | 51.37731481481482 | 4439 | 2015 | 6 | 2015_06_Asomata_english.xlsx
3 | 490 | 0 | 490 | 0 | 0 | 4 | 490 | 54 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 83.9 | 6560.00000000002 | 41.638 | 3378.96 | -3000 | 4310.702127659575 | 4949 | 10.1 | 86.71518703182966 | 4125.1 | 2361.7021276595747 | 245.60212765957567 | 60 |  | 57.280092592592595 | 4949 | 2015 | 6 | 2015_06_Asomata_english.xlsx
4 | 355 | 145 | 500 | 0 | 0 | 4 | 500 | 90 | 7.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 83.8 | 6320 | 42.0305 | 3838.185000000002 | -240.00000000002 | 4909.99999999998 | 5150 | 10.3 | 85.23482138709527 | 4912.9 | 0 | 57.099999999980355 | 60 |  | 59.60648148148148 | 5150 | 2015 | 6 | 2015_06_Asomata_english.xlsx
5 | 465 | 0 | 465 | 0 | 0 | 4 | 465 | 53 | 9.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 83.5 | 5600.000000000007 | 41.772 | 3535.74 | -719.9999999999927 | 3930.0000000000073 | 4650 | 10 | 88.42650602409638 | 3890.9 | 0 | 39.100000000007185 | 0 |  | 53.81944444444444 | 4650 | 2015 | 6 | 2015_06_Asomata_english.xlsx
6 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 50 | 9.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 83.85 | 6439.999999999993 | 41.648 | 3390.66 | 839.9999999999854 | 5249.999999999985 | 4410 | 9.8 | 89.47650744885767 | 5183 | 0 | 126.99999999998545 | 60 |  | 51.041666666666664 | 4410 | 2015 | 6 | 2015_06_Asomata_english.xlsx
7 | 400 | 105 | 505 | 0 | 0 | 4 | 505 | 70 | 8.700000000004366 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.4 | 7760.00000000002 | 41.83 | 3603.6 | 1320.0000000000273 | 7611.989361702155 | 5100.5 | 10.1 | 85.69260227909582 | 7368.05 | 1191.4893617021276 | 243.9393617021551 | 0 |  | 59.03356481481482 | 5100.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
8 | 535 | 205 | 740 | 0 | 0 | 3 | 740 | 108 | 12.400000000001455 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 84.55 | 8120 | 41.632 | 3371.94 | 359.99999999998 | 7759.99999999998 | 7400 | 10 | 86.24441833137486 | 7701.5 | 0 | 58.49999999997999 | 0 |  | 85.64814814814815 | 7400 | 2015 | 6 | 2015_06_Asomata_english.xlsx
9 | 525 | 10 | 535 | 0 | 0 | 3 | 535 | 100 | 10.89999999999418 | 0.20000000000436557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.25 | 7400.000000000007 | 41.649 | 3391.83 | -719.9999999999927 | 4552.250000000007 | 5272.25 | 9.854672897196261 | 88.1376841624437 | 4511.4 | 0 | 40.85000000000764 | 0 |  | 61.02141203703704 | 5272.25 | 2015 | 6 | 2015_06_Asomata_english.xlsx
10 | 590 | 0 | 590 | 0 | 0 | 3 | 590 | 53 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 41.898 | 3683.16 | 119.99999999999272 | 5842.999999999993 | 5723 | 9.7 | 89.43725475859716 | 5537 | 0 | 305.9999999999927 | 0 |  | 66.23842592592592 | 5723 | 2015 | 6 | 2015_06_Asomata_english.xlsx
11 | 0 | 495 | 495 | 0 | 0 | 3 | 495 | 50 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 84.15 | 7160.00000000002 | 41.849 | 3625.83 | -359.99999999998 | 4515.75000000002 | 4875.75 | 9.85 | 88.38870121815367 | 4440.2 | 0 | 75.55000000002019 | 0 |  | 56.432291666666664 | 4875.75 | 2015 | 6 | 2015_06_Asomata_english.xlsx
12 | 500 | 0 | 500 | 0 | 0 | 3 | 500 | 50 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.05 | 6920 | 41.97 | 3767.4 | -240.00000000002 | 4759.99999999998 | 5000 | 10 | 87.26991676575506 | 4684.2 | 0 | 135.79999999998017 | 60 |  | 57.870370370370374 | 5000 | 2015 | 6 | 2015_06_Asomata_english.xlsx
13 | 105 | 265 | 370 | 0 | 0 | 4 | 370 | 50 | 2 | 5.799999999995634 | 0 | 0 | 8.25 | 0 | 0 | 0 | 2.75 | 0 | 1 | 1 | ΒΛΑΒΗ 48V D.C. | 13 | 84.5 | 8000.000000000007 | 41.13 | 2784.6 | 1080.0000000000073 | 5921.542553191497 | 3607.5 | 9.75 | 88.55987933634992 | 5747.7 | 1234.0425531914893 | 173.84255319149725 | 0 |  | 41.75347222222222 | 3607.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
14 | 535 | 40 | 575 | 0 | 0 | 4 | 575 | 50 | 10.900000000001455 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.45 | 7880.000000000014 | 41.889 | 3672.6300000000065 | -119.99999999999363 | 5634.000000000006 | 5754 | 10.00695652173913 | 86.3874897495387 | 5572.5 | 0 | 61.50000000000637 | 0 |  | 66.59722222222223 | 5754 | 2015 | 6 | 2015_06_Asomata_english.xlsx
15 | 385 | 215 | 600 | 0 | 0 | 4 | 600 | 110 | 8.14999999999418 | 4.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84.45 | 7880.000000000014 | 41.598 | 3332.16 | 0 | 6120 | 6120 | 10.2 | 84.75253470057045 | 6130.6 | 0 | 49.399999999999636 | 60 |  | 70.83333333333333 | 6120 | 2015 | 6 | 2015_06_Asomata_english.xlsx
16 | 500 | 90 | 590 | 0 | 0 | 4 | 590 | 85 | 10.85000000000582 | 2.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84 | 6800.000000000007 | 41.901 | 3686.67 | -1080.0000000000064 | 4731.499999999994 | 5811.5 | 9.85 | 88.70437515107567 | 4509.5 | 0 | 221.99999999999363 | 0 |  | 67.26273148148148 | 5811.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
17 | 500 | 0 | 500 | 0 | 0 | 3 | 500 | 49 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.35 | 7639.999999999993 | 41.601 | 3335.67 | 839.9999999999854 | 5714.999999999985 | 4875 | 9.75 | 88.87355069173252 | 5594.4 | 0 | 180.5999999999849 | 60 |  | 56.423611111111114 | 4875 | 2015 | 6 | 2015_06_Asomata_english.xlsx
18 | 215 | 90 | 305 | 0 | 0 | 4 | 305 | 70 | 5.900000000001455 | 2.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 84.55 | 8120 | 41.602 | 3336.84 | 480.0000000000073 | 3560.5000000000073 | 3080.5 | 10.1 | 85.39051319938106 | 3538.75 | 0 | 21.750000000007276 | 0 |  | 35.65393518518518 | 3080.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
19 | 0 | 410 | 410 | 0 | 0 | 4 | 410 | 50 | 0 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.2 | 7280.000000000014 | 41.458 | 3168.36 | -839.9999999999864 | 3219.0000000000136 | 4059 | 9.9 | 87.83809660586911 | 3011.8 | 0 | 207.20000000001346 | 0 |  | 46.979166666666664 | 4059 | 2015 | 6 | 2015_06_Asomata_english.xlsx
20 | 90 | 235 | 325 | 0 | 0 | 3 | 325 | 100 | 2 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.4 | 7760.00000000002 | 41.001 | 2633.6699999999937 | 480.00000000000637 | 3616.2500000000064 | 3136.25 | 9.65 | 89.68863036464951 | 3457.9 | 0 | 158.35000000000628 | 0 |  | 36.29918981481482 | 3136.25 | 2015 | 6 | 2015_06_Asomata_english.xlsx
21 | 0 | 315 | 315 | 0 | 0 | 4 | 315 | 50 | 0 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.2 | 7280.000000000014 | 41.2 | 2866.5 | -480.00000000000637 | 4535.7765957446745 | 3244.5 | 10.3 | 84.42690838816544 | 4401.9 | 1771.276595744681 | 193.8765957446749 | 60 |  | 37.552083333333336 | 3244.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
22 | 285 | 95 | 380 | 0 | 0 | 3 | 380 | 70 | 6.099999999998545 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 83.6 | 5839.999999999993 | 42.119 | 3941.73 | -1440.000000000021 | 4720.936170212744 | 3762 | 9.9 | 89.10499222999223 | 4628.2 | 2398.936170212766 | 92.73617021274458 | 0 |  | 43.541666666666664 | 3762 | 2015 | 6 | 2015_06_Asomata_english.xlsx
23 | 225 | 210 | 435 | 0 | 0 | 4 | 435 | 55 | 4.19999999999709 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.6 | 5839.999999999993 | 41.4 | 3100.5 | 0 | 4632.75 | 4632.75 | 10.65 | 82.82999277717589 | 4571.4 | 0 | 61.350000000000364 | 0 |  | 53.619791666666664 | 4632.75 | 2015 | 6 | 2015_06_Asomata_english.xlsx
24 | 270 | 190 | 460 | 0 | 0 | 4 | 460 | 110 | 5.650000000001455 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83.8 | 6320 | 41.968 | 3765.06 | 480.0000000000073 | 5080.000000000007 | 4600 | 10 | 87.79186602870813 | 5058.9 | 0 | 81.10000000000764 | 60 |  | 53.24074074074074 | 4600 | 2015 | 6 | 2015_06_Asomata_english.xlsx
25 | 565 | 0 | 565 | 0 | 0 | 4 | 565 | 50 | 11.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 83.65 | 5960.00000000002 | 41.649 | 3391.83 | -359.99999999998 | 5346.50000000002 | 5706.5 | 10.1 | 87.23568635374941 | 5278 | 0 | 128.50000000002 | 60 |  | 66.04745370370371 | 5706.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
26 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 50 | 0 | 10.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.1 | 7039.999999999993 | 41.7 | 3451.5 | 1079.9999999999727 | 6179.999999999973 | 5100 | 10 | 87.16627078384799 | 6149 | 0 | 30.999999999972715 | 0 |  | 59.02777777777778 | 5100 | 2015 | 6 | 2015_06_Asomata_english.xlsx
27 | 420 | 0 | 420 | 0 | 0 | 3 | 420 | 50 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 85 | 9200.000000000007 | 41.15 | 2808 | 2160.0000000000146 | 6255.000000000015 | 4095 | 9.75 | 87.53011329755516 | 5920.2 | 0 | 334.80000000001473 | 0 |  | 47.395833333333336 | 4095 | 2015 | 6 | 2015_06_Asomata_english.xlsx
28 | 385 | 40 | 425 | 0 | 0 | 4 | 425 | 95 | 7.94999999999709 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 85.15 | 9560.00000000002 | 40.75 | 2340 | 360.00000000001273 | 4652.500000000013 | 4292.5 | 10.1 | 84.20315959753565 | 4580.6 | 0 | 131.90000000001237 | 60 |  | 49.68171296296296 | 4292.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
29 | 0 | 555 | 555 | 0 | 0 | 4 | 555 | 55 | 0 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.4 | 7760.00000000002 | 41.65 | 3393 | -1800 | 3805.5 | 5605.5 | 10.1 | 85.69260227909582 | 3817.9 | 0 | 47.59999999999991 | 60 |  | 64.87847222222223 | 5605.5 | 2015 | 6 | 2015_06_Asomata_english.xlsx
30 | 0 | 500 | 500 | 0 | 0 | 4 | 500 | 50 | 0 | 9.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.35 | 7639.999999999993 | 42 | 3802.5 | -120.00000000002728 | 4779.999999999973 | 4900 | 9.8 | 88.42011420861144 | 4533.3 | 0 | 246.69999999997253 | 0 |  | 56.71296296296296 | 4900 | 2015 | 6 | 2015_06_Asomata_english.xlsx
1 | 35 | 455 | 490 | 0 | 0 | 4 | 490 | 85 | 1.0500000000029104 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.55 | 8120 | 41.951 | 3745.17 | 480.0000000000073 | 5306.500000000007 | 4826.5 | 9.85 | 87.55778510799479 | 5153.8 | 0 | 152.7000000000071 | 0 |  | 55.86226851851852 | 4826.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
2 | 280 | 20 | 300 | 0 | 0 | 3 | 300 | 50 | 6.19999999999709 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.6 | 8239.999999999993 | 41.3315 | 3020.354999999996 | 119.99999999999272 | 3059.9999999999927 | 2940 | 9.8 | 87.90121682475808 | 2946.15 | 0 | 113.84999999999309 | 0 |  | 34.02777777777778 | 2940 | 2015 | 7 | 2015_07_Asomata_english.xlsx
3 | 335 | 0 | 335 | 0 | 0 | 4 | 335 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.6 | 8239.999999999993 | 40.85 | 2457 | 0 | 3249.5 | 3249.5 | 9.7 | 88.80741493635354 | 3022.2 | 0 | 227.3 | 0 |  | 37.609953703703695 | 3249.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
4 | 395 | 0 | 395 | 0 | 0 | 3 | 395 | 50 | 8.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.6 | 8239.999999999993 | 41.901 | 3686.67 | 0 | 3989.5 | 3989.5 | 10.1 | 85.29028959233953 | 3701.1 | 0 | 288.4 | 0 |  | 46.17476851851852 | 3989.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
5 | 330 | 0 | 330 | 0 | 0 | 3 | 330 | 50 | 6.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480.000000000015 | 41.247 | 2921.49 | 240.00000000002183 | 3573.000000000022 | 3333 | 10.1 | 85.09054652537853 | 3547.8 | 0 | 85.20000000002165 | 60 |  | 38.576388888888886 | 3333 | 2015 | 7 | 2015_07_Asomata_english.xlsx
6 | 335 | 125 | 460 | 0 | 0 | 3 | 460 | 100 | 7 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 84.95 | 9080.000000000015 | 41.71 | 3463.2 | 600 | 5039 | 4439 | 9.65 | 88.54011472552129 | 4719.75 | 0 | 319.25 | 0 |  | 51.37731481481482 | 4439 | 2015 | 7 | 2015_07_Asomata_english.xlsx
7 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 50 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 84.65 | 8360.00000000002 | 41.698 | 3449.16 | -719.9999999999945 | 4152.0000000000055 | 4872 | 10.15 | 84.77064432111526 | 4204.8 | 0 | 7.200000000006185 | 60 |  | 56.388888888888886 | 4872 | 2015 | 7 | 2015_07_Asomata_english.xlsx
8 | 55 | 445 | 500 | 0 | 0 | 4 | 500 | 110 | 1 | 8.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.8 | 8720 | 41.611 | 3347.3699999999935 | 359.99999999998 | 5184.99999999998 | 4825 | 9.65 | 88.85041886591449 | 4920.2 | 0 | 264.7999999999802 | 0 |  | 55.844907407407405 | 4825 | 2015 | 7 | 2015_07_Asomata_english.xlsx
9 | 160 | 370 | 530 | 0 | 0 | 4 | 530 | 85 | 4.200000000004366 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 84.5 | 8000.000000000007 | 41.689 | 3438.63 | -719.9999999999927 | 4553.500000000007 | 5273.5 | 9.95 | 86.77978125923738 | 4496.8 | 0 | 56.700000000008004 | 0 |  | 61.035879629629626 | 5273.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
10 | 425 | 15 | 440 | 0 | 0 | 4 | 440 | 55 | 8.599999999998545 | 0.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.65 | 8360.00000000002 | 41.119 | 2771.73 | 360.00000000001273 | 4628.000000000013 | 4268 | 9.7 | 88.70330307828041 | 4555.2 | 0 | 72.80000000001291 | 0 |  | 49.398148148148145 | 4268 | 2015 | 7 | 2015_07_Asomata_english.xlsx
11 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 50 | 7.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.9 | 8960.00000000002 | 40.229 | 1730.43 | 600 | 4200 | 3600 | 9.6 | 89.10499222999222 | 3978.85 | 0 | 221.15 | 0 |  | 41.666666666666664 | 3600 | 2015 | 7 | 2015_07_Asomata_english.xlsx
12 | 10 | 495 | 505 | 0 | 0 | 3 | 505 | 50 | 0.4000000000014552 | 11.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.1 | 7039.999999999993 | 40.409 | 1941.03 | -1920.0000000000273 | 3180.4999999999727 | 5100.5 | 10.1 | 86.3032383998495 | 3080.4 | 0 | 160.09999999997262 | 60 |  | 59.03356481481482 | 5100.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
13 | 535 | 50 | 585 | 0 | 0 | 4 | 585 | 50 | 10.599999999998545 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.6 | 5839.999999999993 | 40.9595 | 2585.115 | -1200 | 4620.75 | 5820.75 | 9.95 | 88.65722844994204 | 4632.4 | 0 | 48.349999999999454 | 60 |  | 67.36979166666667 | 5820.75 | 2015 | 7 | 2015_07_Asomata_english.xlsx
14 | 580 | 0 | 580 | 0 | 0 | 4 | 580 | 54 | 11.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 83.55 | 5720 | 41.29 | 2971.8 | -119.99999999999272 | 5535.000000000007 | 5655 | 9.75 | 90.58471412262027 | 5313 | 0 | 222.00000000000728 | 0 |  | 65.45138888888889 | 5655 | 2015 | 7 | 2015_07_Asomata_english.xlsx
15 | 535 | 0 | 535 | 0 | 0 | 4 | 535 | 54 | 10.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.55 | 5720 | 41.19 | 2854.8 | 0 | 5457 | 5457 | 10.2 | 86.58832967603408 | 5505.5 | 0 | 11.5 | 60 |  | 63.15972222222222 | 5457 | 2015 | 7 | 2015_07_Asomata_english.xlsx
16 | 550 | 0 | 550 | 0 | 0 | 3 | 550 | 50 | 11.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.5 | 8000.000000000007 | 40.848 | 2454.66 | 2280.0000000000073 | 7670.000000000007 | 5390 | 9.8 | 88.1080432172869 | 7550 | 0 | 120.00000000000728 | 0 |  | 62.38425925925926 | 5390 | 2015 | 7 | 2015_07_Asomata_english.xlsx
17 | 105 | 555 | 660 | 0 | 0 | 4 | 660 | 70 | 2.1999999999970896 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 17 | 84.2 | 7280.000000000014 | 41.45 | 3159 | -719.9999999999936 | 5814.000000000006 | 6534 | 9.9 | 87.83809660586911 | 5852 | 0 | 22.000000000006366 | 60 |  | 75.625 | 6534 | 2015 | 7 | 2015_07_Asomata_english.xlsx
18 | 210 | 395 | 605 | 0 | 0 | 4 | 605 | 70 | 4.80000000000291 | 8.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.35 | 7639.999999999993 | 41.582 | 3313.44 | 359.9999999999791 | 6651.999999999979 | 6292 | 10.4 | 83.31895377349925 | 6645.2 | 0 | 66.79999999997835 | 60 |  | 72.82407407407408 | 6292 | 2015 | 7 | 2015_07_Asomata_english.xlsx
19 | 365 | 250 | 615 | 0 | 0 | 3 | 615 | 85 | 8.19999999999709 | 5.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.05 | 9320 | 41.804 | 3573.1800000000067 | 1680.0000000000073 | 7719.3000000000075 | 6039.3 | 9.82 | 86.80523523303316 | 7649.8 | 0 | 69.50000000000819 | 0 |  | 69.89930555555556 | 6039.3 | 2015 | 7 | 2015_07_Asomata_english.xlsx
20 | 480 | 130 | 610 | 0 | 0 | 4 | 610 | 70 | 9.80000000000291 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 84.85 | 8839.999999999993 | 41.8 | 3568.5 | -480.0000000000073 | 5558.999999999993 | 6039 | 9.9 | 86.50566340181277 | 5431.2 | 0 | 127.79999999999382 | 0 |  | 69.89583333333333 | 6039 | 2015 | 7 | 2015_07_Asomata_english.xlsx
21 | 480 | 365 | 845 | 0 | 0 | 4 | 845 | 110 | 11.30000000000291 | 9.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 84.8 | 8720 | 42 | 3802.5 | -119.99999999999272 | 8414.500000000007 | 8534.5 | 10.1 | 84.89173683723513 | 8236.2 | 0 | 238.30000000000655 | 60 |  | 98.77893518518519 | 8534.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
22 | 565 | 85 | 650 | 0 | 0 | 3 | 650 | 70 | 11.89999999999418 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 84.4 | 7760.00000000002 | 41.732 | 3488.94 | -959.99999999998 | 5540.00000000002 | 6500 | 10 | 86.54952830188678 | 5372.85 | 0 | 167.15000000001965 | 0 |  | 75.23148148148148 | 6500 | 2015 | 7 | 2015_07_Asomata_english.xlsx
23 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 12.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.65 | 8360.00000000002 | 41.733 | 3490.1099999999915 | 600 | 7150.25 | 6550.25 | 9.85 | 87.35249135627615 | 7078.05 | 0 | 72.19999999999982 | 0 |  | 75.81307870370371 | 6550.25 | 2015 | 7 | 2015_07_Asomata_english.xlsx
24 | 115 | 775 | 890 | 0 | 0 | 3 | 890 | 110 | 2.099999999998545 | 15.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.6 | 8239.999999999993 | 41.842 | 3617.64 | -120.00000000002728 | 8557.499999999973 | 8677.5 | 9.75 | 88.35199229565427 | 8467.2 | 0 | 90.29999999997199 | 0 |  | 100.43402777777777 | 8677.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
25 | 0 | 665 | 665 | 0 | 0 | 5 | 665 | 50 | 0 | 13.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.45 | 7880.000000000014 | 41.659 | 3403.53 | -359.9999999999791 | 6356.500000000021 | 6716.5 | 10.1 | 85.5916687075068 | 6278.4 | 0 | 138.10000000002037 | 60 |  | 77.73726851851852 | 6716.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
26 | 0 | 540 | 540 | 0 | 0 | 4 | 540 | 50 | 0 | 10.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.05 | 6920 | 40.983 | 2612.6099999999915 | -960.0000000000136 | 4493.999999999986 | 5454 | 10.1 | 86.4058581839159 | 4477.5 | 0 | 76.49999999998636 | 60 |  | 63.125 | 5454 | 2015 | 7 | 2015_07_Asomata_english.xlsx
27 | 60 | 690 | 750 | 0 | 0 | 4 | 750 | 70 | 1.7000000000043656 | 14.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 83.7 | 6080.000000000014 | 42.102 | 3921.84 | -839.9999999999864 | 6847.500000000014 | 7687.5 | 10.25 | 85.8559981283266 | 6883.9 | 0 | 23.600000000014006 | 60 |  | 88.97569444444444 | 7687.5 | 2015 | 7 | 2015_07_Asomata_english.xlsx
28 | 330 | 400 | 730 | 0 | 0 | 4 | 730 | 55 | 6.69999999999709 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.4 | 7760.00000000002 | 41.851 | 3628.17 | 1680.0000000000064 | 9053.000000000007 | 7373 | 10.1 | 85.69260227909582 | 8971.2 | 0 | 141.80000000000655 | 60 |  | 85.33564814814815 | 7373 | 2015 | 7 | 2015_07_Asomata_english.xlsx
29 | 275 | 350 | 625 | 0 | 0 | 4 | 625 | 50 | 5.900000000001455 | 7.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.4 | 7760.00000000002 | 41.449 | 3157.83 | 0 | 6250 | 6250 | 10 | 86.54952830188678 | 6075.5 | 0 | 174.5 | 0 |  | 72.33796296296296 | 6250 | 2015 | 7 | 2015_07_Asomata_english.xlsx
30 | 505 | 185 | 690 | 0 | 0 | 4 | 690 | 100 | 11.5 | 3.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 30 | 84.25 | 7400.000000000007 | 41.982 | 3781.44 | -360.00000000001273 | 6539.999999999987 | 6900 | 10 | 86.85680473372781 | 6452.5 | 0 | 147.49999999998727 | 60 |  | 79.86111111111111 | 6900 | 2015 | 7 | 2015_07_Asomata_english.xlsx
31 | 0 | 625 | 625 | 0 | 0 | 4 | 625 | 50 | 0 | 13.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.4 | 7760.00000000002 | 41.001 | 2633.6699999999937 | 360.00000000001273 | 6610.000000000013 | 6250 | 10 | 86.54952830188678 | 6475.1 | 0 | 134.90000000001237 | 0 |  | 72.33796296296296 | 6250 | 2015 | 7 | 2015_07_Asomata_english.xlsx
1 | 0 | 625 | 625 | 0 | 0 | 4 | 625 | 55 | 0 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 1 | 84.2 | 7280.000000000014 | 41.34 | 3030.3 | -480.00000000000637 | 5832.499999999994 | 6312.5 | 10.1 | 86.09872835624795 | 5679.4 | 0 | 213.099999999994 | 60 |  | 73.0613425925926 | 6312.5 | 2015 | 8 | 2015_08_Asomata_english.xlsx
2 | 75 | 545 | 620 | 0 | 0 | 3 | 620 | 70 | 2.599999999998545 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 85.1 | 9439.999999999993 | 41.75 | 3510 | 2159.999999999979 | 8421.999999999978 | 6262 | 10.1 | 84.30084307734718 | 8300.1 | 0 | 181.8999999999778 | 60 |  | 72.47685185185185 | 6262 | 2015 | 8 | 2015_08_Asomata_english.xlsx
3 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 12.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.15 | 9560.00000000002 | 41.84 | 3615.3 | 120.00000000002728 | 6716.000000000026 | 6596 | 9.7 | 87.67545483867114 | 6696.85 | 0 | 19.15000000002692 | 0 |  | 76.34259259259258 | 6596 | 2015 | 8 | 2015_08_Asomata_english.xlsx
4 | 635 | 0 | 635 | 0 | 0 | 3 | 635 | 50 | 12.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.9 | 8960.00000000002 | 41.84 | 3615.3 | -600 | 5591.25 | 6191.25 | 9.75 | 87.73414619568464 | 5292.5 | 0 | 298.75 | 0 |  | 71.65798611111111 | 6191.25 | 2015 | 8 | 2015_08_Asomata_english.xlsx
5 | 655 | 0 | 655 | 0 | 0 | 4 | 655 | 50 | 13.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.5 | 8000.000000000007 | 42.03 | 3837.6 | -960.0000000000127 | 5524.499999999987 | 6484.5 | 9.9 | 87.21806298276887 | 5349.6 | 0 | 174.8999999999869 | 0 |  | 75.05208333333333 | 6484.5 | 2015 | 8 | 2015_08_Asomata_english.xlsx
6 | 525 | 0 | 525 | 0 | 0 | 4 | 525 | 50 | 10.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.7 | 8480.000000000015 | 41.427 | 3132.09 | 480.0000000000073 | 5677.500000000007 | 5197.5 | 9.9 | 86.80954746528516 | 5657.5 | 0 | 20.000000000007276 | 0 |  | 60.15625 | 5197.5 | 2015 | 8 | 2015_08_Asomata_english.xlsx
7 | 710 | 0 | 710 | 0 | 0 | 4 | 710 | 50 | 14.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.85 | 8839.999999999993 | 42 | 3802.5 | 359.9999999999782 | 7246.999999999977 | 6887 | 9.7 | 88.28928532762335 | 7244.6 | 0 | 2.399999999976899 | 0 |  | 79.71064814814814 | 6887 | 2015 | 8 | 2015_08_Asomata_english.xlsx
8 | 0 | 520 | 520 | 0 | 0 | 3 | 520 | 50 | 0 | 11.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.6 | 8239.999999999993 | 41.486 | 3201.1199999999935 | -600 | 6448.680851063829 | 5304 | 10.2 | 84.45411028261071 | 6446.8 | 1744.6808510638298 | 61.88085106383005 | 60 |  | 61.388888888888886 | 5304 | 2015 | 8 | 2015_08_Asomata_english.xlsx
9 | 570 | 30 | 600 | 0 | 0 | 4 | 600 | 50 | 12.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.8 | 8720 | 41.67 | 3416.4 | 480.0000000000073 | 6300.000000000007 | 5820 | 9.7 | 88.3924270160902 | 6230.8 | 0 | 69.2000000000071 | 0 |  | 67.36111111111111 | 5820 | 2015 | 8 | 2015_08_Asomata_english.xlsx
10 | 600 | 0 | 600 | 0 | 0 | 3 | 600 | 50 | 14.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 85 | 9200.000000000007 | 41.486 | 3201.1199999999935 | 480.0000000000073 | 6330.000000000007 | 5850 | 9.75 | 87.53011329755516 | 6351 | 0 | 9.000000000007276 | 30 |  | 67.70833333333333 | 5850 | 2015 | 8 | 2015_08_Asomata_english.xlsx
11 | 585 | 0 | 585 | 0 | 0 | 5 | 585 | 50 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 85 | 9200.000000000007 | 41.51 | 3229.2 | 0 | 5674.5 | 5674.5 | 9.7 | 87.9812994485735 | 5469.75 | 0 | 204.75 | 0 |  | 65.67708333333333 | 5674.5 | 2015 | 8 | 2015_08_Asomata_english.xlsx
12 | 0 | 505 | 505 | 0 | 0 | 4 | 505 | 55 | 0 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.7 | 8480.000000000015 | 41.448 | 3156.66 | -719.9999999999927 | 4203.750000000007 | 4923.75 | 9.75 | 88.1450789647511 | 4175.6 | 0 | 28.15000000000782 | 0 |  | 56.98784722222222 | 4923.75 | 2015 | 8 | 2015_08_Asomata_english.xlsx
13 | 555 | 55 | 610 | 0 | 0 | 4 | 610 | 50 | 12.200000000004366 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.25 | 7400.000000000007 | 41.7408 | 3499.235999999999 | -1080.0000000000073 | 4897.999999999993 | 5978 | 9.8 | 88.62939258543653 | 4752.3 | 0 | 205.69999999999254 | 60 |  | 69.18981481481481 | 5978 | 2015 | 8 | 2015_08_Asomata_english.xlsx
14 | 550 | 0 | 550 | 0 | 0 | 4 | 550 | 50 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.7 | 8480.000000000015 | 41.52 | 3240.9 | 1080.0000000000073 | 6415.000000000007 | 5335 | 9.7 | 88.599435041889 | 6322.5 | 0 | 92.50000000000728 | 0 |  | 61.74768518518518 | 5335 | 2015 | 8 | 2015_08_Asomata_english.xlsx
15 | 540 | 0 | 540 | 0 | 0 | 2 | 540 | 50 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.55 | 8120 | 41.48 | 3194.1 | -360.00000000001455 | 4904.999999999985 | 5265 | 9.75 | 88.45581367320499 | 4865 | 0 | 99.99999999998545 | 60 |  | 60.9375 | 5265 | 2015 | 8 | 2015_08_Asomata_english.xlsx
16 | 535 | 0 | 535 | 0 | 0 | 4 | 535 | 50 | 10.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.8 | 8720 | 41.681 | 3429.2699999999936 | 600 | 5950 | 5350 | 10 | 85.74065420560747 | 5942.2 | 0 | 67.80000000000018 | 60 |  | 61.9212962962963 | 5350 | 2015 | 8 | 2015_08_Asomata_english.xlsx
17 | 710 | 100 | 810 | 0 | 0 | 4 | 810 | 105 | 15.80000000000291 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.65 | 8360.00000000002 | 41.562 | 3290.04 | -359.99999999998 | 7497.000000000019 | 7857 | 9.7 | 88.70330307828041 | 7444.4 | 0 | 52.600000000018554 | 0 |  | 90.9375 | 7857 | 2015 | 8 | 2015_08_Asomata_english.xlsx
18 | 495 | 0 | 495 | 0 | 0 | 4 | 495 | 55 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.35 | 7639.999999999993 | 40.852 | 2459.34 | -720.0000000000273 | 4180.499999999973 | 4900.5 | 9.9 | 87.52698174185778 | 4022.3 | 0 | 158.199999999973 | 0 |  | 56.71875 | 4900.5 | 2015 | 8 | 2015_08_Asomata_english.xlsx
19 | 505 | 0 | 505 | 0 | 0 | 3 | 505 | 50 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.4 | 7760.00000000002 | 40.502 | 2049.84 | 120.00000000002728 | 5043.750000000027 | 4923.75 | 9.75 | 88.76874697629414 | 4956 | 0 | 87.75000000002728 | 0 |  | 56.98784722222222 | 4923.75 | 2015 | 8 | 2015_08_Asomata_english.xlsx
20 | 620 | 90 | 710 | 0 | 0 | 4 | 710 | 110 | 12.599999999998545 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 20 | 83.95 | 6680.000000000014 | 41.8315 | 3605.354999999996 | -1080.0000000000064 | 6126.499999999994 | 7206.5 | 10.15 | 86.18517235507906 | 6120 | 0 | 6.4999999999936335 | 0 |  | 83.40856481481481 | 7206.5 | 2015 | 8 | 2015_08_Asomata_english.xlsx
21 | 170 | 255 | 425 | 0 | 0 | 4 | 425 | 55 | 3.400000000001455 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.95 | 6680.000000000014 | 41.299 | 2982.33 | 0 | 4292.5 | 4292.5 | 10.1 | 86.61183162416361 | 4291.2 | 0 | 61.30000000000018 | 60 |  | 49.68171296296296 | 4292.5 | 2015 | 8 | 2015_08_Asomata_english.xlsx
22 | 505 | 0 | 505 | 0 | 0 | 3 | 505 | 50 | 11.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84 | 6800.000000000007 | 41.566 | 3294.72 | 119.99999999999363 | 5068.999999999994 | 4949 | 9.8 | 89.15694849368319 | 5033 | 0 | 35.99999999999363 | 0 |  | 57.280092592592595 | 4949 | 2015 | 8 | 2015_08_Asomata_english.xlsx
23 | 350 | 50 | 400 | 0 | 0 | 4 | 400 | 85 | 8.200000000004366 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.6 | 8239.999999999993 | 41.518 | 3238.56 | 1439.9999999999854 | 6852.3404255319 | 4040 | 10.1 | 85.29028959233953 | 6868.8 | 1372.340425531915 | 43.54042553190084 | 60 |  | 46.75925925925926 | 4040 | 2015 | 8 | 2015_08_Asomata_english.xlsx
24 | 465 | 40 | 505 | 0 | 0 | 4 | 505 | 109 | 9.900000000001455 | 1.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 24 | 84.85 | 8839.999999999993 | 41.78 | 3545.1 | 600 | 5574.25 | 4974.25 | 9.85 | 86.94477844446158 | 5394.7 | 0 | 179.55 | 0 |  | 57.57233796296296 | 4974.25 | 2015 | 8 | 2015_08_Asomata_english.xlsx
25 | 455 | 55 | 510 | 0 | 0 | 4 | 510 | 70 | 9.89999999999418 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.7 | 8480.000000000015 | 41.8499 | 3626.8829999999975 | -359.9999999999782 | 4740.000000000022 | 5100 | 10 | 85.94145199063232 | 4667.52 | 0 | 72.48000000002139 | 0 |  | 59.02777777777778 | 5100 | 2015 | 8 | 2015_08_Asomata_english.xlsx
26 | 485 | 0 | 485 | 0 | 0 | 3 | 485 | 50 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 85.05 | 9320 | 41.381 | 3078.27 | 839.9999999999854 | 5592.999999999985 | 4753 | 9.8 | 86.98238877432506 | 5482.5 | 0 | 110.49999999998545 | 0 |  | 55.011574074074076 | 4753 | 2015 | 8 | 2015_08_Asomata_english.xlsx
27 | 410 | 90 | 500 | 0 | 0 | 3 | 500 | 110 | 8.599999999998545 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 85.15 | 9560.00000000002 | 41.558 | 3285.36 | 240.00000000002 | 5140.000000000021 | 4900 | 9.8 | 86.78080734031732 | 4854.5 | 0 | 285.5000000000209 | 0 |  | 56.712962962962976 | 4900 | 2015 | 8 | 2015_08_Asomata_english.xlsx
28 | 45 | 540 | 585 | 0 | 0 | 3 | 585 | 110 | 0.8000000000029104 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.55 | 8120 | 41.621 | 3359.07 | -1440.00000000002 | 7446.786096256665 | 5967 | 10.2 | 84.55335130526947 | 7504.4 | 2919.7860962566847 | 42.38609625666504 | 100 |  | 69.0625 | 5967 | 2015 | 8 | 2015_08_Asomata_english.xlsx
29 | 440 | 0 | 440 | 0 | 0 | 3 | 440 | 50 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.05 | 9320 | 41.542 | 3266.64 | 1200 | 5644 | 4444 | 10.1 | 84.3987534641966 | 5438.5 | 0 | 205.5 | 0 |  | 51.43518518518518 | 4444 | 2015 | 8 | 2015_08_Asomata_english.xlsx
30 | 445 | 0 | 445 | 0 | 0 | 4 | 445 | 55 | 8.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 83.7 | 6080.000000000014 | 41.672 | 3418.74 | -3239.9999999999864 | 4523.829787234056 | 4450 | 10 | 88.00239808153478 | 4496.8 | 3313.8297872340427 | 27.02978723405613 | 0 |  | 51.504629629629626 | 4450 | 2015 | 8 | 2015_08_Asomata_english.xlsx
31 | 415 | 225 | 640 | 0 | 0 | 4 | 640 | 110 | 8.60000000000582 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 31 | 84.8 | 8720 | 41.88 | 3662.1 | 2639.9999999999864 | 8943.999999999985 | 6304 | 9.85 | 87.04634944731724 | 8537.1 | 0 | 406.8999999999851 | 0 |  | 72.96296296296296 | 6304 | 2015 | 8 | 2015_08_Asomata_english.xlsx
1 | 415 | 330 | 745 | 0 | 0 | 4 | 745 | 110 | 8.299999999995634 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 1 | 84.2 | 7280.000000000014 | 41.968 | 3765.06 | -1439.9999999999864 | 6084.500000000014 | 7524.5 | 10.1 | 86.09872835624795 | 6174 | 0 | 10.500000000013642 | 100 |  | 87.08912037037037 | 7524.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
2 | 145 | 660 | 805 | 0 | 0 | 4 | 805 | 110 | 3 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.4 | 7760.00000000002 | 41.599 | 3333.33 | 480.00000000000637 | 8570.250000000007 | 8090.25 | 10.05 | 86.11893363371819 | 8551.4 | 0 | 18.85000000000582 | 0 |  | 93.63715277777779 | 8090.25 | 2015 | 9 | 2015_09_Asomata_english.xlsx
3 | 335 | 515 | 850 | 0 | 0 | 0 | 850 | 110 | 7 | 10.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.75 | 8600.000000000007 | 41.651 | 3394.17 | 839.9999999999873 | 9254.999999999987 | 8415 | 9.9 | 86.70801583082284 | 9216.9 | 0 | 38.09999999998763 | 0 |  | 97.39583333333333 | 8415 | 2015 | 9 | 2015_09_Asomata_english.xlsx
4 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 50 | 0 | 9.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.2 | 7280.000000000014 | 41.699 | 3450.33 | -1319.9999999999936 | 3831.0000000000064 | 5151 | 10.1 | 86.09872835624795 | 3814.65 | 0 | 16.350000000006276 | 0 |  | 59.61805555555556 | 5151 | 2015 | 9 | 2015_09_Asomata_english.xlsx
5 | 425 | 125 | 550 | 0 | 0 | 5 | 550 | 110 | 8.150000000001455 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 83.9 | 6560.00000000002 | 41.848 | 3624.66 | -719.9999999999936 | 4835.000000000006 | 5555 | 10.1 | 86.71518703182966 | 4832.6 | 0 | 62.40000000000691 | 60 |  | 64.29398148148148 | 5555 | 2015 | 9 | 2015_09_Asomata_english.xlsx
6 | 0 | 375 | 375 | 0 | 0 | 4 | 375 | 55 | 0 | 7.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.55 | 8120 | 41.383 | 3080.61 | 1559.99999999998 | 5347.49999999998 | 3787.5 | 10.1 | 85.39051319938106 | 5032.8 | 0 | 314.6999999999798 | 0 |  | 43.83680555555556 | 3787.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
7 | 615 | 735 | 1350 | 0 | 0 | 4 | 1350 | 110 | 13.75 | 15.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.15 | 7160.00000000002 | 41.622 | 3360.24 | -959.99999999998 | 12540 | 13500 | 10 | 87.06287069988136 | 12519.5 | 0 | 20.500000000021828 | 0 |  | 156.25 | 13500 | 2015 | 9 | 2015_09_Asomata_english.xlsx
8 | 65 | 515 | 580 | 0 | 0 | 4 | 580 | 70 | 1.6999999999970896 | 11.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.6 | 8239.999999999993 | 41.891 | 3674.9699999999934 | 1079.9999999999727 | 6792.999999999973 | 5713 | 9.85 | 87.45501775458165 | 6621.1 | 0 | 171.89999999997235 | 0 |  | 66.12268518518519 | 5713 | 2015 | 9 | 2015_09_Asomata_english.xlsx
9 | 0 | 405 | 405 | 0 | 0 | 4 | 405 | 55 | 0 | 8.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.7 | 8480.000000000015 | 41.2 | 2866.5 | 240.00000000002183 | 4553.250000000022 | 4313.25 | 10.65 | 80.6961990522369 | 4622.4 | 0 | 130.8500000000222 | 200 |  | 49.921875 | 4313.25 | 2015 | 9 | 2015_09_Asomata_english.xlsx
10 | 490 | 0 | 490 | 0 | 0 | 5 | 490 | 45 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 41.848 | 3624.66 | -960.0000000000146 | 3768.4999999999854 | 4728.5 | 9.65 | 89.90066022366761 | 3522.4 | 0 | 246.09999999998536 | 0 |  | 54.72800925925926 | 4728.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
11 | 670 | 80 | 750 | 0 | 0 | 4 | 750 | 110 | 13.30000000000291 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.5 | 8000.000000000007 | 42.099 | 3918.33 | 480.0000000000073 | 7980.000000000007 | 7500 | 10 | 86.34588235294117 | 7867.2 | 0 | 112.80000000000655 | 0 |  | 86.80555555555556 | 7500 | 2015 | 9 | 2015_09_Asomata_english.xlsx
12 | 210 | 95 | 305 | 0 | 0 | 3 | 305 | 80 | 5.400000000001455 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.3 | 7520 | 41.165 | 2825.55 | -480.0000000000073 | 2600.4999999999927 | 3080.5 | 10.1 | 85.89518526320718 | 2460.1 | 0 | 140.39999999999281 | 0 |  | 35.65393518518518 | 3080.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
13 | 0 | 190 | 190 | 0 | 0 | 4 | 190 | 55 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 84.4 | 7760.00000000002 | 40.402 | 1932.84 | 240.00000000002 | 2235.00000000002 | 1995 | 10.5 | 82.42812219227312 | 2071.1 | 0 | 163.9000000000201 | 0 |  | 23.09027777777778 | 1995 | 2015 | 9 | 2015_09_Asomata_english.xlsx
14 | 225 | 45 | 270 | 0 | 0 | 3 | 270 | 110 | 5.400000000001455 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84 | 6800.000000000007 | 41.019 | 2654.73 | -960.0000000000127 | 3393.4468085106255 | 2646 | 9.8 | 89.15694849368319 | 3268.8 | 1707.4468085106382 | 124.6468085106253 | 0 |  | 30.625 | 2646 | 2015 | 9 | 2015_09_Asomata_english.xlsx
15 | 0 | 450 | 450 | 0 | 0 | 4 | 450 | 55 | 0 | 10.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.2 | 7280.000000000014 | 40.9315 | 2552.355 | 480.00000000000637 | 5025.000000000006 | 4545 | 10.1 | 86.09872835624795 | 5082 | 0 | 13.000000000006366 | 70 |  | 52.604166666666664 | 4545 | 2015 | 9 | 2015_09_Asomata_english.xlsx
16 | 485 | 75 | 560 | 0 | 0 | 4 | 560 | 110 | 10.799999999995634 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.35 | 7639.999999999993 | 41.372 | 3067.74 | 359.9999999999791 | 5959.999999999979 | 5600 | 10 | 86.65171192443921 | 5792.75 | 0 | 167.24999999997908 | 0 |  | 64.81481481481481 | 5600 | 2015 | 9 | 2015_09_Asomata_english.xlsx
17 | 385 | 130 | 515 | 0 | 0 | 3 | 515 | 110 | 8.599999999998545 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 85.1 | 9439.999999999993 | 41.65 | 3393 | 1800 | 6924.25 | 5124.25 | 9.95 | 85.57171005841273 | 6869.3 | 0 | 114.95000000000073 | 60 |  | 59.308449074074076 | 5124.25 | 2015 | 9 | 2015_09_Asomata_english.xlsx
18 | 395 | 0 | 395 | 0 | 0 | 4 | 395 | 55 | 7.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.55 | 8120 | 40.87 | 2480.4 | -1319.9999999999927 | 2827.5000000000073 | 4147.5 | 10.5 | 82.13754126797606 | 2847 | 0 | 40.500000000007276 | 60 |  | 48.00347222222222 | 4147.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
19 | 220 | 95 | 315 | 0 | 0 | 4 | 315 | 100 | 5.900000000001455 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.6 | 8239.999999999993 | 41.019 | 2654.73 | 119.99999999999272 | 3269.9999999999927 | 3150 | 10 | 86.14319248826293 | 3212 | 0 | 117.99999999999272 | 60 |  | 36.458333333333336 | 3150 | 2015 | 9 | 2015_09_Asomata_english.xlsx
20 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 40 | 6.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.55 | 8120 | 40.821 | 2423.07 | -119.99999999999272 | 2455.5000000000073 | 2575.5 | 10.1 | 85.39051319938106 | 2445.5 | 0 | 70.00000000000728 | 60 |  | 29.80902777777778 | 2575.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
21 | 470 | 70 | 540 | 0 | 0 | 3 | 540 | 70 | 9.80000000000291 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.6 | 8239.999999999993 | 41.45 | 3159 | 119.99999999999272 | 5573.999999999993 | 5454 | 10.1 | 85.29028959233953 | 5307.1 | 0 | 326.89999999999327 | 60 |  | 63.125 | 5454 | 2015 | 9 | 2015_09_Asomata_english.xlsx
22 | 590 | 205 | 795 | 0 | 0 | 3 | 795 | 110 | 11.30000000000291 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 83.9 | 6560.00000000002 | 40.86 | 2468.7 | -1679.9999999999727 | 6270.000000000027 | 7950 | 10 | 87.58233890214795 | 6153.9 | 0 | 116.10000000002674 | 0 |  | 92.01388888888889 | 7950 | 2015 | 9 | 2015_09_Asomata_english.xlsx
23 | 335 | 60 | 395 | 0 | 0 | 3 | 395 | 110 | 7.399999999994179 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.15 | 7160.00000000002 | 41.3 | 2983.5 | 600 | 4589.5 | 3989.5 | 10.1 | 86.20086207909047 | 4526 | 0 | 123.5 | 60 |  | 46.17476851851852 | 3989.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
24 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 40 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 24 | 84 | 6800.000000000007 | 40.57 | 2129.4 | -360.00000000001273 | 1876.4999999999873 | 2236.5 | 10.65 | 82.04113570310753 | 1657.6 | 0 | 218.89999999998713 | 0 |  | 25.885416666666668 | 2236.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
25 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 35 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84 | 6800.000000000007 | 40.078 | 1553.76 | 0 | 1683 | 1683 | 10.2 | 85.66059757236228 | 1540.3 | 0 | 142.7 | 0 |  | 19.479166666666664 | 1683 | 2015 | 9 | 2015_09_Asomata_english.xlsx
26 | 310 | 30 | 340 | 0 | 0 | 3 | 340 | 110 | 7 | 0.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84.05 | 6920 | 41.138 | 2793.96 | 119.99999999999272 | 3553.9999999999927 | 3434 | 10.1 | 86.4058581839159 | 3598.9 | 0 | 15.099999999993088 | 60 |  | 39.745370370370374 | 3434 | 2015 | 9 | 2015_09_Asomata_english.xlsx
27 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 54 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.55 | 8120 | 40.572 | 2131.74 | 1200 | 2797.5 | 1597.5 | 10.65 | 80.98067448955386 | 2628 | 0 | 169.5 | 0 |  | 18.489583333333332 | 1597.5 | 2015 | 9 | 2015_09_Asomata_english.xlsx
28 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 55 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.4 | 7760.00000000002 | 40.749 | 2338.83 | -359.99999999998 | 1660.00000000002 | 2020 | 10.1 | 85.69260227909582 | 1627.9 | 0 | 32.100000000020145 | 0 |  | 23.37962962962963 | 2020 | 2015 | 9 | 2015_09_Asomata_english.xlsx
29 | 430 | 75 | 505 | 0 | 0 | 4 | 505 | 90 | 9.950000000004366 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.4 | 7760.00000000002 | 41.702 | 3453.84 | 0 | 4923.75 | 4923.75 | 9.75 | 88.76874697629414 | 4935 | 0 | 48.75 | 60 |  | 56.98784722222222 | 4923.75 | 2015 | 9 | 2015_09_Asomata_english.xlsx
30 | 300 | 0 | 300 | 0 | 0 | 3 | 300 | 40 | 7.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.65 | 8360.00000000002 | 40.925 | 2544.75 | 600 | 3495 | 2895 | 9.65 | 89.16290568490362 | 3204.6 | 0 | 290.4 | 0 |  | 33.50694444444444 | 2895 | 2015 | 9 | 2015_09_Asomata_english.xlsx
1 | 165 | 0 | 165 | 0 | 0 | 3 | 165 | 55 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.3 | 7520 | 40.33 | 1848.6 | -840.00000000002 | 2138.811224489776 | 1575.75 | 9.55 | 90.84202839354896 | 1545 | 1403.061224489796 | 593.8112244897761 | 0 |  | 18.237847222222225 | 1575.75 | 2015 | 10 | 2015_10_Asomata_english.xlsx
2 | 265 | 75 | 340 | 0 | 0 | 3 | 340 | 70 | 7.099999999998545 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 2 | 84.65 | 8360.00000000002 | 41.212 | 2880.5400000000086 | 840.00000000002 | 5340.421052631599 | 3332 | 9.8 | 87.79816733258366 | 5400 | 1168.421052631579 | 40.421052631599196 | 100 |  | 38.56481481481482 | 3332 | 2015 | 10 | 2015_10_Asomata_english.xlsx
3 | 445 | 145 | 590 | 0 | 0 | 3 | 590 | 55 | 9.10000000000582 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.4 | 7760.00000000002 | 41.289 | 2970.6300000000065 | -600 | 5742.5 | 6342.5 | 10.75 | 80.51118911803421 | 5909.2 | 0 | 33.30000000000018 | 200 |  | 73.40856481481481 | 6342.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
4 | 295 | 0 | 295 | 0 | 0 | 5 | 295 | 55 | 6.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.5 | 8000.000000000007 | 41.521 | 3242.07 | 239.99999999998727 | 3219.4999999999873 | 2979.5 | 10.1 | 85.49097262667443 | 3233.9 | 0 | 45.599999999987176 | 60 |  | 34.4849537037037 | 2979.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
5 | 390 | 85 | 475 | 0 | 0 | 3 | 475 | 80 | 9.80000000000291 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 5 | 84.6 | 8239.999999999993 | 41.452 | 3161.34 | 239.99999999998545 | 4989.999999999985 | 4750 | 10 | 86.14319248826293 | 4905.6 | 0 | 84.39999999998508 | 0 |  | 54.976851851851855 | 4750 | 2015 | 10 | 2015_10_Asomata_english.xlsx
6 | 100 | 165 | 265 | 0 | 0 | 4 | 265 | 35 | 2.8000000000029104 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84.45 | 7880.000000000014 | 40.602 | 2166.84 | -359.9999999999791 | 2356.250000000021 | 2716.25 | 10.25 | 84.33910770203109 | 2234.4 | 0 | 121.85000000002083 | 0 |  | 31.438078703703702 | 2716.25 | 2015 | 10 | 2015_10_Asomata_english.xlsx
7 | 95 | 140 | 235 | 0 | 0 | 4 | 235 | 55 | 2.1499999999941792 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.4 | 7760.00000000002 | 41 | 2632.5 | -119.99999999999363 | 2183.0000000000064 | 2303 | 9.8 | 88.31584520600691 | 2160.8 | 0 | 82.20000000000618 | 60 |  | 26.65509259259259 | 2303 | 2015 | 10 | 2015_10_Asomata_english.xlsx
8 | 425 | 0 | 425 | 0 | 0 | 4 | 425 | 55 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.75 | 8600.000000000007 | 41.006 | 2639.52 | 839.9999999999873 | 5004.999999999987 | 4165 | 9.8 | 87.59279150256593 | 4825.3 | 0 | 179.699999999988 | 0 |  | 48.20601851851852 | 4165 | 2015 | 10 | 2015_10_Asomata_english.xlsx
9 | 370 | 80 | 450 | 0 | 0 | 4 | 450 | 108 | 9 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.15 | 7160.00000000002 | 41.4 | 3100.5 | -1439.9999999999873 | 3060.0000000000127 | 4500 | 10 | 87.06287069988136 | 2993 | 0 | 67.00000000001273 | 0 |  | 52.083333333333336 | 4500 | 2015 | 10 | 2015_10_Asomata_english.xlsx
10 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 50 | 0 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.3 | 7520 | 40.162 | 1652.04 | 359.99999999998 | 1731.99999999998 | 1372 | 9.8 | 88.52462971004005 | 1602.3 | 0 | 129.69999999998004 | 0 |  | 15.87962962962963 | 1372 | 2015 | 10 | 2015_10_Asomata_english.xlsx
11 | 265 | 0 | 265 | 0 | 0 | 4 | 265 | 55 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 83.8 | 6320 | 41.425 | 3129.75 | -1200 | 1542.75 | 2742.75 | 10.35 | 84.82305896493541 | 1391.6 | 0 | 151.15 | 0 |  | 31.744791666666668 | 2742.75 | 2015 | 10 | 2015_10_Asomata_english.xlsx
12 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 2.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.1 | 7039.999999999993 | 40.412 | 1944.54 | 719.9999999999927 | 1615.4999999999927 | 895.5 | 9.95 | 87.60429224507337 | 1391.2 | 0 | 224.29999999999268 | 0 |  | 10.364583333333332 | 895.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
13 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 40 | 4.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.95 | 6680.000000000014 | 41.093 | 2741.31 | -359.9999999999791 | 1740.000000000021 | 2100 | 10 | 87.47794994040524 | 1693.6 | 0 | 46.40000000002101 | 0 |  | 24.305555555555557 | 2100 | 2015 | 10 | 2015_10_Asomata_english.xlsx
14 | 0 | 215 | 215 | 0 | 0 | 2 | 215 | 45 | 0 | 5.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.6 | 5839.999999999993 | 41.214 | 2882.88 | -840.0000000000209 | 1309.999999999979 | 2150 | 10 | 88.21394230769232 | 1414 | 0 | 45.99999999997908 | 150 |  | 24.88425925925926 | 2150 | 2015 | 10 | 2015_10_Asomata_english.xlsx
15 | 605 | 580 | 1185 | 0 | 0 | 2 | 1185 | 110 | 11.200000000004366 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 15 | 84.5 | 8000.000000000007 | 41.682 | 3430.44 | 2160.0000000000146 | 14010 | 11850 | 10 | 86.34588235294117 | 14037.8 | 0 | 32.20000000001346 | 60 |  | 137.15277777777777 | 11850 | 2015 | 10 | 2015_10_Asomata_english.xlsx
16 | 90 | 280 | 370 | 0 | 0 | 4 | 370 | 110 | 2.25 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.35 | 7639.999999999993 | 41.698 | 3449.16 | -360.00000000001455 | 3265.9999999999854 | 3626 | 9.8 | 88.42011420861144 | 3013.5 | 0 | 252.49999999998545 | 0 |  | 41.967592592592595 | 3626 | 2015 | 10 | 2015_10_Asomata_english.xlsx
17 | 205 | 0 | 205 | 0 | 0 | 8 | 205 | 55 | 4.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.25 | 7400.000000000007 | 41.098 | 2747.16 | -239.99999999998545 | 1830.5000000000146 | 2070.5 | 10.1 | 85.99683637002754 | 1773.9 | 0 | 56.60000000001469 | 0 |  | 23.96412037037037 | 2070.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
18 | 0 | 145 | 145 | 0 | 0 | 4 | 145 | 55 | 0 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84 | 6800.000000000007 | 40.54 | 2094.3 | -600 | 864.5 | 1464.5 | 10.1 | 86.50872230080151 | 700.8 | 0 | 163.7 | 0 |  | 16.95023148148148 | 1464.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
19 | 95 | 365 | 460 | 0 | 0 | 1 | 460 | 109 | 2 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 83.9 | 6560.00000000002 | 41.389 | 3087.6300000000065 | -239.99999999998727 | 4406.000000000013 | 4646 | 10.1 | 86.71518703182966 | 4277.8 | 0 | 188.20000000001346 | 60 |  | 53.773148148148145 | 4646 | 2015 | 10 | 2015_10_Asomata_english.xlsx
20 | 250 | 0 | 250 | 0 | 0 | 1 | 250 | 35 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84 | 6800.000000000007 | 41.323 | 3010.41 | 239.99999999998727 | 2777.4999999999873 | 2537.5 | 10.15 | 86.08257095941825 | 2584.2 | 0 | 193.29999999998745 | 0 |  | 29.369212962962962 | 2537.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
21 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 35 | 3 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | ΣΥΝΤΗΡΗΣΗ ΓΡΑΜΜΗΣ ΜΕΤΑΦΟΡΑΣ 150KV | 21 | 84.2 | 7280.000000000014 | 40.867 | 2476.89 | 480.00000000000637 | 1596.5000000000064 | 1116.5 | 10.15 | 85.67459668946839 | 1275 | 0 | 321.50000000000637 | 0 |  | 12.922453703703704 | 1116.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
22 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 35 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.3 | 7520 | 40.701 | 2282.67 | 239.99999999998636 | 1304.9999999999864 | 1065 | 10.65 | 81.45928367684436 | 1050 | 0 | 314.99999999998636 | 60 |  | 12.32638888888889 | 1065 | 2015 | 10 | 2015_10_Asomata_english.xlsx
23 | 150 | 0 | 150 | 0 | 0 | 4 | 150 | 35 | 4.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.4 | 7760.00000000002 | 41.0075 | 2641.275 | 240.00000000002 | 1815.00000000002 | 1575 | 10.5 | 82.42812219227312 | 1460 | 0 | 355.00000000002 | 0 |  | 18.229166666666668 | 1575 | 2015 | 10 | 2015_10_Asomata_english.xlsx
24 | 265 | 0 | 265 | 0 | 0 | 3 | 265 | 40 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 24 | 84.25 | 7400.000000000007 | 41.798 | 3566.16 | -360.00000000001273 | 2342.9999999999873 | 2703 | 10.2 | 85.1537301311057 | 2271.8 | 0 | 71.19999999998709 | 0 |  | 31.28472222222222 | 2703 | 2015 | 10 | 2015_10_Asomata_english.xlsx
25 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.35 | 7639.999999999993 | 41.202 | 2868.84 | 239.99999999998545 | 2089.9999999999854 | 1850 | 10 | 86.65171192443921 | 1961 | 0 | 128.99999999998545 | 0 |  | 21.412037037037038 | 1850 | 2015 | 10 | 2015_10_Asomata_english.xlsx
26 | 230 | 0 | 230 | 0 | 0 | 4 | 230 | 35 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.05 | 6920 | 41.268 | 2946.06 | -719.9999999999927 | 1580.0000000000073 | 2300 | 10 | 87.26991676575506 | 1503.8 | 0 | 76.20000000000732 | 0 |  | 26.62037037037037 | 2300 | 2015 | 10 | 2015_10_Asomata_english.xlsx
27 | 0 | 115 | 115 | 0 | 0 | 4 | 115 | 35 | 0 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 83.95 | 6680.000000000014 | 39.883 | 1325.61 | -239.99999999998636 | 973.2500000000136 | 1213.25 | 10.55 | 82.91748809517084 | 800.8 | 0 | 232.45000000001357 | 60 |  | 14.04224537037037 | 1213.25 | 2015 | 10 | 2015_10_Asomata_english.xlsx
28 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 40 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 83.95 | 6680.000000000014 | 40.87 | 2480.4 | 0 | 1985.1 | 1985.1 | 10.18 | 85.93118854656703 | 1868.8 | 0 | 116.3 | 0 |  | 22.975694444444443 | 1985.1 | 2015 | 10 | 2015_10_Asomata_english.xlsx
29 | 495 | 0 | 495 | 0 | 0 | 2 | 495 | 55 | 9.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.1 | 7039.999999999993 | 41.648 | 3390.66 | 359.9999999999791 | 5359.499999999979 | 4999.5 | 10.1 | 86.3032383998495 | 5117.3 | 0 | 242.1999999999798 | 0 |  | 57.864583333333336 | 4999.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
30 | 165 | 430 | 595 | 0 | 0 | 4 | 595 | 110 | 3 | 8.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 83.85 | 6439.999999999993 | 40.861 | 2469.87 | -600 | 5409.5 | 6009.5 | 10.1 | 86.81878940582232 | 5431.2 | 0 | 38.30000000000018 | 60 |  | 69.55439814814815 | 6009.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
31 | 105 | 400 | 505 | 0 | 0 | 4 | 505 | 70 | 3 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 31 | 84.15 | 7160.00000000002 | 41.431 | 3136.7699999999936 | 720.0000000000273 | 5820.500000000027 | 5100.5 | 10.1 | 86.20086207909047 | 5489.6 | 0 | 330.90000000002783 | 0 |  | 59.03356481481482 | 5100.5 | 2015 | 10 | 2015_10_Asomata_english.xlsx
1 | 0 | 230 | 230 | 0 | 0 | 4 | 230 | 50 | 0 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 84.3 | 7520 | 40.395 | 1924.6500000000053 | 359.99999999998 | 2809.49999999998 | 2449.5 | 10.65 | 81.45928367684436 | 2592.6 | 0 | 216.89999999998008 | 0 |  | 28.350694444444443 | 2449.5 | 2015 | 11 | 2015_11_Asomata_english.xlsx
2 | 475 | 0 | 475 | 0 | 0 | 4 | 475 | 55 | 9.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.65 | 8360.00000000002 | 41.932 | 3722.94 | 840.00000000002 | 5518.75000000002 | 4678.75 | 9.85 | 87.35249135627615 | 5482.3 | 0 | 36.45000000001983 | 0 |  | 54.152199074074076 | 4678.75 | 2015 | 11 | 2015_11_Asomata_english.xlsx
3 | 520 | 65 | 585 | 0 | 0 | 4 | 585 | 110 | 11.30000000000291 | 1.3499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 3 | 84.3 | 7520 | 41.318 | 3004.56 | -840.00000000002 | 4980.74999999998 | 5820.75 | 9.95 | 87.1900875536073 | 4955.8 | 0 | 24.94999999997981 | 0 |  | 67.36979166666667 | 5820.75 | 2015 | 11 | 2015_11_Asomata_english.xlsx
4 | 315 | 0 | 315 | 0 | 0 | 3 | 315 | 50 | 7.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.1 | 7039.999999999993 | 41.2415 | 2915.0550000000067 | -480.0000000000073 | 2717.2499999999927 | 3197.25 | 10.15 | 85.87809929443152 | 2685.15 | 0 | 32.09999999999263 | 0 |  | 37.005208333333336 | 3197.25 | 2015 | 11 | 2015_11_Asomata_english.xlsx
5 | 275 | 0 | 275 | 0 | 0 | 3 | 275 | 55 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.1 | 7039.999999999993 | 41.208 | 2875.86 | 0 | 2777.5 | 2777.5 | 10.1 | 86.3032383998495 | 2671.8 | 0 | 165.7 | 60 |  | 32.14699074074074 | 2777.5 | 2015 | 11 | 2015_11_Asomata_english.xlsx
6 | 405 | 120 | 525 | 0 | 0 | 3 | 525 | 110 | 8.80000000000291 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 84 | 6800.000000000007 | 41.13 | 2784.6 | -239.99999999998545 | 5062.500000000015 | 5302.5 | 10.1 | 86.50872230080151 | 4968 | 0 | 94.50000000001455 | 0 |  | 61.37152777777778 | 5302.5 | 2015 | 11 | 2015_11_Asomata_english.xlsx
7 | 480 | 0 | 480 | 0 | 0 | 4 | 480 | 55 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.2 | 7280.000000000014 | 41.5 | 3217.5 | 480.00000000000637 | 5472.000000000006 | 4992 | 10.4 | 83.6151111921254 | 5572.2 | 0 | 4.800000000005639 | 105 |  | 57.77777777777778 | 4992 | 2015 | 11 | 2015_11_Asomata_english.xlsx
8 | 410 | 240 | 650 | 0 | 0 | 3 | 650 | 110 | 8.400000000001455 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 8 | 84.2 | 7280.000000000014 | 41.81 | 3580.2 | 0 | 6370 | 6370 | 9.8 | 88.73440371409225 | 6230.8 | 0 | 139.2 | 0 |  | 73.72685185185185 | 6370 | 2015 | 11 | 2015_11_Asomata_english.xlsx
9 | 0 | 270 | 270 | 0 | 0 | 4 | 270 | 55 | 0 | 6.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.2 | 7280.000000000014 | 40.1445 | 1631.565 | 0 | 2700 | 2700 | 10 | 86.95971563981043 | 2592 | 0 | 168 | 60 |  | 31.25 | 2700 | 2015 | 11 | 2015_11_Asomata_english.xlsx
10 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 55 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.35 | 7639.999999999993 | 41.42 | 3123.9 | 359.9999999999791 | 4909.999999999979 | 4550 | 10 | 86.65171192443921 | 4847.2 | 0 | 62.79999999997926 | 0 |  | 52.66203703703704 | 4550 | 2015 | 11 | 2015_11_Asomata_english.xlsx
11 | 325 | 0 | 325 | 0 | 0 | 4 | 325 | 50 | 7.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 83.95 | 6680.000000000014 | 41.6 | 3334.5 | -959.9999999999791 | 2290.000000000021 | 3250 | 10 | 87.47794994040524 | 2138.9 | 0 | 151.10000000002083 | 0 |  | 37.61574074074074 | 3250 | 2015 | 11 | 2015_11_Asomata_english.xlsx
12 | 265 | 0 | 265 | 0 | 0 | 4 | 265 | 50 | 6.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 83.8 | 6320 | 41.27 | 2948.4 | -360.00000000001364 | 2289.9999999999864 | 2650 | 10 | 87.79186602870813 | 2211.9 | 0 | 78.09999999998627 | 0 |  | 30.671296296296298 | 2650 | 2015 | 11 | 2015_11_Asomata_english.xlsx
13 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 50 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.9 | 6560.00000000002 | 41.55 | 3276 | 240.00000000002 | 3952.50000000002 | 3712.5 | 9.9 | 88.46700899206864 | 3744.4 | 0 | 208.10000000001946 | 0 |  | 42.96875 | 3712.5 | 2015 | 11 | 2015_11_Asomata_english.xlsx
14 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 50 | 0 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.3 | 7520 | 41.112 | 2763.54 | 959.99999999998 | 3009.99999999998 | 2050 | 10 | 86.75413711583924 | 2890.8 | 0 | 119.19999999998026 | 0 |  | 23.72685185185185 | 2050 | 2015 | 11 | 2015_11_Asomata_english.xlsx
15 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 50 | 0 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 83.8 | 6320 | 40.68 | 2258.1 | -1200 | 3276.595744680851 | 2450 | 10 | 87.79186602870813 | 3255.8 | 2026.595744680851 | 80.79574468085139 | 60 |  | 28.35648148148148 | 2450 | 2015 | 11 | 2015_11_Asomata_english.xlsx
16 | 450 | 115 | 565 | 0 | 0 | 4 | 565 | 70 | 9 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.3 | 7520 | 40.43 | 1965.6 | 1200 | 8071.393617021276 | 5706.5 | 10.1 | 85.89518526320718 | 8042.4 | 1164.8936170212767 | 88.9936170212768 | 60 |  | 66.04745370370371 | 5706.5 | 2015 | 11 | 2015_11_Asomata_english.xlsx
17 | 425 | 0 | 425 | 0 | 0 | 4 | 425 | 50 | 9.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.05 | 6920 | 40.079 | 1554.93 | -600 | 4747.4358974358975 | 4250 | 10 | 87.26991676575506 | 4620.3 | 1097.4358974358975 | 127.13589743589728 | 0 |  | 49.18981481481482 | 4250 | 2015 | 11 | 2015_11_Asomata_english.xlsx
18 | 380 | 120 | 500 | 0 | 0 | 4 | 500 | 110 | 7.400000000001455 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 84.1 | 7039.999999999993 | 40.603 | 2168.01 | 119.99999999999272 | 5069.999999999993 | 4950 | 9.9 | 88.04673816550302 | 5015.1 | 0 | 54.89999999999236 | 0 |  | 57.291666666666664 | 4950 | 2015 | 11 | 2015_11_Asomata_english.xlsx
19 | 395 | 200 | 595 | 0 | 0 | 2 | 595 | 110 | 7.400000000001455 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 83.75 | 6200.000000000007 | 40.483 | 2027.61 | -839.9999999999854 | 5169.500000000015 | 6009.5 | 10.1 | 87.02673860200392 | 5112.25 | 0 | 117.25000000001455 | 60 |  | 69.55439814814815 | 6009.5 | 2015 | 11 | 2015_11_Asomata_english.xlsx
20 | 160 | 85 | 245 | 0 | 0 | 4 | 245 | 70 | 4.599999999998545 | 2.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 84 | 6800.000000000007 | 40.581 | 2142.27 | 600 | 3050 | 2450 | 10 | 87.37380952380953 | 3002.35 | 0 | 47.65000000000009 | 0 |  | 28.35648148148148 | 2450 | 2015 | 11 | 2015_11_Asomata_english.xlsx
21 | 230 | 0 | 230 | 0 | 0 | 4 | 230 | 50 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.35 | 7639.999999999993 | 40.322 | 1839.24 | 839.9999999999854 | 3093.9999999999854 | 2254 | 9.8 | 88.42011420861144 | 2912.7 | 0 | 181.29999999998563 | 0 |  | 26.087962962962962 | 2254 | 2015 | 11 | 2015_11_Asomata_english.xlsx
22 | 325 | 0 | 325 | 0 | 0 | 4 | 325 | 50 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.35 | 7639.999999999993 | 40.34 | 1860.3000000000054 | 0 | 3185 | 3185 | 9.8 | 88.42011420861144 | 3095.2 | 0 | 89.80000000000064 | 0 |  | 36.86342592592593 | 3185 | 2015 | 11 | 2015_11_Asomata_english.xlsx
23 | 470 | 185 | 655 | 0 | 0 | 2 | 655 | 100 | 9.099999999998545 | 4.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 83.75 | 6200.000000000007 | 40.45 | 1989.0000000000055 | -1439.9999999999854 | 4979.000000000015 | 6419 | 9.8 | 89.69082243675912 | 4949 | 0 | 30.000000000014552 | 0 |  | 74.29398148148148 | 6419 | 2015 | 11 | 2015_11_Asomata_english.xlsx
24 | 0 | 365 | 365 | 0 | 0 | 3 | 365 | 55 | 0 | 8.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.2 | 7280.000000000014 | 40.752 | 2342.34 | 1080.0000000000064 | 4730.000000000006 | 3650 | 10 | 86.95971563981043 | 4584.4 | 0 | 145.60000000000673 | 0 |  | 42.245370370370374 | 3650 | 2015 | 11 | 2015_11_Asomata_english.xlsx
25 | 515 | 445 | 960 | 0 | 0 | 4 | 960 | 110 | 11.400000000001455 | 9.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 83.7 | 6080.000000000014 | 40.638 | 2208.96 | -1200 | 8736 | 9936 | 10.35 | 85.0264715763621 | 8811.1 | 0 | 24.899999999999636 | 100 |  | 115 | 9936 | 2015 | 11 | 2015_11_Asomata_english.xlsx
26 | 355 | 165 | 520 | 0 | 0 | 0 | 520 | 110 | 6.900000000001455 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 83.85 | 6439.999999999993 | 40.539 | 2093.13 | 359.9999999999791 | 7304.3076923076715 | 5252 | 10.1 | 86.81878940582232 | 7263.5 | 1692.3076923076922 | 40.80769230767146 | 0 |  | 60.78703703703704 | 5252 | 2015 | 11 | 2015_11_Asomata_english.xlsx
27 | 0 | 155 | 155 | 0 | 0 | 7 | 155 | 50 | 0 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.2 | 7280.000000000014 | 40.628 | 2197.26 | 840.0000000000209 | 2359.000000000021 | 1519 | 9.8 | 88.73440371409225 | 2080.5 | 0 | 278.5000000000209 | 0 |  | 17.58101851851852 | 1519 | 2015 | 11 | 2015_11_Asomata_english.xlsx
28 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 35 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.4 | 7760.00000000002 | 40.562 | 2120.04 | 480.00000000000637 | 2212.5000000000064 | 1732.5 | 9.9 | 87.4237659615018 | 2153.55 | 0 | 118.95000000000664 | 60 |  | 20.052083333333332 | 1732.5 | 2015 | 11 | 2015_11_Asomata_english.xlsx
29 | 395 | 120 | 515 | 0 | 0 | 3 | 515 | 110 | 7.599999999998545 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 83.6 | 5839.999999999993 | 40.37 | 1895.3999999999946 | -1920.0000000000273 | 3146.7499999999727 | 5066.75 | 9.838349514563106 | 89.66335479047032 | 3007.6 | 0 | 139.1499999999728 | 0 |  | 58.64293981481482 | 5066.75 | 2015 | 11 | 2015_11_Asomata_english.xlsx
30 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 55 | 4.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.2 | 7280.000000000014 | 40.5 | 2047.5 | 1440.000000000021 | 3460.000000000021 | 2020 | 10.1 | 86.09872835624795 | 3394.5 | 0 | 125.50000000002092 | 60 |  | 23.37962962962963 | 2020 | 2015 | 11 | 2015_11_Asomata_english.xlsx
1 | 430 | 0 | 430 | 0 | 0 | 4 | 430 | 55 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.15 | 7160.00000000002 | 40.69 | 2269.8 | -119.99999999999363 | 4094.0000000000064 | 4214 | 9.8 | 88.83966397947077 | 4052.8 | 0 | 41.200000000006185 | 0 |  | 48.773148148148145 | 4214 | 2015 | 12 | 2015_12_Asomata_english.xlsx
2 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 35 | 3.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.3 | 7520 | 40.27 | 1778.4000000000053 | 359.99999999998 | 1909.99999999998 | 1550 | 10 | 86.75413711583924 | 1861.5 | 0 | 78.49999999997999 | 30 |  | 17.939814814814813 | 1550 | 2015 | 12 | 2015_12_Asomata_english.xlsx
3 | 0 | 220 | 220 | 0 | 0 | 3 | 220 | 55 | 0 | 5.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 84.65 | 8360.00000000002 | 41.401 | 3101.67 | 840.00000000002 | 3051.00000000002 | 2211 | 10.05 | 85.61413331933531 | 2831.25 | 0 | 219.75000000002 | 0 |  | 25.59027777777778 | 2211 | 2015 | 12 | 2015_12_Asomata_english.xlsx
4 | 330 | 0 | 330 | 0 | 0 | 4 | 330 | 55 | 7.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.4 | 7760.00000000002 | 39.819 | 1250.73 | -600 | 2601 | 3201 | 9.7 | 89.22631783699669 | 2430.9 | 0 | 170.09999999999945 | 0 |  | 37.04861111111111 | 3201 | 2015 | 12 | 2015_12_Asomata_english.xlsx
5 | 440 | 180 | 620 | 0 | 0 | 4 | 620 | 110 | 8.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 83.75 | 6200.000000000007 | 41.239 | 2912.13 | -1560.0000000000127 | 4577.999999999987 | 6138 | 9.9 | 88.78485453335753 | 4537.55 | 0 | 40.449999999987085 | 0 |  | 71.04166666666667 | 6138 | 2015 | 12 | 2015_12_Asomata_english.xlsx
6 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.05 | 6920 | 40.711 | 2294.37 | 719.9999999999927 | 1518.7499999999927 | 798.75 | 10.65 | 81.94358381761039 | 1461.6 | 0 | 77.14999999999259 | 20 |  | 9.244791666666666 | 798.75 | 2015 | 12 | 2015_12_Asomata_english.xlsx
7 | 105 | 135 | 240 | 0 | 0 | 4 | 240 | 55 | 1.8999999999941792 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.1 | 7039.999999999993 | 41.426 | 3130.92 | 119.99999999999272 | 2471.9999999999927 | 2352 | 9.8 | 88.94517426923264 | 2454.8 | 0 | 17.199999999992542 | 0 |  | 27.22222222222222 | 2352 | 2015 | 12 | 2015_12_Asomata_english.xlsx
8 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.2 | 7280.000000000014 | 40.649 | 2221.83 | 240.00000000002092 | 975.0000000000209 | 735 | 9.8 | 88.73440371409225 | 934.4 | 0 | 40.60000000002094 | 0 |  | 8.506944444444445 | 735 | 2015 | 12 | 2015_12_Asomata_english.xlsx
9 | 230 | 0 | 230 | 0 | 0 | 4 | 230 | 35 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.05 | 6920 | 41.89 | 3673.8 | -360.00000000001364 | 2054.9999999999864 | 2415 | 10.5 | 83.11420644357625 | 1953.6 | 0 | 101.39999999998622 | 0 |  | 27.95138888888889 | 2415 | 2015 | 12 | 2015_12_Asomata_english.xlsx
10 | 420 | 0 | 420 | 0 | 0 | 4 | 420 | 55 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 10 | 83.8 | 6320 | 41.499 | 3216.3300000000063 | -600 | 3642 | 4242 | 10.1 | 86.9226396323843 | 3585.6 | 0 | 56.40000000000009 | 0 |  | 49.09722222222222 | 4242 | 2015 | 12 | 2015_12_Asomata_english.xlsx
11 | 275 | 0 | 275 | 0 | 0 | 3 | 275 | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 11 | 83.55 | 5720 | 41.65 | 3393 | -600 | 2177.5 | 2777.5 | 10.1 | 87.44563987084629 | 2124.3 | 0 | 113.2 | 60 |  | 32.14699074074074 | 2777.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
12 | 130 | 0 | 130 | 0 | 0 | 5 | 130 | 35 | 3.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 12 | 83.9 | 6560.00000000002 | 41.8345 | 3608.8649999999975 | 840.00000000002 | 2114.00000000002 | 1274 | 9.8 | 89.36973357362037 | 1990.6 | 0 | 123.40000000001987 | 0 |  | 14.74537037037037 | 1274 | 2015 | 12 | 2015_12_Asomata_english.xlsx
13 | 155 | 0 | 155 | 0 | 0 | 5 | 155 | 55 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 13 | 84.45 | 7880.000000000014 | 41.698 | 3449.16 | 1319.9999999999936 | 2831.2499999999936 | 1511.25 | 9.75 | 88.66419014828908 | 2744.8 | 0 | 86.4499999999939 | 0 |  | 17.491319444444443 | 1511.25 | 2015 | 12 | 2015_12_Asomata_english.xlsx
14 | 175 | 380 | 555 | 0 | 0 | 4 | 555 | 110 | 3.3000000000029104 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.3 | 7520 | 41.47 | 3182.4 | -360.00000000001364 | 5245.499999999986 | 5605.5 | 10.1 | 85.89518526320718 | 5217 | 0 | 88.49999999998636 | 60 |  | 64.87847222222223 | 5605.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
15 | 180 | 365 | 545 | 0 | 0 | 5 | 545 | 110 | 4.899999999994179 | 8.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84 | 6800.000000000007 | 41.5 | 3217.5 | -719.9999999999927 | 4730.000000000007 | 5450 | 10 | 87.37380952380953 | 4773 | 0 | 17.000000000007276 | 60 |  | 63.0787037037037 | 5450 | 2015 | 12 | 2015_12_Asomata_english.xlsx
16 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 55 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.15 | 7160.00000000002 | 40.428 | 1963.26 | 360.00000000001273 | 1152.0000000000127 | 792 | 9.9 | 87.9422936362438 | 984.2 | 0 | 227.8000000000127 | 60 |  | 9.166666666666666 | 792 | 2015 | 12 | 2015_12_Asomata_english.xlsx
17 | 470 | 235 | 705 | 0 | 0 | 4 | 705 | 110 | 10.200000000004366 | 4.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.05 | 6920 | 41.54 | 3264.3 | -240.00000000002 | 6739.49999999998 | 6979.5 | 9.9 | 88.15143107652027 | 6719.2 | 0 | 80.29999999998017 | 60 |  | 80.78125 | 6979.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
18 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 55 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.15 | 7160.00000000002 | 40.415 | 1948.05 | 240.00000000002 | 864.00000000002 | 624 | 9.6 | 90.69049031237643 | 775.2 | 0 | 148.80000000002008 | 60 |  | 7.222222222222222 | 624 | 2015 | 12 | 2015_12_Asomata_english.xlsx
19 | 115 | 285 | 400 | 0 | 0 | 5 | 400 | 100 | 3 | 6.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 83.95 | 6680.000000000014 | 41.77 | 3533.4 | -480.00000000000637 | 3479.9999999999936 | 3960 | 9.9 | 88.36156559636892 | 3394.5 | 0 | 145.49999999999363 | 60 |  | 45.833333333333336 | 3960 | 2015 | 12 | 2015_12_Asomata_english.xlsx
20 | 0 | 305 | 305 | 0 | 0 | 5 | 305 | 55 | 0 | 5.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.65 | 5960.00000000002 | 41.31 | 2995.2 | -719.9999999999936 | 2360.5000000000064 | 3080.5 | 10.1 | 87.23568635374941 | 2237.95 | 0 | 182.5500000000061 | 60 |  | 35.65393518518518 | 3080.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
21 | 115 | 360 | 475 | 0 | 0 | 4 | 475 | 110 | 2.5 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 83.7 | 6080.000000000014 | 41.6 | 3334.5 | 119.99999999999363 | 4774.999999999994 | 4655 | 9.8 | 89.79836538932118 | 4562.5 | 0 | 272.49999999999363 | 60 |  | 53.87731481481482 | 4655 | 2015 | 12 | 2015_12_Asomata_english.xlsx
22 | 0 | 170 | 170 | 0 | 0 | 4 | 170 | 36 | 0 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.95 | 6680.000000000014 | 41.329 | 3017.43 | 600 | 2317 | 1717 | 10.1 | 86.61183162416361 | 2360.6 | 0 | 16.399999999999636 | 60 |  | 19.872685185185187 | 1717 | 2015 | 12 | 2015_12_Asomata_english.xlsx
23 | 140 | 55 | 195 | 0 | 0 | 4 | 195 | 70 | 3 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.85 | 6439.999999999993 | 41.266 | 2943.7199999999934 | -240.00000000002092 | 1670.999999999979 | 1911 | 9.8 | 89.47650744885767 | 1496.5 | 0 | 234.49999999997908 | 60 |  | 22.118055555555557 | 1911 | 2015 | 12 | 2015_12_Asomata_english.xlsx
24 | 275 | 0 | 275 | 0 | 0 | 5 | 275 | 55 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 24 | 84.35 | 7639.999999999993 | 41.75 | 3510 | 1200 | 3977.5 | 2777.5 | 10.1 | 85.79377418261309 | 3890.9 | 0 | 146.6 | 60 |  | 32.14699074074074 | 2777.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
25 | 0 | 150 | 150 | 0 | 0 | 4 | 150 | 36 | 0 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 84.05 | 6920 | 41.348 | 3039.66 | -719.9999999999927 | 1107.8723404255393 | 1530 | 10.2 | 85.55874192721085 | 922.5 | 297.8723404255319 | 245.37234042553928 | 60 |  | 17.708333333333332 | 1530 | 2015 | 12 | 2015_12_Asomata_english.xlsx
26 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.1 | 7039.999999999993 | 40.292 | 1804.14 | 119.99999999999272 | 2427.936170212759 | 909 | 10.1 | 86.3032383998495 | 2430.9 | 1398.936170212766 | 57.03617021275886 | 60 |  | 10.520833333333334 | 909 | 2015 | 12 | 2015_12_Asomata_english.xlsx
27 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.15 | 7160.00000000002 | 39.2995 | 642.9150000000031 | 120.00000000002728 | 877.5000000000273 | 757.5 | 10.1 | 86.20086207909047 | 759.2 | 0 | 178.30000000002735 | 60 |  | 8.76736111111111 | 757.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
28 | 235 | 165 | 400 | 0 | 0 | 5 | 400 | 70 | 6.19999999999709 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84 | 6800.000000000007 | 41.402 | 3102.84 | -360.00000000001273 | 3719.9999999999873 | 4080 | 10.2 | 85.66059757236228 | 3502.5 | 0 | 277.49999999998727 | 60 |  | 47.22222222222222 | 4080 | 2015 | 12 | 2015_12_Asomata_english.xlsx
29 | 0 | 185 | 185 | 0 | 0 | 5 | 185 | 35 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.05 | 6920 | 41.031 | 2668.7699999999936 | 119.99999999999272 | 1988.4999999999927 | 1868.5 | 10.1 | 86.4058581839159 | 1949.1 | 0 | 99.39999999999281 | 60 |  | 21.62615740740741 | 1868.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
30 | 200 | 230 | 430 | 0 | 0 | 4 | 430 | 55 | 3.8000000000029104 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84 | 6800.000000000007 | 41.559 | 3286.53 | -119.99999999999272 | 4180.000000000007 | 4300 | 10 | 87.37380952380953 | 4212.25 | 0 | 27.750000000007276 | 60 |  | 49.76851851851852 | 4300 | 2015 | 12 | 2015_12_Asomata_english.xlsx
31 | 70 | 275 | 345 | 0 | 0 | 4 | 345 | 110 | 1.3000000000029104 | 6.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 31 | 83.6 | 5839.999999999993 | 41.3 | 2983.5 | -960.0000000000146 | 2524.4999999999854 | 3484.5 | 10.1 | 87.34053693830923 | 2423.6 | 0 | 160.89999999998554 | 60 |  | 40.329861111111114 | 3484.5 | 2015 | 12 | 2015_12_Asomata_english.xlsx
1 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.2 | 7280.000000000014 | 40.43 | 1965.6 | 1440.000000000021 | 2801.6326530612455 | 780 | 9.75 | 89.1894519382671 | 2597.4 | 581.6326530612245 | 204.2326530612454 | 0 |  | 9.027777777777779 | 780 | 2016 | 1 | 2016_01_Asomata_english.xlsx
2 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.5 | 8000.000000000007 | 40.51 | 2059.2 | 719.9999999999936 | 1646.2499999999936 | 926.25 | 9.75 | 88.55987933634992 | 1567.5 | 0 | 78.74999999999363 | 0 |  | 10.72048611111111 | 926.25 | 2016 | 1 | 2016_01_Asomata_english.xlsx
3 | 285 | 0 | 285 | 0 | 0 | 5 | 285 | 55 | 6.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.1 | 7039.999999999993 | 41.64 | 3381.3 | -960.0000000000146 | 1790.2499999999854 | 2750.25 | 9.65 | 90.32774174492019 | 1757 | 0 | 33.24999999998545 | 0 |  | 31.83159722222222 | 2750.25 | 2016 | 1 | 2016_01_Asomata_english.xlsx
4 | 405 | 0 | 405 | 0 | 0 | 5 | 405 | 55 | 7.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84 | 6800.000000000007 | 41.049 | 2689.83 | -239.99999999998545 | 3850.5000000000146 | 4090.5 | 10.1 | 86.50872230080151 | 3839.8 | 0 | 40.700000000014825 | 30 |  | 47.34375 | 4090.5 | 2016 | 1 | 2016_01_Asomata_english.xlsx
5 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5 | 84 | 6800.000000000007 | 40.835 | 2439.45 | 0 | 858.5 | 858.5 | 10.1 | 86.50872230080151 | 744.6 | 0 | 113.9 | 0 |  | 9.936342592592593 | 858.5 | 2016 | 1 | 2016_01_Asomata_english.xlsx
6 | 80 | 85 | 165 | 0 | 0 | 4 | 165 | 80 | 2.099999999998545 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 83.6 | 5839.999999999993 | 41.746 | 3505.32 | -960.0000000000146 | 813.7499999999854 | 1773.75 | 10.75 | 82.05948121645797 | 734.4 | 0 | 79.34999999998547 | 0 |  | 20.52951388888889 | 1773.75 | 2016 | 1 | 2016_01_Asomata_english.xlsx
7 | 100 | 0 | 100 | 0 | 0 | 5 | 100 | 35 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.1 | 7039.999999999993 | 41.34 | 3030.3 | 1200 | 2175 | 975 | 9.75 | 89.40130336804921 | 2007.5 | 0 | 167.5 | 0 |  | 11.284722222222221 | 975 | 2016 | 1 | 2016_01_Asomata_english.xlsx
8 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 55 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.2 | 7280.000000000014 | 41.57 | 3299.4 | 240.00000000002092 | 2287.500000000021 | 2047.5 | 10.5 | 82.81877679981945 | 2022.1 | 0 | 265.400000000021 | 0 |  | 23.697916666666668 | 2047.5 | 2016 | 1 | 2016_01_Asomata_english.xlsx
9 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 36 | 4.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.055 | 6932.000000000024 | 41.481 | 3195.27 | -347.99999999999 | 1465.0000000000102 | 1813 | 9.8 | 89.04034803791922 | 1316 | 0 | 149.00000000001023 | 0 |  | 20.983796296296298 | 1813 | 2016 | 1 | 2016_01_Asomata_english.xlsx
10 | 200 | 0 | 200 | 0 | 0 | 5 | 200 | 55 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.2 | 7280.000000000014 | 41.5 | 3217.5 | 347.99999999999 | 2367.99999999999 | 2020 | 10.1 | 86.09872835624795 | 2146.2 | 0 | 221.79999999999018 | 0 |  | 23.37962962962963 | 2020 | 2016 | 1 | 2016_01_Asomata_english.xlsx
11 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.9 | 6560.00000000002 | 40.85 | 2457 | -719.9999999999936 | 1761.4583333333396 | 757.5 | 10.1 | 86.71518703182966 | 1620.6 | 1723.9583333333333 | 140.85833333333971 | 0 |  | 8.76736111111111 | 757.5 | 2016 | 1 | 2016_01_Asomata_english.xlsx
12 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 35 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 83.55 | 5720 | 41.55 | 3276 | -840.00000000002 | 1230.49999999998 | 2070.5 | 10.1 | 87.44563987084629 | 1189.9 | 0 | 40.59999999998013 | 0 |  | 23.96412037037037 | 2070.5 | 2016 | 1 | 2016_01_Asomata_english.xlsx
13 | 135 | 0 | 135 | 0 | 0 | 4 | 135 | 35 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.15 | 7160.00000000002 | 41.112 | 2763.54 | 1440.00000000002 | 2756.25000000002 | 1316.25 | 9.75 | 89.29525199987833 | 2584.2 | 0 | 172.0500000000202 | 0 |  | 15.234375 | 1316.25 | 2016 | 1 | 2016_01_Asomata_english.xlsx
14 | 95 | 0 | 95 | 0 | 0 | 5 | 95 | 35 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.5 | 8000.000000000007 | 40.71 | 2293.2 | 839.9999999999873 | 1789.9999999999873 | 950 | 10 | 86.34588235294117 | 1708.2 | 0 | 81.79999999998722 | 0 |  | 10.99537037037037 | 950 | 2016 | 1 | 2016_01_Asomata_english.xlsx
15 | 230 | 0 | 230 | 0 | 0 | 4 | 230 | 36 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.9 | 6560.00000000002 | 41.535 | 3258.45 | -1439.9999999999873 | 860.0000000000127 | 2300 | 10 | 87.58233890214795 | 790.4 | 0 | 69.60000000001276 | 0 |  | 26.62037037037037 | 2300 | 2016 | 1 | 2016_01_Asomata_english.xlsx
16 | 70 | 0 | 70 | 0 | 0 | 5 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 84.55 | 8120 | 40.54 | 2094.3 | 1559.99999999998 | 2273.99999999998 | 714 | 10.2 | 84.55335130526947 | 2190 | 0 | 83.99999999997999 | 0 |  | 8.26388888888889 | 714 | 2016 | 1 | 2016_01_Asomata_english.xlsx
17 | 155 | 0 | 155 | 0 | 0 | 5 | 155 | 35 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.5 | 8000.000000000007 | 41.47 | 3182.4 | -119.99999999999272 | 2440.291666666674 | 1565.5 | 10.1 | 85.49097262667443 | 2321.4 | 994.7916666666666 | 118.8916666666737 | 0 |  | 18.119212962962962 | 1565.5 | 2016 | 1 | 2016_01_Asomata_english.xlsx
18 | 340 | 115 | 455 | 0 | 0 | 3 | 455 | 110 | 6.94999999999709 | 2.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 83.5 | 5600.000000000007 | 41.652 | 3395.34 | -2400 | 2195.5 | 4595.5 | 10.1 | 87.55099606346177 | 2168.1 | 0 | 87.40000000000009 | 60 |  | 53.188657407407405 | 4595.5 | 2016 | 1 | 2016_01_Asomata_english.xlsx
19 | 215 | 130 | 345 | 0 | 0 | 5 | 345 | 110 | 4.150000000001455 | 2.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 84 | 6800.000000000007 | 41.3 | 2983.5 | 1200 | 4581 | 3381 | 9.8 | 89.15694849368319 | 4565.8 | 0 | 15.199999999999818 | 0 |  | 39.13194444444444 | 3381 | 2016 | 1 | 2016_01_Asomata_english.xlsx
20 | 580 | 0 | 580 | 0 | 0 | 4 | 580 | 55 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2 | 0 | 1 | 0 | ΒΛΑΒΗ ΒΑΛΒΙΔΑΣ SA & ΡΥΘΜΙΣΤΗ ΣΤΟΦΩΝ | 20 | 83.95 | 6680.000000000014 | 40.65 | 2223 | -119.99999999999363 | 5622.000000000006 | 5742 | 9.9 | 88.36156559636892 | 5577.2 | 0 | 44.80000000000655 | 0 |  | 66.45833333333333 | 5742 | 2016 | 1 | 2016_01_Asomata_english.xlsx
21 | 225 | 0 | 225 | 0 | 0 | 4 | 225 | 40 | 5.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 1 | 0 | ΒΛΑΒΗ ΒΑΛΒΙΔΑΣ SA & ΡΥΘΜΙΣΤΗ ΣΤΟΦΩΝ | 21 | 84.1 | 7039.999999999993 | 41.499 | 3216.3300000000063 | 359.9999999999791 | 2531.249999999979 | 2171.25 | 9.65 | 90.32774174492019 | 2484.3 | 0 | 46.949999999979354 | 0 |  | 25.130208333333332 | 2171.25 | 2016 | 1 | 2016_01_Asomata_english.xlsx
22 | 210 | 0 | 210 | 0 | 0 | 5 | 210 | 40 | 5.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.1 | 7039.999999999993 | 41.755 | 3515.85 | 0 | 2016 | 2016 | 9.6 | 90.798198733175 | 1882.5 | 0 | 133.5 | 0 |  | 23.333333333333332 | 2016 | 2016 | 1 | 2016_01_Asomata_english.xlsx
23 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 55 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.25 | 7400.000000000007 | 41.202 | 2868.84 | 360.00000000001455 | 1752.0000000000146 | 1392 | 9.6 | 90.47583826429981 | 1531.8 | 0 | 220.20000000001437 | 0 |  | 16.11111111111111 | 1392 | 2016 | 1 | 2016_01_Asomata_english.xlsx
24 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 55 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 24 | 84.4 | 7760.00000000002 | 41.79 | 3556.8 | 360.00000000001273 | 2481.0000000000127 | 2121 | 10.1 | 85.69260227909582 | 2394.4 | 0 | 86.60000000001264 | 0 |  | 24.54861111111111 | 2121 | 2016 | 1 | 2016_01_Asomata_english.xlsx
25 | 310 | 160 | 470 | 0 | 0 | 4 | 470 | 110 | 7 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 83.8 | 6320 | 41.6815 | 3429.854999999996 | -1440.00000000002 | 3306.99999999998 | 4747 | 10.1 | 86.9226396323843 | 3337.4 | 0 | 29.599999999980355 | 60 |  | 54.942129629629626 | 4747 | 2016 | 1 | 2016_01_Asomata_english.xlsx
26 | 160 | 0 | 160 | 0 | 0 | 4 | 160 | 55 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.2 | 7280.000000000014 | 41.52 | 3240.9 | 960.0000000000136 | 2496.0000000000136 | 1536 | 9.6 | 90.58303712480253 | 2355 | 0 | 141.00000000001364 | 0 |  | 17.77777777777778 | 1536 | 2016 | 1 | 2016_01_Asomata_english.xlsx
27 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 55 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.1 | 7039.999999999993 | 41.8 | 3568.5 | -240.00000000002092 | 1856.249999999979 | 2096.25 | 9.75 | 89.40130336804921 | 1803.1 | 0 | 53.14999999997917 | 0 |  | 24.26215277777778 | 2096.25 | 2016 | 1 | 2016_01_Asomata_english.xlsx
28 | 175 | 40 | 215 | 0 | 0 | 4 | 215 | 70 | 4.80000000000291 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 83.9 | 6560.00000000002 | 41.9 | 3685.5 | -479.9999999999727 | 1616.2500000000273 | 2096.25 | 9.75 | 89.82803989963894 | 1533 | 0 | 83.25000000002728 | 0 |  | 24.26215277777778 | 2096.25 | 2016 | 1 | 2016_01_Asomata_english.xlsx
29 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 36 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.35 | 7639.999999999993 | 41.5 | 3217.5 | 1079.9999999999727 | 2329.9999999999727 | 1250 | 10 | 86.65171192443921 | 2227.5 | 0 | 102.49999999997272 | 0 |  | 14.467592592592593 | 1250 | 2016 | 1 | 2016_01_Asomata_english.xlsx
30 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 1.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.75 | 8600.000000000007 | 40.85 | 2457 | 960.0000000000146 | 1691.2500000000146 | 731.25 | 9.75 | 88.0419853051432 | 1492.5 | 0 | 198.75000000001455 | 0 |  | 8.463541666666666 | 731.25 | 2016 | 1 | 2016_01_Asomata_english.xlsx
31 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 40 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.1 | 7039.999999999993 | 40.869 | 2479.23 | -1560.0000000000146 | 1102.765957446794 | 700 | 10 | 87.16627078384799 | 1043.9 | 1962.7659574468084 | 58.86595744679403 | 0 |  | 8.101851851851851 | 700 | 2016 | 1 | 2016_01_Asomata_english.xlsx
1 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 35 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84 | 6800.000000000007 | 41.53 | 3252.6 | -239.99999999998545 | 1160.0000000000146 | 1400 | 10 | 87.37380952380953 | 1000.1 | 0 | 159.90000000001453 | 0 |  | 16.203703703703702 | 1400 | 2016 | 2 | 2016_02_Asomata_english.xlsx
2 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 35 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.35 | 7639.999999999993 | 41.25 | 2925 | 839.9999999999854 | 2246.4999999999854 | 1406.5 | 9.7 | 89.3316617777724 | 2168.2 | 0 | 78.29999999998518 | 0 |  | 16.278935185185187 | 1406.5 | 2016 | 2 | 2016_02_Asomata_english.xlsx
3 | 110 | 0 | 110 | 0 | 0 | 3 | 110 | 35 | 2.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84 | 6800.000000000007 | 41.35 | 3042 | -839.9999999999854 | 1202.1052631579091 | 1100 | 10 | 87.37380952380953 | 1196.25 | 942.1052631578947 | 5.855263157909121 | 0 |  | 12.731481481481481 | 1100 | 2016 | 2 | 2016_02_Asomata_english.xlsx
4 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.3 | 7520 | 40.83 | 2433.6 | 719.9999999999927 | 1426.9999999999927 | 707 | 10.1 | 85.89518526320718 | 1197.2 | 0 | 229.79999999999268 | 0 |  | 8.18287037037037 | 707 | 2016 | 2 | 2016_02_Asomata_english.xlsx
5 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 55 | 4.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.3 | 7520 | 41.299 | 2982.33 | 0 | 2211.744680851064 | 1616 | 10.1 | 85.89518526320718 | 2153.5 | 595.7446808510638 | 58.244680851064004 | 0 |  | 18.703703703703702 | 1616 | 2016 | 2 | 2016_02_Asomata_english.xlsx
6 | 60 | 170 | 230 | 0 | 0 | 4 | 230 | 109 | 1.1999999999970896 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 83.85 | 6439.999999999993 | 41.728 | 3484.26 | -1080.0000000000073 | 1242.9999999999927 | 2323 | 10.1 | 86.81878940582232 | 1239 | 0 | 23.999999999992724 | 20 |  | 26.886574074074073 | 2323 | 2016 | 2 | 2016_02_Asomata_english.xlsx
7 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 55 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.1 | 7039.999999999993 | 41.284 | 2964.78 | 600 | 2050 | 1450 | 10 | 87.16627078384799 | 1868.8 | 0 | 181.2 | 0 |  | 16.78240740740741 | 1450 | 2016 | 2 | 2016_02_Asomata_english.xlsx
8 | 190 | 0 | 190 | 0 | 0 | 4 | 190 | 50 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.35 | 7639.999999999993 | 41.64 | 3381.3 | 600 | 2500 | 1900 | 10 | 86.65171192443921 | 2438.2 | 0 | 91.80000000000018 | 30 |  | 21.99074074074074 | 1900 | 2016 | 2 | 2016_02_Asomata_english.xlsx
9 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.3 | 7520 | 41.05 | 2691 | -119.99999999999272 | 839.5000000000073 | 959.5 | 10.1 | 85.89518526320718 | 854.1 | 0 | 45.40000000000725 | 60 |  | 11.105324074074074 | 959.5 | 2016 | 2 | 2016_02_Asomata_english.xlsx
10 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 54 | 0 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.05 | 6920 | 41.04 | 2679.3 | -600 | 1050 | 1650 | 10 | 87.26991676575506 | 1036.75 | 0 | 73.25 | 60 |  | 19.09722222222222 | 1650 | 2016 | 2 | 2016_02_Asomata_english.xlsx
11 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 35 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.25 | 7400.000000000007 | 40.44 | 1977.3 | 480.0000000000073 | 1641.5000000000073 | 1161.5 | 10.1 | 85.99683637002754 | 1401.6 | 0 | 239.90000000000737 | 0 |  | 13.443287037037036 | 1161.5 | 2016 | 2 | 2016_02_Asomata_english.xlsx
12 | 150 | 0 | 150 | 0 | 0 | 4 | 150 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84 | 6800.000000000007 | 40.279 | 1788.9300000000062 | -600 | 885 | 1485 | 9.9 | 88.25637325637325 | 813.2 | 0 | 71.80000000000007 | 0 |  | 17.1875 | 1485 | 2016 | 2 | 2016_02_Asomata_english.xlsx
13 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 35 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.25 | 7400.000000000007 | 41.12 | 2772.9 | 600 | 1761.5 | 1161.5 | 10.1 | 85.99683637002754 | 1759.3 | 0 | 32.2 | 30 |  | 13.443287037037036 | 1161.5 | 2016 | 2 | 2016_02_Asomata_english.xlsx
14 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 83.8 | 6320 | 40.7 | 2281.5 | -1080.0000000000073 | 1801.7797927461068 | 959.5 | 10.1 | 86.9226396323843 | 1657.1 | 1922.279792746114 | 144.67979274610684 | 0 |  | 11.105324074074074 | 959.5 | 2016 | 2 | 2016_02_Asomata_english.xlsx
15 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 83.8 | 6320 | 40.6 | 2164.5 | 0 | 3441.06914893617 | 685.75 | 10.55 | 83.21503888977074 | 3423.7 | 2755.31914893617 | 77.3691489361704 | 60 |  | 7.936921296296297 | 685.75 | 2016 | 2 | 2016_02_Asomata_english.xlsx
16 | 135 | 0 | 135 | 0 | 0 | 3 | 135 | 55 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 83.5 | 5600.000000000007 | 41.117 | 2769.39 | -719.9999999999927 | 2542.4922680412446 | 1437.75 | 10.65 | 83.02958312121726 | 2569.6 | 1824.7422680412371 | 32.89226804124473 | 60 |  | 16.640625 | 1437.75 | 2016 | 2 | 2016_02_Asomata_english.xlsx
17 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 35 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.85 | 6439.999999999993 | 40.89 | 2503.8 | 839.9999999999854 | 2033.9999999999854 | 1194 | 9.95 | 88.12761537676437 | 1876.1 | 0 | 157.89999999998554 | 0 |  | 13.819444444444445 | 1194 | 2016 | 2 | 2016_02_Asomata_english.xlsx
18 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 55 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.15 | 7160.00000000002 | 40.81 | 2410.2 | 720.0000000000273 | 2134.0000000000273 | 1414 | 10.1 | 86.20086207909047 | 2077.5 | 0 | 56.500000000027285 | 0 |  | 16.36574074074074 | 1414 | 2016 | 2 | 2016_02_Asomata_english.xlsx
19 | 170 | 0 | 170 | 0 | 0 | 4 | 170 | 50 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 83.95 | 6680.000000000014 | 40.808 | 2407.86 | -480.00000000000637 | 1236.9999999999936 | 1717 | 10.1 | 86.61183162416361 | 1123.2 | 0 | 113.79999999999359 | 0 |  | 19.872685185185187 | 1717 | 2016 | 2 | 2016_02_Asomata_english.xlsx
20 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 55 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.55 | 8120 | 40.532 | 2084.94 | 1439.9999999999864 | 2550.9999999999864 | 1111 | 10.1 | 85.39051319938106 | 2547.7 | 0 | 63.29999999998654 | 60 |  | 12.858796296296296 | 1111 | 2016 | 2 | 2016_02_Asomata_english.xlsx
21 | 55 | 0 | 55 | 0 | 0 | 3 | 55 | 36 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.3 | 7520 | 40.95 | 2574 | -600 | 2386.2692307692305 | 555.5 | 10.1 | 85.89518526320718 | 2343.3 | 2430.7692307692305 | 42.96923076923076 | 0 |  | 6.429398148148148 | 555.5 | 2016 | 2 | 2016_02_Asomata_english.xlsx
22 | 65 | 35 | 100 | 0 | 0 | 4 | 100 | 70 | 1.8000000000029104 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.25 | 7400.000000000007 | 41.15 | 2808 | -119.99999999999272 | 880.0000000000073 | 1000 | 10 | 86.85680473372781 | 803 | 0 | 77.00000000000728 | 0 |  | 11.574074074074074 | 1000 | 2016 | 2 | 2016_02_Asomata_english.xlsx
23 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.3 | 7520 | 40.7 | 2281.5 | 119.99999999999272 | 927.9999999999927 | 808 | 10.1 | 85.89518526320718 | 978.2 | 0 | 9.799999999992792 | 60 |  | 9.351851851851851 | 808 | 2016 | 2 | 2016_02_Asomata_english.xlsx
24 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 35 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.5 | 8000.000000000007 | 41 | 2632.5 | 480.0000000000073 | 1519.5000000000073 | 1039.5 | 9.9 | 87.21806298276887 | 1330.35 | 0 | 189.15000000000737 | 0 |  | 12.03125 | 1039.5 | 2016 | 2 | 2016_02_Asomata_english.xlsx
25 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.8 | 8720 | 40.6508 | 2223.935999999994 | 719.9999999999927 | 1511.9999999999927 | 792 | 9.9 | 86.60672141980554 | 1394.3 | 0 | 117.69999999999277 | 0 |  | 9.166666666666666 | 792 | 2016 | 2 | 2016_02_Asomata_english.xlsx
26 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 35 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.8 | 8720 | 40.707 | 2289.69 | 0 | 1399.25 | 1399.25 | 9.65 | 88.85041886591449 | 1275.95 | 0 | 123.3 | 0 |  | 16.19502314814815 | 1399.25 | 2016 | 2 | 2016_02_Asomata_english.xlsx
27 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 55 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.5 | 8000.000000000007 | 41.2 | 2866.5 | -719.9999999999927 | 1152.0000000000073 | 1872 | 9.6 | 89.94362745098039 | 1041.9 | 0 | 110.10000000000741 | 0 |  | 21.666666666666668 | 1872 | 2016 | 2 | 2016_02_Asomata_english.xlsx
28 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 83.75 | 6200.000000000007 | 40.89 | 2503.8 | -1800 | 1236.7872340425533 | 707 | 10.1 | 87.02673860200392 | 1109.6 | 2329.7872340425533 | 187.18723404255343 | 60 |  | 8.18287037037037 | 707 | 2016 | 2 | 2016_02_Asomata_english.xlsx
29 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 83.9 | 6560.00000000002 | 40.521 | 2072.07 | 360.00000000001273 | 1010.0000000000127 | 650 | 10 | 87.58233890214795 | 934.4 | 0 | 75.60000000001276 | 0 |  | 7.523148148148148 | 650 | 2016 | 2 | 2016_02_Asomata_english.xlsx
1 | 105 | 0 | 105 | 0 | 0 | 4 | 105 | 35 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.9 | 6560.00000000002 | 40.781 | 2376.27 | 0 | 1060.5 | 1060.5 | 10.1 | 86.71518703182966 | 844.9 | 0 | 215.6 | 0 |  | 12.274305555555555 | 1060.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
2 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 35 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.2 | 7280.000000000014 | 40.46 | 2000.7 | 719.9999999999936 | 1552.9999999999936 | 833 | 9.8 | 88.73440371409225 | 1204.5 | 0 | 348.49999999999363 | 0 |  | 9.641203703703704 | 833 | 2016 | 3 | 2016_03_Asomata_english.xlsx
3 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 35 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 84.25 | 7400.000000000007 | 40.544 | 2098.98 | 119.99999999999363 | 944.4999999999935 | 824.5 | 9.7 | 89.54309766363691 | 791.8 | 0 | 152.69999999999345 | 0 |  | 9.542824074074073 | 824.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
4 | 185 | 120 | 305 | 0 | 0 | 4 | 305 | 108 | 3.8000000000029104 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.25 | 7400.000000000007 | 41.749 | 3508.8300000000063 | 0 | 3080.5 | 3080.5 | 10.1 | 85.99683637002754 | 3022.2 | 0 | 58.30000000000018 | 0 |  | 35.65393518518518 | 3080.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
5 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.25 | 7400.000000000007 | 41.65 | 3393 | 0 | 1775.051282051282 | 693 | 9.9 | 87.73414619568464 | 1709.4 | 1082.051282051282 | 65.6512820512819 | 0 |  | 8.020833333333334 | 693 | 2016 | 3 | 2016_03_Asomata_english.xlsx
6 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 84.3 | 7520 | 41.65 | 3393 | 119.99999999999272 | 776.4999999999927 | 656.5 | 10.1 | 85.89518526320718 | 828 | 0 | 8.499999999992724 | 60 |  | 7.59837962962963 | 656.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
7 | 210 | 0 | 210 | 0 | 0 | 2 | 210 | 51 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 83.6 | 5839.999999999993 | 41.408 | 3109.86 | -1680.0000000000073 | 2072.978371501265 | 2068.5 | 9.85 | 89.55730183522063 | 1933.05 | 1684.4783715012722 | 139.92837150126502 | 0 |  | 23.94097222222222 | 2068.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
8 | 110 | 55 | 165 | 0 | 0 | 3 | 165 | 70 | 2.7999999999956344 | 1.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.05 | 6920 | 41.802 | 3570.84 | 1080.0000000000073 | 2730.0000000000073 | 1650 | 10 | 87.26991676575506 | 2715.8 | 0 | 14.200000000007094 | 0 |  | 19.09722222222222 | 1650 | 2016 | 3 | 2016_03_Asomata_english.xlsx
9 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 55 | 2.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.35 | 7639.999999999993 | 41.503 | 3221.01 | 719.9999999999927 | 1781.4999999999927 | 1061.5 | 9.65 | 89.79452012895254 | 1537.5 | 0 | 243.99999999999272 | 0 |  | 12.28587962962963 | 1061.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
10 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 35 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.15 | 7160.00000000002 | 41.2 | 2866.5 | -479.9999999999727 | 1351.5000000000273 | 1831.5 | 9.9 | 87.9422936362438 | 1270.2 | 0 | 81.30000000002724 | 0 |  | 21.197916666666668 | 1831.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
11 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 35 | 0 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 11 | 84.3 | 7520 | 41.102 | 2751.84 | 359.99999999998 | 1547.99999999998 | 1188 | 9.9 | 87.63044153115075 | 1416.2 | 0 | 131.79999999997995 | 0 |  | 13.75 | 1188 | 2016 | 3 | 2016_03_Asomata_english.xlsx
12 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.4 | 7760.00000000002 | 40.582 | 2143.44 | 240.00000000002 | 877.00000000002 | 637 | 9.8 | 88.31584520600691 | 766.5 | 0 | 110.50000000002001 | 0 |  | 7.372685185185185 | 637 | 2016 | 3 | 2016_03_Asomata_english.xlsx
13 | 180 | 20 | 200 | 0 | 0 | 3 | 200 | 70 | 4.099999999998545 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.2 | 7280.000000000014 | 40.902 | 2517.84 | -480.00000000000637 | 1539.9999999999936 | 2020 | 10.1 | 86.09872835624795 | 985.5 | 0 | 554.4999999999936 | 0 |  | 23.37962962962963 | 2020 | 2016 | 3 | 2016_03_Asomata_english.xlsx
14 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.6 | 8239.999999999993 | 40.43 | 1965.6 | 959.9999999999791 | 2681.714285714265 | 686 | 9.8 | 87.90121682475808 | 2077.5 | 1035.7142857142858 | 604.2142857142649 | 0 |  | 7.939814814814815 | 686 | 2016 | 3 | 2016_03_Asomata_english.xlsx
15 | 0 | 220 | 220 | 0 | 0 | 4 | 220 | 55 | 0 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 84.25 | 7400.000000000007 | 41.645 | 3387.15 | -839.9999999999854 | 2584.1276595744825 | 2222 | 10.1 | 85.99683637002754 | 2430.9 | 1202.127659574468 | 213.22765957448246 | 60 |  | 25.71759259259259 | 2222 | 2016 | 3 | 2016_03_Asomata_english.xlsx
16 | 190 | 0 | 190 | 0 | 0 | 4 | 190 | 55 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.15 | 7160.00000000002 | 41.25 | 2925 | -239.99999999998727 | 1641.0000000000127 | 1881 | 9.9 | 87.9422936362438 | 1460 | 0 | 181.00000000001273 | 0 |  | 21.770833333333332 | 1881 | 2016 | 3 | 2016_03_Asomata_english.xlsx
17 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 55 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.3 | 7520 | 41.45 | 3159 | 359.99999999998 | 1731.99999999998 | 1372 | 9.8 | 88.52462971004005 | 1497.45 | 0 | 234.54999999997995 | 0 |  | 15.87962962962963 | 1372 | 2016 | 3 | 2016_03_Asomata_english.xlsx
18 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.25 | 7400.000000000007 | 41.11 | 2761.2 | -119.99999999999272 | 815.7500000000073 | 935.75 | 9.85 | 88.17949719160184 | 715.4 | 0 | 100.3500000000073 | 0 |  | 10.830439814814815 | 935.75 | 2016 | 3 | 2016_03_Asomata_english.xlsx
19 | 150 | 25 | 175 | 0 | 0 | 4 | 175 | 70 | 4 | 0.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 3.75 | 0 | 1 | 1 | ΧΑΜΗΜΗ ΡΟΗ ΝΕΡΟΥ ΣΤΟΥΣ ΔΑΚΤΥΛΙΟΥΣ ΣΤΕΓΑΝΟΤΗΤΑΣ | 19 | 84.5 | 8000.000000000007 | 41.44 | 3147.3 | 600 | 2315 | 1715 | 9.8 | 88.1080432172869 | 2035 | 0 | 280 | 0 |  | 19.849537037037038 | 1715 | 2016 | 3 | 2016_03_Asomata_english.xlsx
20 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 51 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 0 | 0 | 1 | ΧΑΜΗΜΗ ΡΟΗ ΝΕΡΟΥ ΣΤΟΥΣ ΔΑΚΤΥΛΙΟΥΣ ΣΤΕΓΑΝΟΤΗΤΑΣ | 20 | 84.6 | 8239.999999999993 | 40.78 | 2375.1 | 239.99999999998545 | 3509.958333333319 | 858.5 | 10.1 | 85.29028959233953 | 3292.3 | 2411.4583333333335 | 217.6583333333192 | 0 |  | 9.936342592592593 | 858.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
21 | 135 | 30 | 165 | 0 | 0 | 4 | 165 | 35 | 3.75 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.9 | 6560.00000000002 | 41.123 | 2776.41 | -1679.9999999999727 | 2336.492146596886 | 1650 | 10 | 87.58233890214795 | 2279.2 | 2366.4921465968587 | 57.29214659688569 | 0 |  | 19.09722222222222 | 1650 | 2016 | 3 | 2016_03_Asomata_english.xlsx
22 | 155 | 30 | 185 | 0 | 0 | 4 | 185 | 70 | 3.9500000000043656 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 84.15 | 7160.00000000002 | 41 | 2632.5 | 600 | 2940.047872340426 | 1951.75 | 10.55 | 82.52404805675958 | 2908.8 | 388.29787234042556 | 91.2478723404256 | 60 |  | 22.589699074074073 | 1951.75 | 2016 | 3 | 2016_03_Asomata_english.xlsx
23 | 330 | 0 | 330 | 0 | 0 | 3 | 330 | 55 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.35 | 7639.999999999993 | 41.62 | 3357.9 | 479.9999999999727 | 3730.4999999999727 | 3250.5 | 9.85 | 87.97128114156266 | 3590.9 | 0 | 139.59999999997262 | 0 |  | 37.62152777777778 | 3250.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
24 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.4 | 7760.00000000002 | 40.81 | 2410.2 | 120.00000000002728 | 1170.0000000000273 | 1050 | 10 | 86.54952830188678 | 1036.6 | 0 | 133.40000000002738 | 0 |  | 12.152777777777779 | 1050 | 2016 | 3 | 2016_03_Asomata_english.xlsx
25 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 35 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.4 | 7760.00000000002 | 40.83 | 2433.6 | 0 | 1831.5 | 1831.5 | 9.9 | 87.4237659615018 | 1721.4 | 0 | 110.1 | 0 |  | 21.197916666666668 | 1831.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
26 | 175 | 125 | 300 | 0 | 0 | 4 | 300 | 109 | 3.7999999999956344 | 2.6499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.55 | 8120 | 41.803 | 3572.0099999999916 | 359.99999999998 | 4214.468085106363 | 3030 | 10.1 | 85.39051319938106 | 4182.9 | 824.468085106383 | 91.56808510636347 | 60 |  | 35.06944444444444 | 3030 | 2016 | 3 | 2016_03_Asomata_english.xlsx
27 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 35 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.6 | 8239.999999999993 | 40.58 | 2141.1 | 119.99999999999272 | 1148.9999999999927 | 1029 | 9.8 | 87.90121682475808 | 960 | 0 | 188.99999999999272 | 0 |  | 11.909722222222221 | 1029 | 2016 | 3 | 2016_03_Asomata_english.xlsx
28 | 300 | 0 | 300 | 0 | 0 | 4 | 300 | 55 | 7.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.15 | 7160.00000000002 | 41.2655 | 2943.1350000000025 | -1079.9999999999727 | 1920.0000000000273 | 3000 | 10 | 87.06287069988136 | 1825.25 | 0 | 94.75000000002728 | 0 |  | 34.72222222222222 | 3000 | 2016 | 3 | 2016_03_Asomata_english.xlsx
29 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.3 | 7520 | 40.7 | 2281.5 | 359.99999999998 | 1045.99999999998 | 686 | 9.8 | 88.52462971004005 | 882 | 0 | 163.99999999998 | 0 |  | 7.939814814814815 | 686 | 2016 | 3 | 2016_03_Asomata_english.xlsx
30 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.85 | 8839.999999999993 | 40.648 | 2220.66 | 1319.9999999999927 | 2002.4999999999927 | 682.5 | 10.5 | 81.5624826359949 | 1737.21 | 0 | 265.2899999999927 | 0 |  | 7.899305555555555 | 682.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
31 | 95 | 60 | 155 | 0 | 0 | 4 | 155 | 70 | 2.599999999998545 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.2 | 7280.000000000014 | 40.978 | 2606.76 | -1559.999999999979 | 2806.520408163286 | 1565.5 | 10.1 | 86.09872835624795 | 2786.4 | 2801.020408163265 | 20.1204081632859 | 0 |  | 18.119212962962962 | 1565.5 | 2016 | 3 | 2016_03_Asomata_english.xlsx
1 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 35 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.3 | 7520 | 41.05 | 2691 | 239.99999999998636 | 2012.9999999999864 | 1773 | 9.85 | 88.07526610745101 | 1912.6 | 0 | 100.39999999998645 | 0 |  | 20.520833333333332 | 1773 | 2016 | 4 | 2016_04_Asomata_english.xlsx
2 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 55 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.6 | 8239.999999999993 | 41.24 | 2913.3 | 719.9999999999927 | 2669.9999999999927 | 1950 | 10 | 86.14319248826293 | 2535.75 | 0 | 134.24999999999272 | 0 |  | 22.569444444444443 | 1950 | 2016 | 4 | 2016_04_Asomata_english.xlsx
3 | 200 | 65 | 265 | 0 | 0 | 4 | 265 | 75 | 5.400000000001455 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.7 | 8480.000000000015 | 41.801 | 3569.67 | 240.00000000002183 | 2890.000000000022 | 2650 | 10 | 85.94145199063232 | 2760 | 0 | 130.00000000002183 | 0 |  | 30.671296296296298 | 2650 | 2016 | 4 | 2016_04_Asomata_english.xlsx
4 | 180 | 220 | 400 | 0 | 0 | 4 | 400 | 110 | 4 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84.3 | 7520 | 40.922 | 2541.24 | -960.0000000000146 | 2979.9999999999854 | 3940 | 9.85 | 88.07526610745101 | 2832.4 | 0 | 147.5999999999858 | 0 |  | 45.601851851851855 | 3940 | 2016 | 4 | 2016_04_Asomata_english.xlsx
5 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 55 | 5.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 83.8 | 6320 | 39.182 | 505.4400000000032 | -1200 | 1350 | 2550 | 10 | 87.79186602870813 | 1343.2 | 0 | 6.7999999999999545 | 0 |  | 29.51388888888889 | 2550 | 2016 | 4 | 2016_04_Asomata_english.xlsx
6 | 195 | 35 | 230 | 0 | 0 | 4 | 230 | 110 | 5.100000000005821 | 0.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 83.7 | 6080.000000000014 | 40.611 | 2177.37 | -239.99999999998636 | 2083.0000000000136 | 2323 | 10.1 | 87.13108720944037 | 2044 | 0 | 39.00000000001364 | 0 |  | 26.886574074074073 | 2323 | 2016 | 4 | 2016_04_Asomata_english.xlsx
7 | 90 | 0 | 90 | 0 | 0 | 5 | 90 | 52 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84 | 6800.000000000007 | 40.692 | 2272.14 | 719.9999999999936 | 1606.4999999999936 | 886.5 | 9.85 | 88.70437515107567 | 1387 | 0 | 219.49999999999363 | 0 |  | 10.260416666666666 | 886.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
8 | 150 | 0 | 150 | 0 | 0 | 4 | 150 | 35 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.4 | 7760.00000000002 | 41.227 | 2898.09 | 960.0000000000127 | 2557.5000000000127 | 1597.5 | 10.65 | 81.26716272477633 | 2533.1 | 0 | 84.40000000001282 | 60 |  | 18.489583333333332 | 1597.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
9 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.65 | 8360.00000000002 | 40.9 | 2515.5 | 600 | 1243.5 | 643.5 | 9.9 | 86.91131715750706 | 1005.75 | 0 | 237.75 | 0 |  | 7.447916666666667 | 643.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
10 | 105 | 0 | 105 | 0 | 0 | 5 | 105 | 35 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 40.92 | 2538.9 | -840.00000000002 | 914.7144670050561 | 1023.75 | 9.75 | 88.97860217009155 | 645 | 730.9644670050761 | 269.7144670050561 | 0 |  | 11.848958333333334 | 1023.75 | 2016 | 4 | 2016_04_Asomata_english.xlsx
11 | 180 | 60 | 240 | 0 | 0 | 4 | 240 | 110 | 4.099999999998545 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.15 | 7160.00000000002 | 41.547 | 3272.49 | -359.99999999998 | 2016.00000000002 | 2376 | 9.9 | 87.9422936362438 | 1795.8 | 0 | 220.20000000001983 | 0 |  | 27.5 | 2376 | 2016 | 4 | 2016_04_Asomata_english.xlsx
12 | 150 | 55 | 205 | 0 | 0 | 4 | 205 | 110 | 3.400000000001455 | 1.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.2 | 7280.000000000014 | 41.399 | 3099.33 | 119.99999999999363 | 2128.9999999999936 | 2009 | 9.8 | 88.73440371409225 | 2107.5 | 0 | 21.499999999993634 | 0 |  | 23.252314814814813 | 2009 | 2016 | 4 | 2016_04_Asomata_english.xlsx
13 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 55 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.8 | 6320 | 41.282 | 2962.44 | -960.0000000000136 | 1612.4999999999864 | 2572.5 | 10.5 | 83.61130097972203 | 1512.3 | 0 | 160.1999999999864 | 60 |  | 29.774305555555557 | 2572.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
14 | 45 | 60 | 105 | 0 | 0 | 4 | 105 | 70 | 1.2000000000043656 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.85 | 6439.999999999993 | 40.69 | 2269.8 | 119.99999999999272 | 1180.4999999999927 | 1060.5 | 10.1 | 86.81878940582232 | 1065.8 | 0 | 144.69999999999277 | 30 |  | 12.274305555555555 | 1060.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
15 | 165 | 0 | 165 | 0 | 0 | 5 | 165 | 35 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84 | 6800.000000000007 | 41.17 | 2831.4 | 360.00000000001455 | 1977.0000000000148 | 1617 | 9.8 | 89.15694849368319 | 1785 | 0 | 192.00000000001478 | 0 |  | 18.715277777777782 | 1617 | 2016 | 4 | 2016_04_Asomata_english.xlsx
16 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.4 | 7760.00000000002 | 40.88 | 2492.1 | 960.0000000000127 | 1869.0000000000127 | 909 | 10.1 | 85.69260227909582 | 1591.4 | 0 | 277.60000000001287 | 0 |  | 10.520833333333334 | 909 | 2016 | 4 | 2016_04_Asomata_english.xlsx
17 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 55 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480.000000000015 | 40.703 | 2285.01 | 719.9999999999945 | 2406.6956521739075 | 1078 | 9.8 | 87.6953591741146 | 2058 | 608.695652173913 | 348.69565217390755 | 0 |  | 12.476851851851851 | 1078 | 2016 | 4 | 2016_04_Asomata_english.xlsx
18 | 110 | 130 | 240 | 0 | 0 | 4 | 240 | 70 | 2.5 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.5 | 8000.000000000007 | 41.369 | 3064.23 | -480.0000000000073 | 2027.9999999999927 | 2508 | 10.45 | 82.62763861525472 | 1773.9 | 0 | 314.09999999999286 | 60 |  | 29.02777777777778 | 2508 | 2016 | 4 | 2016_04_Asomata_english.xlsx
19 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 40 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.5 | 8000.000000000007 | 41.09 | 2737.8 | 0 | 2110 | 2110 | 10.55 | 81.84443824923333 | 1785 | 0 | 425 | 100 |  | 24.421296296296298 | 2110 | 2016 | 4 | 2016_04_Asomata_english.xlsx
20 | 210 | 0 | 210 | 0 | 0 | 5 | 210 | 40 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.5 | 8000.000000000007 | 41.171 | 2832.57 | 0 | 2236.5 | 2236.5 | 10.65 | 81.07594587130627 | 1825 | 0 | 471.5 | 60 |  | 25.885416666666668 | 2236.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
21 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 88 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.4 | 7760.00000000002 | 41.37 | 3065.4 | -239.99999999998727 | 1729.5000000000127 | 1969.5 | 10.1 | 85.69260227909582 | 1531.8 | 0 | 197.70000000001255 | 0 |  | 22.79513888888889 | 1969.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
22 | 220 | 0 | 220 | 0 | 0 | 4 | 220 | 55 | 5.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.3 | 7520 | 41.252 | 2927.34 | -240.00000000002 | 1981.99999999998 | 2222 | 10.1 | 85.89518526320718 | 1832.3 | 0 | 209.69999999998004 | 60 |  | 25.71759259259259 | 2222 | 2016 | 4 | 2016_04_Asomata_english.xlsx
23 | 235 | 95 | 330 | 0 | 0 | 4 | 330 | 70 | 5.700000000004366 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.3 | 7520 | 41.834 | 3608.2800000000066 | 0 | 3333 | 3333 | 10.1 | 85.89518526320718 | 3328.8 | 0 | 64.19999999999982 | 60 |  | 38.576388888888886 | 3333 | 2016 | 4 | 2016_04_Asomata_english.xlsx
24 | 205 | 95 | 300 | 0 | 0 | 4 | 300 | 70 | 5.400000000001455 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 24 | 84.4 | 7760.00000000002 | 41.821 | 3593.0699999999933 | 240.00000000002 | 3270.00000000002 | 3030 | 10.1 | 85.69260227909582 | 3022.2 | 0 | 307.8000000000202 | 60 |  | 35.06944444444444 | 3030 | 2016 | 4 | 2016_04_Asomata_english.xlsx
25 | 0 | 285 | 285 | 0 | 0 | 4 | 285 | 55 | 0 | 7.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.6 | 8239.999999999993 | 41.012 | 2646.54 | 479.9999999999727 | 3321.449999999973 | 2841.45 | 9.97 | 86.40239968732489 | 3225 | 0 | 96.44999999997299 | 0 |  | 32.887152777777786 | 2841.45 | 2016 | 4 | 2016_04_Asomata_english.xlsx
26 | 420 | 50 | 470 | 0 | 0 | 3 | 470 | 110 | 9.799999999995634 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84.25 | 7400.000000000007 | 41.389 | 3087.6300000000065 | -839.9999999999854 | 5105.7051282051425 | 4817.5 | 10.25 | 84.73834608168566 | 5137.65 | 1128.2051282051282 | 28.055128205142864 | 60 |  | 55.758101851851855 | 4817.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
27 | 230 | 260 | 490 | 0 | 0 | 4 | 490 | 110 | 4.80000000000291 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 84.3 | 7520 | 41.782 | 3547.44 | 119.99999999999272 | 5068.999999999993 | 4949 | 10.1 | 85.89518526320718 | 4993.2 | 0 | 135.7999999999929 | 60 |  | 57.280092592592595 | 4949 | 2016 | 4 | 2016_04_Asomata_english.xlsx
28 | 320 | 0 | 320 | 0 | 0 | 3 | 320 | 55 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.35 | 7639.999999999993 | 40.937 | 2558.79 | 119.99999999999272 | 3351.9999999999927 | 3232 | 10.1 | 85.79377418261309 | 3285 | 0 | 126.99999999999272 | 60 |  | 37.407407407407405 | 3232 | 2016 | 4 | 2016_04_Asomata_english.xlsx
29 | 280 | 0 | 280 | 0 | 0 | 5 | 280 | 45 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.05 | 6920 | 40.449 | 1987.83 | -719.9999999999927 | 2108.0000000000073 | 2828 | 10.1 | 86.4058581839159 | 1971 | 0 | 137.00000000000728 | 0 |  | 32.73148148148148 | 2828 | 2016 | 4 | 2016_04_Asomata_english.xlsx
30 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 40 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.55 | 8120 | 40.12 | 1602.8999999999946 | 1200 | 3674.5 | 2474.5 | 10.1 | 85.39051319938106 | 3445.6 | 0 | 228.9 | 0 |  | 28.640046296296298 | 2474.5 | 2016 | 4 | 2016_04_Asomata_english.xlsx
1 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 55 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.7 | 6080.000000000014 | 39.361 | 714.869999999999 | -2039.9999999999864 | 2211.414893617035 | 1969.5 | 10.1 | 87.13108720944037 | 2168.1 | 2281.9148936170213 | 103.31489361703507 | 60 |  | 22.79513888888889 | 1969.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
2 | 205 | 0 | 205 | 0 | 0 | 3 | 205 | 50 | 5.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 83.7 | 6080.000000000014 | 40.46 | 2000.7 | 0 | 2557.6794871794873 | 2070.5 | 10.1 | 87.13108720944037 | 2425.5 | 487.1794871794872 | 132.1794871794873 | 0 |  | 23.96412037037037 | 2070.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
3 | 265 | 0 | 265 | 0 | 0 | 3 | 265 | 55 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.05 | 6920 | 41.18 | 2843.1 | 839.9999999999864 | 5138.840425531901 | 2676.5 | 10.1 | 86.4058581839159 | 5068.8 | 1622.340425531915 | 130.04042553190084 | 60 |  | 30.97800925925926 | 2676.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
4 | 315 | 0 | 315 | 0 | 0 | 4 | 315 | 55 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 4 | 84.1 | 7039.999999999993 | 40.93 | 2550.6 | 119.99999999999272 | 3348.7499999999927 | 3228.75 | 10.25 | 85.0402641793639 | 3166.6 | 0 | 182.14999999999281 | 0 |  | 37.369791666666664 | 3228.75 | 2016 | 5 | 2016_05_Asomata_english.xlsx
5 | 270 | 60 | 330 | 0 | 0 | 4 | 330 | 70 | 6.80000000000291 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.3 | 7520 | 41.4095 | 3111.6149999999975 | 480.0000000000073 | 3747.0000000000073 | 3267 | 9.9 | 87.63044153115075 | 3642.7 | 0 | 104.30000000000746 | 0 |  | 37.8125 | 3267 | 2016 | 5 | 2016_05_Asomata_english.xlsx
6 | 205 | 190 | 395 | 0 | 0 | 3 | 395 | 75 | 5.400000000001455 | 5.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.5 | 8000.000000000007 | 41.78 | 3545.1 | 480.0000000000073 | 4469.500000000007 | 3989.5 | 10.1 | 85.49097262667443 | 4431.1 | 0 | 38.40000000000782 | 0 |  | 46.17476851851852 | 3989.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
7 | 160 | 45 | 205 | 0 | 0 | 3 | 205 | 80 | 4 | 1.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.65 | 8360.00000000002 | 41.39 | 3088.8 | 360.00000000001273 | 2369.0000000000127 | 2009 | 9.8 | 87.79816733258366 | 2255.7 | 0 | 173.30000000001291 | 60 |  | 23.252314814814813 | 2009 | 2016 | 5 | 2016_05_Asomata_english.xlsx
8 | 170 | 65 | 235 | 0 | 0 | 4 | 235 | 75 | 4.19999999999709 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.55 | 8120 | 41.69 | 3439.8 | -240.00000000002 | 2227.49999999998 | 2467.5 | 10.5 | 82.13754126797606 | 1977.15 | 0 | 250.34999999998013 | 0 |  | 28.55902777777778 | 2467.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
9 | 280 | 0 | 280 | 0 | 0 | 4 | 280 | 55 | 6.5 | 0 | 0 | 0 | 0 | 0 | 16.25 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 9 | 84.45 | 7880.000000000014 | 41.38 | 3077.1 | -239.99999999998636 | 2490.0000000000136 | 2730 | 9.75 | 88.66419014828908 | 2286.6 | 0 | 203.40000000001328 | 0 |  | 31.59722222222222 | 2730 | 2016 | 5 | 2016_05_Asomata_english.xlsx
10 | 380 | 0 | 380 | 0 | 0 | 4 | 380 | 55 | 8.599999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 10 | 84 | 6800.000000000007 | 41.832 | 3605.94 | -1080.0000000000064 | 2757.9999999999936 | 3838 | 10.1 | 86.50872230080151 | 2695.55 | 0 | 122.44999999999345 | 60 |  | 44.4212962962963 | 3838 | 2016 | 5 | 2016_05_Asomata_english.xlsx
11 | 310 | 0 | 310 | 0 | 0 | 4 | 310 | 55 | 7.200000000004366 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 11 | 83.8 | 6320 | 41.7 | 3451.5 | -480.0000000000073 | 2650.9999999999927 | 3131 | 10.1 | 86.9226396323843 | 2606.1 | 0 | 104.89999999999281 | 60 |  | 36.238425925925924 | 3131 | 2016 | 5 | 2016_05_Asomata_english.xlsx
12 | 340 | 0 | 340 | 0 | 0 | 4 | 340 | 40 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 12 | 84.15 | 7160.00000000002 | 41.852 | 3629.34 | 840.00000000002 | 4410.00000000002 | 3570 | 10.5 | 82.91701971417272 | 4020.45 | 0 | 389.5500000000202 | 0 |  | 41.31944444444444 | 3570 | 2016 | 5 | 2016_05_Asomata_english.xlsx
13 | 345 | 0 | 345 | 0 | 0 | 3 | 345 | 55 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 13 | 84.2 | 7280.000000000014 | 41.537 | 3260.79 | 119.99999999999363 | 3535.4999999999936 | 3415.5 | 9.9 | 87.83809660586911 | 3367 | 0 | 168.49999999999363 | 0 |  | 39.53125 | 3415.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
14 | 295 | 0 | 295 | 0 | 0 | 3 | 295 | 50 | 7 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 14 | 84.1 | 7039.999999999993 | 41.456 | 3166.02 | -240.00000000002092 | 2813.249999999979 | 3053.25 | 10.35 | 84.21861911482898 | 2628 | 0 | 185.24999999997908 | 0 |  | 35.338541666666664 | 3053.25 | 2016 | 5 | 2016_05_Asomata_english.xlsx
15 | 435 | 0 | 435 | 0 | 0 | 4 | 435 | 50 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 15 | 84.5 | 8000.000000000007 | 41.602 | 3336.84 | 960.0000000000146 | 5353.500000000015 | 4393.5 | 10.1 | 85.49097262667443 | 5234.4 | 0 | 179.100000000014 | 60 |  | 50.85069444444444 | 4393.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
16 | 355 | 0 | 355 | 0 | 0 | 3 | 355 | 40 | 8.900000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 16 | 84.6 | 8239.999999999993 | 41.24 | 2913.3 | 239.99999999998545 | 3914.2499999999854 | 3674.25 | 10.35 | 83.23013766981926 | 3708.4 | 0 | 265.84999999998536 | 60 |  | 42.526041666666664 | 3674.25 | 2016 | 5 | 2016_05_Asomata_english.xlsx
17 | 410 | 0 | 410 | 0 | 0 | 4 | 410 | 45 | 9.69999999999709 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 17 | 84.25 | 7400.000000000007 | 41.473 | 3185.91 | -839.9999999999854 | 3526.5000000000146 | 4366.5 | 10.65 | 81.55568519598854 | 3328.8 | 0 | 197.70000000001482 | 0 |  | 50.53819444444444 | 4366.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
18 | 550 | 0 | 550 | 0 | 0 | 4 | 550 | 50 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 18 | 84.1 | 7039.999999999993 | 41.922 | 3711.24 | -360.00000000001455 | 5029.999999999985 | 5390 | 9.8 | 88.94517426923264 | 4861.8 | 0 | 168.19999999998527 | 0 |  | 62.38425925925926 | 5390 | 2016 | 5 | 2016_05_Asomata_english.xlsx
19 | 420 | 0 | 420 | 0 | 0 | 4 | 420 | 45 | 9.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 19 | 84.15 | 7160.00000000002 | 41.577 | 3307.59 | 120.00000000002728 | 4572.000000000027 | 4452 | 10.6 | 82.13478367913336 | 4314.45 | 0 | 257.55000000002747 | 0 |  | 51.52777777777778 | 4452 | 2016 | 5 | 2016_05_Asomata_english.xlsx
20 | 460 | 0 | 460 | 0 | 0 | 3 | 460 | 55 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 20 | 83.9 | 6560.00000000002 | 41.8 | 3568.5 | -600 | 4046 | 4646 | 10.1 | 86.71518703182966 | 4051.5 | 0 | 54.5 | 60 |  | 53.773148148148145 | 4646 | 2016 | 5 | 2016_05_Asomata_english.xlsx
21 | 175 | 390 | 565 | 0 | 0 | 4 | 565 | 110 | 3.5 | 8.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 83.7 | 6080.000000000014 | 41.95 | 3744 | -480.00000000000637 | 5226.499999999994 | 5706.5 | 10.1 | 87.13108720944037 | 4839.9 | 0 | 446.599999999994 | 60 |  | 66.04745370370371 | 5706.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
22 | 115 | 340 | 455 | 0 | 0 | 4 | 455 | 70 | 2.900000000001455 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 83.7 | 6080.000000000014 | 41.965 | 3761.55 | 0 | 4595.5 | 4595.5 | 10.1 | 87.13108720944037 | 4555.2 | 0 | 100.3 | 60 |  | 53.188657407407405 | 4595.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
23 | 0 | 470 | 470 | 0 | 0 | 3 | 470 | 45 | 0 | 11.5 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 23 | 83.8 | 6320 | 41.329 | 3017.43 | 239.99999999998636 | 4986.999999999986 | 4747 | 10.1 | 86.9226396323843 | 4869.1 | 0 | 117.899999999986 | 0 |  | 54.942129629629626 | 4747 | 2016 | 5 | 2016_05_Asomata_english.xlsx
24 | 0 | 430 | 430 | 0 | 0 | 3 | 430 | 45 | 0 | 9.69999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 24 | 84.1 | 7039.999999999993 | 41.191 | 2855.97 | 719.9999999999927 | 4955.499999999993 | 4235.5 | 9.85 | 88.49367592268831 | 4777.5 | 0 | 177.99999999999272 | 0 |  | 49.02199074074074 | 4235.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
25 | 0 | 700 | 700 | 0 | 0 | 4 | 700 | 40 | 0 | 17.30000000000291 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 25 | 83.8 | 6320 | 41.821 | 3593.0699999999933 | -719.9999999999927 | 6420.000000000006 | 7140 | 10.2 | 86.07045689089034 | 6447 | 0 | 33.00000000000637 | 60 |  | 82.63888888888887 | 7140 | 2016 | 5 | 2016_05_Asomata_english.xlsx
26 | 0 | 730 | 730 | 0 | 0 | 3 | 730 | 40 | 0 | 16.900000000001455 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 26 | 83.5 | 5600.000000000007 | 41.861 | 3639.8699999999935 | -719.9999999999927 | 6653.000000000007 | 7373 | 10.1 | 87.55099606346177 | 6643 | 0 | 70.00000000000728 | 60 |  | 85.33564814814815 | 7373 | 2016 | 5 | 2016_05_Asomata_english.xlsx
27 | 0 | 775 | 775 | 0 | 0 | 4 | 775 | 40 | 0 | 19.099999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 27 | 84.25 | 7400.000000000007 | 41.7 | 3451.5 | 1800 | 9550 | 7750 | 10 | 86.85680473372781 | 9442.5 | 0 | 107.5 | 0 |  | 89.69907407407408 | 7750 | 2016 | 5 | 2016_05_Asomata_english.xlsx
28 | 0 | 795 | 795 | 0 | 0 | 4 | 795 | 40 | 0 | 19 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 28 | 84.3 | 7520 | 41.589 | 3321.63 | 119.99999999999272 | 8149.499999999993 | 8029.5 | 10.1 | 85.89518526320718 | 8217.3 | 0 | 32.19999999999345 | 100 |  | 92.93402777777777 | 8029.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
29 | 0 | 725 | 725 | 0 | 0 | 4 | 725 | 45 | 0 | 18 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 29 | 84.5 | 8000.000000000007 | 41.698 | 3449.16 | 480.0000000000073 | 7802.500000000007 | 7322.5 | 10.1 | 85.49097262667443 | 7822.1 | 0 | 40.40000000000691 | 60 |  | 84.7511574074074 | 7322.5 | 2016 | 5 | 2016_05_Asomata_english.xlsx
30 | 0 | 810 | 810 | 0 | 0 | 4 | 810 | 45 | 0 | 19.25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 30 | 84.8 | 8720 | 41.549 | 3274.83 | 719.9999999999927 | 8738.999999999993 | 8019 | 9.9 | 86.60672141980554 | 8679.2 | 0 | 59.799999999991996 | 0 |  | 92.8125 | 8019 | 2016 | 5 | 2016_05_Asomata_english.xlsx
31 | 0 | 790 | 790 | 0 | 0 | 4 | 790 | 40 | 0 | 19.30000000000291 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 31 | 85 | 9200.000000000007 | 41.501 | 3218.6699999999937 | 480.0000000000073 | 8459.000000000007 | 7979 | 10.1 | 84.49689154962007 | 8475 | 0 | 44.000000000007276 | 60 |  | 92.34953703703704 | 7979 | 2016 | 5 | 2016_05_Asomata_english.xlsx
1 | 0 | 840 | 840 | 0 | 0 | 2 | 840 | 55 | 0 | 19.32999999999447 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 85 | 9200.000000000007 | 41.569 | 3298.2300000000064 | 0 | 8274 | 8274 | 9.85 | 86.6414827057018 | 7965.25 | 0 | 308.75 | 0 |  | 95.76388888888889 | 8274 | 2016 | 6 | 2016_06_Asomata_english.xlsx
2 | 0 | 760 | 760 | 0 | 0 | 2 | 760 | 40 | 0 | 20.220000000001164 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 83.6 | 5839.999999999993 | 41.421 | 3125.07 | -3360.0000000000146 | 4505.999999999985 | 7866 | 10.35 | 85.23086213303606 | 4416.5 | 0 | 149.49999999998545 | 60 |  | 91.04166666666667 | 7866 | 2016 | 6 | 2016_06_Asomata_english.xlsx
3 | 0 | 780 | 780 | 0 | 0 | 3 | 780 | 40 | 0 | 19.099999999998545 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 3 | 83.7 | 6080.000000000014 | 41.652 | 3395.34 | 240.00000000002092 | 8469.000000000022 | 8229 | 10.55 | 83.41459533794765 | 8560.05 | 0 | 58.95000000002074 | 150 |  | 95.24305555555556 | 8229 | 2016 | 6 | 2016_06_Asomata_english.xlsx
4 | 610 | 195 | 805 | 0 | 0 | 4 | 805 | 80 | 14.200000000004366 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 83.5 | 5600.000000000007 | 41.542 | 3266.64 | -480.00000000000637 | 7650.499999999994 | 8130.5 | 10.1 | 87.55099606346177 | 7613.9 | 0 | 36.599999999994 | 0 |  | 94.10300925925925 | 8130.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
5 | 155 | 570 | 725 | 0 | 0 | 5 | 725 | 90 | 3.6999999999970896 | 13.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 5 | 84.85 | 8839.999999999993 | 40.92 | 2538.9 | 3239.9999999999854 | 10562.5 | 7322.5 | 10.1 | 84.79267996811352 | 10575 | 0 | 47.49999999998545 | 60 |  | 84.7511574074074 | 7322.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
6 | 60 | 805 | 865 | 0 | 0 | 5 | 865 | 80 | 1.5 | 18.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.8 | 8720 | 41.501 | 3218.6699999999937 | -119.99999999999272 | 8616.500000000007 | 8736.5 | 10.1 | 84.89173683723513 | 8614 | 0 | 12.500000000007276 | 10 |  | 101.11689814814815 | 8736.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
7 | 165 | 800 | 965 | 0 | 0 | 4 | 965 | 80 | 4.19999999999709 | 19.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84 | 6800.000000000007 | 41.7515 | 3511.754999999996 | -1919.9999999999927 | 7585.250000000007 | 9505.25 | 9.85 | 88.70437515107567 | 7469.5 | 0 | 115.75000000000728 | 0 |  | 110.0144675925926 | 9505.25 | 2016 | 6 | 2016_06_Asomata_english.xlsx
8 | 0 | 760 | 760 | 0 | 0 | 4 | 760 | 55 | 0 | 17.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.5 | 8000.000000000007 | 41.5 | 3217.5 | 1200 | 8952 | 7752 | 10.2 | 84.65282583621685 | 9000 | 0 | 12 | 60 |  | 89.72222222222221 | 7752 | 2016 | 6 | 2016_06_Asomata_english.xlsx
9 | 180 | 670 | 850 | 0 | 0 | 5 | 850 | 90 | 4.55000000000291 | 15.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 83.75 | 6200.000000000007 | 41.45 | 3159 | -1800 | 6700 | 8500 | 10 | 87.89700598802395 | 6645 | 0 | 55 | 0 |  | 98.37962962962963 | 8500 | 2016 | 6 | 2016_06_Asomata_english.xlsx
10 | 70 | 755 | 825 | 0 | 0 | 4 | 825 | 70 | 1.4000000000014552 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84 | 6800.000000000007 | 41.75 | 3510 | 600 | 8932.5 | 8332.5 | 10.1 | 86.50872230080151 | 8760 | 0 | 172.5 | 0 |  | 96.44097222222223 | 8332.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
11 | 605 | 15 | 620 | 0 | 0 | 4 | 620 | 80 | 13.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.4 | 7760.00000000002 | 41.35 | 3042 | 960.0000000000127 | 7222.000000000013 | 6262 | 10.1 | 85.69260227909582 | 7080 | 0 | 142.00000000001273 | 0 |  | 72.47685185185185 | 6262 | 2016 | 6 | 2016_06_Asomata_english.xlsx
12 | 645 | 120 | 765 | 0 | 0 | 4 | 765 | 80 | 14.25 | 3.150999999998021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.4 | 7760.00000000002 | 41.98 | 3779.1 | 0 | 7650 | 7650 | 10 | 86.54952830188678 | 7530 | 0 | 120 | 0 |  | 88.54166666666667 | 7650 | 2016 | 6 | 2016_06_Asomata_english.xlsx
13 | 570 | 165 | 735 | 0 | 0 | 4 | 735 | 80 | 13.400000000001455 | 3.8990000000048894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.05 | 6920 | 42.031 | 3838.7699999999936 | -840.00000000002 | 6509.99999999998 | 7350 | 10 | 87.26991676575506 | 6453.2 | 0 | 116.79999999998017 | 60 |  | 85.06944444444444 | 7350 | 2016 | 6 | 2016_06_Asomata_english.xlsx
14 | 540 | 135 | 675 | 0 | 0 | 4 | 675 | 80 | 12.69999999999709 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84 | 6800.000000000007 | 42.001 | 3803.6699999999937 | -119.99999999999272 | 6697.500000000007 | 6817.5 | 10.1 | 86.50872230080151 | 6475.1 | 0 | 222.40000000000782 | 0 |  | 78.90625 | 6817.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
15 | 180 | 520 | 700 | 0 | 0 | 3 | 700 | 85 | 4.599999999998545 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 15 | 84.05 | 6920 | 41.9 | 3685.5 | 119.99999999999272 | 7294.999999999993 | 7175 | 10.25 | 85.14138221049274 | 7345.7 | 0 | 9.299999999992906 | 60 |  | 83.04398148148148 | 7175 | 2016 | 6 | 2016_06_Asomata_english.xlsx
16 | 580 | 155 | 735 | 0 | 0 | 3 | 735 | 110 | 12.700000000004366 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.4 | 7760.00000000002 | 41.967 | 3763.89 | 840.00000000002 | 8116.50000000002 | 7276.5 | 9.9 | 87.4237659615018 | 8002.5 | 0 | 114.00000000002001 | 0 |  | 84.21875 | 7276.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
17 | 235 | 895 | 1130 | 0 | 0 | 3 | 1130 | 100 | 4.899999999994179 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 85 | 9200.000000000007 | 42.151 | 3979.17 | 1439.9999999999873 | 12853 | 11413 | 10.1 | 84.49689154962007 | 12949.09 | 0 | 3.9099999999853026 | 100 |  | 132.09490740740742 | 11413 | 2016 | 6 | 2016_06_Asomata_english.xlsx
18 | 620 | 105 | 725 | 0 | 0 | 3 | 725 | 100 | 12.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.35 | 7639.999999999993 | 41.399 | 3099.33 | -1560.0000000000146 | 5762.499999999985 | 7322.5 | 10.1 | 85.79377418261309 | 5606.4 | 0 | 156.0999999999858 | 0 |  | 84.7511574074074 | 7322.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
19 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 55 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.45 | 7880.000000000014 | 41.52 | 3240.9 | 240.00000000002092 | 5635.500000000021 | 5395.5 | 9.9 | 87.32079332786046 | 5572.5 | 0 | 63.00000000002092 | 0 |  | 62.447916666666664 | 5395.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
20 | 520 | 155 | 675 | 0 | 0 | 2 | 675 | 80 | 12.200000000004366 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 20 | 84.1 | 7039.999999999993 | 41.981 | 3780.27 | -840.0000000000209 | 5977.499999999979 | 6817.5 | 10.1 | 86.3032383998495 | 5937.65 | 0 | 39.849999999979445 | 0 |  | 78.90625 | 6817.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
21 | 135 | 465 | 600 | 0 | 0 | 4 | 600 | 90 | 2.7999999999956344 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 83.9 | 6560.00000000002 | 42.051 | 3862.17 | -479.9999999999727 | 5520.000000000027 | 6000 | 10 | 87.58233890214795 | 5438.5 | 0 | 81.50000000002728 | 0 |  | 69.44444444444444 | 6000 | 2016 | 6 | 2016_06_Asomata_english.xlsx
22 | 80 | 525 | 605 | 0 | 0 | 4 | 605 | 90 | 1.75 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 83.8 | 6320 | 42.061 | 3873.87 | -240.00000000002 | 5870.49999999998 | 6110.5 | 10.1 | 86.9226396323843 | 5897.51 | 0 | 32.98999999997977 | 60 |  | 70.72337962962963 | 6110.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
23 | 105 | 535 | 640 | 0 | 0 | 4 | 640 | 90 | 2.4500000000043656 | 12.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 23 | 84 | 6800.000000000007 | 42.0715 | 3886.1549999999957 | 480.0000000000073 | 6816.000000000007 | 6336 | 9.9 | 88.25637325637325 | 6786.95 | 0 | 29.05000000000655 | 0 |  | 73.33333333333333 | 6336 | 2016 | 6 | 2016_06_Asomata_english.xlsx
24 | 80 | 505 | 585 | 0 | 0 | 4 | 585 | 90 | 1.6999999999970896 | 10.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.05 | 6920 | 41.811 | 3581.37 | 119.99999999999272 | 6028.499999999993 | 5908.5 | 10.1 | 86.4058581839159 | 5956.9 | 0 | 71.59999999999309 | 0 |  | 68.38541666666667 | 5908.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
25 | 535 | 165 | 700 | 0 | 0 | 3 | 700 | 90 | 12.099999999998545 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.5 | 8000.000000000007 | 42.029 | 3836.4300000000067 | 1080.0000000000073 | 8010.000000000007 | 6930 | 9.9 | 87.21806298276887 | 7972.8 | 0 | 37.200000000008004 | 0 |  | 80.20833333333333 | 6930 | 2016 | 6 | 2016_06_Asomata_english.xlsx
26 | 450 | 220 | 670 | 0 | 0 | 4 | 670 | 90 | 9.599999999998545 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84 | 6800.000000000007 | 41.998 | 3800.16 | -1200 | 5600.5 | 6800.5 | 10.15 | 86.08257095941825 | 5641.35 | 0 | 19.149999999999636 | 60 |  | 78.70949074074075 | 6800.5 | 2016 | 6 | 2016_06_Asomata_english.xlsx
27 | 560 | 145 | 705 | 0 | 0 | 3 | 705 | 110 | 11.400000000001455 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 83.75 | 6200.000000000007 | 42.04 | 3849.3 | -600 | 6450 | 7050 | 10 | 87.89700598802395 | 6153.9 | 0 | 296.1 | 0 |  | 81.59722222222223 | 7050 | 2016 | 6 | 2016_06_Asomata_english.xlsx
28 | 515 | 70 | 585 | 0 | 0 | 3 | 585 | 55 | 10.200000000004366 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.1 | 7039.999999999993 | 41.143 | 2799.81 | 839.9999999999854 | 6799.999999999985 | 5960 | 10.188034188034187 | 85.55749732978369 | 6840 | 0 | 19.999999999985448 | 60 |  | 68.98148148148148 | 5960 | 2016 | 6 | 2016_06_Asomata_english.xlsx
29 | 525 | 145 | 670 | 0 | 0 | 3 | 670 | 100 | 11.299999999995634 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.05 | 6920 | 41.881 | 3663.27 | -119.99999999999272 | 6446.000000000007 | 6566 | 9.8 | 89.05093547526026 | 6256.1 | 0 | 189.90000000000782 | 0 |  | 75.99537037037037 | 6566 | 2016 | 6 | 2016_06_Asomata_english.xlsx
30 | 120 | 515 | 635 | 0 | 0 | 3 | 635 | 90 | 2.900000000001455 | 11.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.4 | 7760.00000000002 | 42.03 | 3837.6 | 840.00000000002 | 7190.00000000002 | 6350 | 10 | 86.54952830188678 | 7021.5 | 0 | 168.50000000002 | 0 |  | 73.49537037037037 | 6350 | 2016 | 6 | 2016_06_Asomata_english.xlsx
1 | 345 | 255 | 600 | 0 | 0 | 3 | 600 | 90 | 7.69999999999709 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.2 | 7280.000000000014 | 41.1 | 2749.5 | -480.00000000000637 | 5639.999999999994 | 6120 | 10.2 | 85.25462317628474 | 5663 | 0 | 36.99999999999363 | 60 |  | 70.83333333333333 | 6120 | 2016 | 7 | 2016_07_Asomata_english.xlsx
2 | 615 | 0 | 615 | 0 | 0 | 4 | 615 | 50 | 12.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.45 | 7880.000000000014 | 41.603 | 3338.01 | 600 | 6627 | 6027 | 9.8 | 88.21182183120597 | 6349.2 | 0 | 307.8 | 30 |  | 69.75694444444444 | 6027 | 2016 | 7 | 2016_07_Asomata_english.xlsx
3 | 0 | 535 | 535 | 0 | 0 | 3 | 535 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 3 | 83.9 | 6560.00000000002 | 41.449 | 3157.83 | -1319.9999999999936 | 4083.5000000000064 | 5403.5 | 10.1 | 86.71518703182966 | 4073.4 | 0 | 40.100000000006276 | 30 |  | 62.54050925925926 | 5403.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
4 | 640 | 10 | 650 | 0 | 0 | 4 | 650 | 50 | 12.75 | 0.1500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.3 | 7520 | 41.621 | 3359.07 | 959.99999999998 | 7329.99999999998 | 6370 | 9.8 | 88.52462971004005 | 7081.8 | 0 | 248.1999999999789 | 0 |  | 73.72685185185185 | 6370 | 2016 | 7 | 2016_07_Asomata_english.xlsx
5 | 660 | 0 | 660 | 0 | 0 | 4 | 660 | 50 | 13.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.05 | 6920 | 41.799 | 3567.33 | -600 | 5934 | 6534 | 9.9 | 88.15143107652027 | 5950 | 0 | 14 | 30 |  | 75.625 | 6534 | 2016 | 7 | 2016_07_Asomata_english.xlsx
6 | 660 | 0 | 660 | 0 | 0 | 3 | 660 | 50 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.25 | 7400.000000000007 | 41.48 | 3194.1 | 480.0000000000073 | 7014.000000000007 | 6534 | 9.9 | 87.73414619568464 | 6759.8 | 0 | 284.2000000000071 | 30 |  | 75.625 | 6534 | 2016 | 7 | 2016_07_Asomata_english.xlsx
7 | 690 | 0 | 690 | 0 | 0 | 2 | 690 | 50 | 13.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.2 | 7280.000000000014 | 41.44 | 3147.3 | -119.99999999999363 | 6711.000000000006 | 6831 | 9.9 | 87.83809660586911 | 6465.6 | 0 | 275.400000000006 | 30 |  | 79.0625 | 6831 | 2016 | 7 | 2016_07_Asomata_english.xlsx
8 | 0 | 695 | 695 | 0 | 0 | 4 | 695 | 50 | 0 | 13.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.15 | 7160.00000000002 | 41.55 | 3276 | -119.99999999999363 | 6760.500000000006 | 6880.5 | 9.9 | 87.9422936362438 | 6759.8 | 0 | 30.700000000006185 | 30 |  | 79.63541666666667 | 6880.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
9 | 650 | 5 | 655 | 0 | 0 | 3 | 655 | 50 | 13.099999999998545 | 0.20000000000436557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.25 | 7400.000000000007 | 41.848 | 3624.66 | 239.99999999998727 | 6658.999999999988 | 6419 | 9.8 | 88.62939258543653 | 6423.2 | 0 | 235.79999999998745 | 0 |  | 74.2939814814815 | 6419 | 2016 | 7 | 2016_07_Asomata_english.xlsx
10 | 55 | 610 | 665 | 0 | 0 | 4 | 665 | 50 | 1.3000000000029104 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.5 | 8000.000000000007 | 41.889 | 3672.6300000000065 | 600 | 7316.5 | 6716.5 | 10.1 | 85.49097262667443 | 7300 | 0 | 76.5 | 60 |  | 77.73726851851852 | 6716.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
11 | 615 | 40 | 655 | 0 | 0 | 4 | 655 | 100 | 12.299999999995634 | 0.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.8 | 8720 | 42.086 | 3903.1199999999935 | 719.9999999999927 | 7138.999999999993 | 6419 | 9.8 | 87.49046347510966 | 6748.8 | 0 | 390.19999999999345 | 0 |  | 74.29398148148148 | 6419 | 2016 | 7 | 2016_07_Asomata_english.xlsx
12 | 15 | 650 | 665 | 0 | 0 | 4 | 665 | 50 | 0.4000000000014552 | 12.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.6 | 8239.999999999993 | 41.651 | 3394.17 | -480.0000000000073 | 6236.499999999993 | 6716.5 | 10.1 | 85.29028959233953 | 6180 | 0 | 56.499999999992724 | 0 |  | 77.73726851851852 | 6716.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
13 | 640 | 120 | 760 | 0 | 0 | 0 | 760 | 85 | 13.380000000004657 | 2.3300000000017462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.5 | 8000.000000000007 | 41.85 | 3627 | -239.99999999998545 | 7132.000000000015 | 7372 | 9.7 | 89.01637355973318 | 6710.4 | 0 | 421.600000000014 | 0 |  | 85.32407407407408 | 7372 | 2016 | 7 | 2016_07_Asomata_english.xlsx
14 | 105 | 635 | 740 | 0 | 0 | 8 | 740 | 85 | 3.0199999999967986 | 14.119999999995343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.5 | 8000.000000000007 | 41.7 | 3451.5 | 0 | 7622 | 7622 | 10.3 | 83.83095374071958 | 7657.5 | 0 | 4.5 | 40 |  | 88.2175925925926 | 7622 | 2016 | 7 | 2016_07_Asomata_english.xlsx
15 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 13.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.3 | 7520 | 41.23 | 2901.6 | -480.0000000000073 | 6387.999999999993 | 6868 | 10.1 | 85.89518526320718 | 6205 | 0 | 182.99999999999272 | 0 |  | 79.49074074074075 | 6868 | 2016 | 7 | 2016_07_Asomata_english.xlsx
16 | 760 | 0 | 760 | 0 | 0 | 4 | 760 | 50 | 15.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 83.65 | 5960.00000000002 | 41.8 | 3568.5 | -1559.99999999998 | 5888.000000000021 | 7448 | 9.8 | 89.90616654825193 | 5853.4 | 0 | 94.60000000002037 | 60 |  | 86.20370370370371 | 7448 | 2016 | 7 | 2016_07_Asomata_english.xlsx
17 | 295 | 385 | 680 | 0 | 0 | 4 | 680 | 50 | 5.75 | 8.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.15 | 7160.00000000002 | 41.9 | 3685.5 | 1200 | 8000 | 6800 | 10 | 87.06287069988136 | 7972.5 | 0 | 27.5 | 0 |  | 78.70370370370371 | 6800 | 2016 | 7 | 2016_07_Asomata_english.xlsx
18 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 13.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4 | 0 | 2 | 0 | ΒΛΑΒΗ ΣΤΟ ΣΥΣΤΗΜΑ ΦΡΕΝΩΝ | 18 | 84.4 | 7760.00000000002 | 41.6 | 3334.5 | 600 | 7332 | 6732 | 9.9 | 87.4237659615018 | 7241.6 | 0 | 90.39999999999964 | 0 |  | 77.91666666666667 | 6732 | 2016 | 7 | 2016_07_Asomata_english.xlsx
19 | 665 | 0 | 665 | 0 | 0 | 4 | 665 | 50 | 13.099999999998545 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 | 24 | 0 | 3 | 0 | ΒΛΑΒΗ ΣΤΟ ΣΥΣΤΗΜΑ ΦΡΕΝΩΝ | 19 | 84.75 | 8600.000000000007 | 41.18 | 2843.1 | 839.9999999999873 | 7290.499999999986 | 6450.5 | 9.7 | 88.49580997166457 | 7137.45 | 0 | 153.04999999998563 | 0 |  | 74.65856481481481 | 6450.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
20 | 695 | 0 | 695 | 0 | 0 | 2 | 695 | 50 | 13.80000000000291 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 0 | ΒΛΑΒΗ ΣΤΟ ΣΥΣΤΗΜΑ ΦΡΕΝΩΝ | 20 | 85 | 9200.000000000007 | 41.15 | 2808 | 600 | 7272 | 6672 | 9.6 | 88.89777131782945 | 6976.8 | 0 | 295.2000000000007 | 0 |  | 77.22222222222223 | 6672 | 2016 | 7 | 2016_07_Asomata_english.xlsx
21 | 0 | 650 | 650 | 0 | 0 | 2 | 650 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 83.8 | 6320 | 40.8 | 2398.5 | -2880.0000000000073 | 3684.9999999999927 | 6565 | 10.1 | 86.9226396323843 | 3693.6 | 0 | 51.399999999992815 | 60 |  | 75.98379629629629 | 6565 | 2016 | 7 | 2016_07_Asomata_english.xlsx
22 | 0 | 795 | 795 | 0 | 0 | 3 | 795 | 50 | 0 | 15.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.4 | 7760.00000000002 | 41.8 | 3568.5 | 1440.00000000002 | 9231.000000000022 | 7791 | 9.8 | 88.31584520600691 | 9212.6 | 0 | 18.400000000021464 | 0 |  | 90.17361111111113 | 7791 | 2016 | 7 | 2016_07_Asomata_english.xlsx
23 | 0 | 695 | 695 | 0 | 0 | 3 | 695 | 50 | 0 | 13.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 84.4 | 7760.00000000002 | 41.75 | 3510 | 0 | 6741.5 | 6741.5 | 9.7 | 89.22631783699669 | 6745.2 | 0 | 11.299999999999272 | 15 |  | 78.02662037037037 | 6741.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
24 | 0 | 735 | 735 | 0 | 0 | 4 | 735 | 55 | 0 | 15.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 24 | 84.7 | 8480.000000000015 | 42 | 3802.5 | 719.9999999999945 | 7775.9999999999945 | 7056 | 9.6 | 89.52234582357532 | 7676 | 0 | 99.99999999999545 | 0 |  | 81.66666666666667 | 7056 | 2016 | 7 | 2016_07_Asomata_english.xlsx
25 | 120 | 590 | 710 | 0 | 0 | 4 | 710 | 105 | 2.599999999998545 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 25 | 85 | 9200.000000000007 | 42 | 3802.5 | 719.9999999999927 | 7677.999999999993 | 6958 | 9.8 | 87.08353108685334 | 7365.7 | 0 | 312.2999999999938 | 0 |  | 80.5324074074074 | 6958 | 2016 | 7 | 2016_07_Asomata_english.xlsx
26 | 10 | 705 | 715 | 0 | 0 | 3 | 715 | 50 | 0.19999999999708962 | 14.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.75 | 8600.000000000007 | 42.001 | 3803.6699999999937 | -600 | 6478.5 | 7078.5 | 9.9 | 86.70801583082284 | 6278 | 0 | 260.5 | 60 |  | 81.92708333333333 | 7078.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
27 | 0 | 690 | 690 | 0 | 0 | 4 | 690 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.1 | 7039.999999999993 | 41.87 | 3650.4 | -1560.0000000000146 | 5270.999999999985 | 6831 | 9.9 | 88.04673816550302 | 5175.9 | 0 | 125.09999999998581 | 30 |  | 79.0625 | 6831 | 2016 | 7 | 2016_07_Asomata_english.xlsx
28 | 0 | 705 | 705 | 0 | 0 | 4 | 705 | 50 | 0 | 13.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.3 | 7520 | 41.97 | 3767.4 | 480.0000000000073 | 7600.500000000007 | 7120.5 | 10.1 | 85.89518526320718 | 7597.5 | 0 | 63.000000000007276 | 60 |  | 82.41319444444444 | 7120.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
29 | 0 | 725 | 725 | 0 | 0 | 3 | 725 | 50 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.75 | 8600.000000000007 | 41.681 | 3429.2699999999936 | 1080.0000000000073 | 8330.000000000007 | 7250 | 10 | 85.84093567251462 | 8205 | 0 | 125.00000000000728 | 0 |  | 83.91203703703704 | 7250 | 2016 | 7 | 2016_07_Asomata_english.xlsx
30 | 0 | 740 | 740 | 0 | 0 | 5 | 740 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 83.95 | 6680.000000000014 | 42.102 | 3921.84 | -1919.9999999999936 | 5517.000000000007 | 7437 | 10.05 | 87.04273625910967 | 5371.45 | 0 | 145.55000000000746 | 0 |  | 86.0763888888889 | 7437 | 2016 | 7 | 2016_07_Asomata_english.xlsx
31 | 555 | 115 | 670 | 0 | 0 | 4 | 670 | 100 | 12 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 84.1 | 7039.999999999993 | 42.102 | 3921.84 | 359.9999999999791 | 7227.499999999979 | 6867.5 | 10.25 | 85.0402641793639 | 7156.8 | 0 | 70.69999999997981 | 0 |  | 79.48495370370371 | 6867.5 | 2016 | 7 | 2016_07_Asomata_english.xlsx
1 | 685 | 25 | 710 | 0 | 0 | 3 | 710 | 50 | 13.30000000000291 | 0.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.1 | 7039.999999999993 | 41.788 | 3554.4599999999914 | 0 | 6958 | 6958 | 9.8 | 88.94517426923264 | 6855.2 | 0 | 102.80000000000109 | 0 |  | 80.53240740740742 | 6958 | 2016 | 8 | 2016_08_Asomata_english.xlsx
2 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 50 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.5 | 8000.000000000007 | 41.492 | 3208.14 | 960.0000000000146 | 7477.0000000000155 | 6517 | 9.8 | 88.1080432172869 | 7175.7 | 0 | 301.30000000001473 | 0 |  | 75.42824074074075 | 6517 | 2016 | 8 | 2016_08_Asomata_english.xlsx
3 | 0 | 685 | 685 | 0 | 0 | 4 | 685 | 50 | 0 | 14.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 3 | 84.5 | 8000.000000000007 | 41.778 | 3542.76 | 0 | 7055.5 | 7055.5 | 10.3 | 83.83095374071958 | 6847.4 | 0 | 208.10000000000127 | 0 |  | 81.66087962962963 | 7055.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
4 | 700 | 0 | 700 | 0 | 0 | 4 | 700 | 50 | 14.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.85 | 8839.999999999993 | 41.961 | 3756.8699999999935 | 839.9999999999854 | 7664.999999999985 | 6825 | 9.75 | 87.83651976184066 | 7422.8 | 0 | 242.19999999998527 | 0 |  | 78.99305555555556 | 6825 | 2016 | 8 | 2016_08_Asomata_english.xlsx
5 | 715 | 0 | 715 | 0 | 0 | 4 | 715 | 50 | 14.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.95 | 9080.000000000015 | 41.752 | 3512.34 | 240.00000000002183 | 7211.250000000022 | 6971.25 | 9.75 | 87.63201098474671 | 7117.5 | 0 | 93.75000000002183 | 0 |  | 80.68576388888889 | 6971.25 | 2016 | 8 | 2016_08_Asomata_english.xlsx
6 | 680 | 55 | 735 | 0 | 0 | 3 | 735 | 50 | 13.400000000001455 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 85.1 | 9439.999999999993 | 41.552 | 3278.34 | 359.9999999999782 | 7545.499999999978 | 7185.5 | 9.776190476190477 | 87.09307752900797 | 7185 | 0 | 360.4999999999782 | 0 |  | 83.16550925925925 | 7185.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
7 | 695 | 0 | 695 | 0 | 0 | 4 | 695 | 50 | 14.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.6 | 8239.999999999993 | 41.648 | 3390.66 | -1200 | 5680.5 | 6880.5 | 9.9 | 87.01332574572012 | 5632.5 | 0 | 48 | 0 |  | 79.63541666666667 | 6880.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
8 | 25 | 640 | 665 | 0 | 0 | 3 | 665 | 50 | 0.3000000000029104 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 83.8 | 6320 | 41.37 | 3065.4 | -1919.9999999999927 | 4796.500000000007 | 6716.5 | 10.1 | 86.9226396323843 | 4605 | 0 | 191.50000000000728 | 0 |  | 77.73726851851852 | 6716.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
9 | 690 | 0 | 690 | 0 | 0 | 4 | 690 | 50 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.15 | 7160.00000000002 | 41.951 | 3745.17 | 840.00000000002 | 7740.00000000002 | 6900 | 10 | 87.06287069988136 | 7584.7 | 0 | 155.30000000001928 | 0 |  | 79.86111111111111 | 6900 | 2016 | 8 | 2016_08_Asomata_english.xlsx
10 | 730 | 0 | 730 | 0 | 0 | 3 | 730 | 50 | 14.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.75 | 8600.000000000007 | 41.888 | 3671.46 | 1439.9999999999873 | 8593.999999999989 | 7154 | 9.8 | 87.59279150256593 | 8252.15 | 0 | 341.84999999998945 | 0 |  | 82.80092592592594 | 7154 | 2016 | 8 | 2016_08_Asomata_english.xlsx
11 | 720 | 220 | 940 | 0 | 0 | 4 | 940 | 85 | 16.200000000004366 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.25 | 7400.000000000007 | 41.801 | 3569.67 | -1200 | 8059 | 9259 | 9.85 | 88.17949719160184 | 7897.3 | 0 | 161.70000000000073 | 0 |  | 107.16435185185185 | 9259 | 2016 | 8 | 2016_08_Asomata_english.xlsx
12 | 725 | 0 | 725 | 0 | 0 | 4 | 725 | 50 | 14.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.4 | 7760.00000000002 | 41.7915 | 3558.5549999999957 | 360.00000000001273 | 7537.500000000013 | 7177.5 | 9.9 | 87.4237659615018 | 7350.48 | 0 | 187.02000000001317 | 0 |  | 83.07291666666667 | 7177.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
13 | 575 | 0 | 575 | 0 | 0 | 4 | 575 | 50 | 11.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.7 | 6080.000000000014 | 41.369 | 3064.23 | -1680.0000000000064 | 5464.287564766833 | 5807.5 | 10.1 | 87.13108720944037 | 5320.6 | 1336.7875647668393 | 143.68756476683302 | 0 |  | 67.21643518518519 | 5807.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
14 | 630 | 0 | 630 | 0 | 0 | 3 | 630 | 50 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.05 | 6920 | 41.67 | 3416.4 | 839.9999999999864 | 8632.227979274598 | 6300 | 10 | 87.26991676575506 | 8364.3 | 1492.2279792746115 | 267.92797927459833 | 0 |  | 72.91666666666667 | 6300 | 2016 | 8 | 2016_08_Asomata_english.xlsx
15 | 370 | 250 | 620 | 0 | 0 | 4 | 620 | 50 | 7.5 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.3 | 7520 | 41.6815 | 3429.854999999996 | 600 | 6707 | 6107 | 9.85 | 88.07526610745101 | 6420.6 | 0 | 286.40000000000055 | 0 |  | 70.68287037037037 | 6107 | 2016 | 8 | 2016_08_Asomata_english.xlsx
16 | 0 | 725 | 725 | 0 | 0 | 4 | 725 | 55 | 0 | 14.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.1 | 7039.999999999993 | 42 | 3802.5 | -480.0000000000073 | 6842.499999999993 | 7322.5 | 10.1 | 86.3032383998495 | 6793.25 | 0 | 49.249999999992724 | 0 |  | 84.7511574074074 | 7322.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
17 | 335 | 440 | 775 | 0 | 0 | 3 | 775 | 54 | 6.400000000001455 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.3 | 7520 | 41.688 | 3437.46 | 480.0000000000073 | 8307.500000000007 | 7827.5 | 10.1 | 85.89518526320718 | 8158.15 | 0 | 209.35000000000673 | 60 |  | 90.59606481481481 | 7827.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
18 | 565 | 0 | 565 | 0 | 0 | 4 | 565 | 50 | 11.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.75 | 8600.000000000007 | 41.3 | 2983.5 | 1080.0000000000073 | 6730.000000000007 | 5650 | 10 | 85.84093567251462 | 6421.9 | 0 | 308.10000000000764 | 0 |  | 65.39351851851852 | 5650 | 2016 | 8 | 2016_08_Asomata_english.xlsx
19 | 620 | 0 | 620 | 0 | 0 | 4 | 620 | 50 | 12.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.8 | 8720 | 41.351 | 3043.17 | 119.99999999999272 | 6319.999999999993 | 6200 | 10 | 85.74065420560747 | 6175.8 | 0 | 144.19999999999254 | 0 |  | 71.75925925925925 | 6200 | 2016 | 8 | 2016_08_Asomata_english.xlsx
20 | 10 | 580 | 590 | 0 | 0 | 4 | 590 | 50 | 0.25 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.7 | 8480.000000000015 | 41.449 | 3157.83 | -239.99999999998545 | 5660.000000000015 | 5900 | 10 | 85.94145199063232 | 5564.8 | 0 | 95.20000000001437 | 0 |  | 68.28703703703704 | 5900 | 2016 | 8 | 2016_08_Asomata_english.xlsx
21 | 515 | 60 | 575 | 0 | 0 | 4 | 575 | 90 | 11 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 83.7 | 6080.000000000014 | 41.848 | 3624.66 | -2400 | 6810.732984293192 | 5750 | 10 | 88.00239808153478 | 6697 | 3460.7329842931936 | 113.7329842931922 | 0 |  | 66.55092592592592 | 5750 | 2016 | 8 | 2016_08_Asomata_english.xlsx
22 | 600 | 0 | 600 | 0 | 0 | 4 | 600 | 50 | 12.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 2 | 0 | Αποκ. Βλ. κυκλ. Ρ.Σ. Μον. ΝοΙΙ | 22 | 83.65 | 5960.00000000002 | 41.65 | 3393 | -119.99999999999363 | 5880.000000000006 | 6000 | 10 | 88.1080432172869 | 5788.9 | 0 | 91.10000000000673 | 0 |  | 69.44444444444444 | 6000 | 2016 | 8 | 2016_08_Asomata_english.xlsx
23 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 50 | 12.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 83.8 | 6320 | 42.001 | 3803.6699999999937 | 359.99999999998 | 5973.49999999998 | 5613.5 | 10.3 | 85.23482138709527 | 5837.4 | 0 | 136.09999999998035 | 0 |  | 64.97106481481481 | 5613.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
24 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 45 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.5 | 8000.000000000007 | 40.1 | 1579.5 | 1680.0000000000073 | 8159.381443298977 | 2000 | 10 | 86.34588235294117 | 8095.86 | 4479.381443298969 | 63.52144329897692 | 0 |  | 23.14814814814815 | 2000 | 2016 | 8 | 2016_08_Asomata_english.xlsx
25 | 555 | 0 | 555 | 0 | 0 | 4 | 555 | 54 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.8 | 8720 | 41 | 2632.5 | 719.9999999999927 | 6186.749999999993 | 5466.75 | 9.85 | 87.04634944731724 | 5985 | 0 | 201.74999999999272 | 0 |  | 63.27256944444444 | 5466.75 | 2016 | 8 | 2016_08_Asomata_english.xlsx
26 | 0 | 545 | 545 | 0 | 0 | 3 | 545 | 50 | 0 | 12.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.7 | 8480.000000000015 | 41.75 | 3510 | -239.99999999998545 | 5369.574468085121 | 5450 | 10 | 85.94145199063232 | 5312.45 | 159.5744680851064 | 57.12446808512141 | 0 |  | 63.0787037037037 | 5450 | 2016 | 8 | 2016_08_Asomata_english.xlsx
27 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 50 | 0 | 10.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.55 | 8120 | 42 | 3802.5 | -360.00000000001455 | 4735.999999999985 | 5096 | 9.8 | 88.00450850140291 | 4492.25 | 0 | 243.74999999998545 | 0 |  | 58.98148148148148 | 5096 | 2016 | 8 | 2016_08_Asomata_english.xlsx
28 | 0 | 535 | 535 | 0 | 0 | 4 | 535 | 50 | 0 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.9 | 8960.00000000002 | 41.8 | 3568.5 | 840.00000000002 | 6190.00000000002 | 5350 | 10 | 85.54079254079252 | 6134.6 | 0 | 55.400000000019645 | 0 |  | 61.9212962962963 | 5350 | 2016 | 8 | 2016_08_Asomata_english.xlsx
29 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 50 | 0 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.75 | 8600.000000000007 | 41.758 | 3519.36 | -360.00000000001273 | 4790.999999999987 | 5151 | 10.1 | 84.9910254183313 | 4730.4 | 0 | 60.59999999998763 | 0 |  | 59.61805555555556 | 5151 | 2016 | 8 | 2016_08_Asomata_english.xlsx
30 | 0 | 430 | 430 | 0 | 0 | 3 | 430 | 45 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85 | 9200.000000000007 | 41.733 | 3490.1099999999915 | 600 | 4814 | 4214 | 9.8 | 87.08353108685334 | 4552.65 | 0 | 261.35 | 0 |  | 48.773148148148145 | 4214 | 2016 | 8 | 2016_08_Asomata_english.xlsx
31 | 0 | 445 | 445 | 0 | 0 | 4 | 445 | 45 | 0 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.85 | 8839.999999999993 | 41.615 | 3352.05 | -360.00000000001455 | 4134.499999999985 | 4494.5 | 10.1 | 84.79267996811352 | 4060.25 | 0 | 74.24999999998545 | 0 |  | 52.019675925925924 | 4494.5 | 2016 | 8 | 2016_08_Asomata_english.xlsx
1 | 385 | 0 | 385 | 0 | 0 | 4 | 385 | 45 | 7.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85 | 9200.000000000007 | 41.638 | 3378.96 | 360.00000000001455 | 4094.500000000014 | 3734.5 | 9.7 | 87.9812994485735 | 3669.3 | 0 | 425.20000000001437 | 0 |  | 43.223379629629626 | 3734.5 | 2016 | 9 | 2016_09_Asomata_english.xlsx
2 | 395 | 0 | 395 | 0 | 0 | 4 | 395 | 45 | 9.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.9 | 8960.00000000002 | 41.622 | 3360.24 | -239.99999999998727 | 3848.2500000000127 | 4088.25 | 10.35 | 82.64810873506525 | 3881.45 | 0 | 26.80000000001246 | 60 |  | 47.317708333333336 | 4088.25 | 2016 | 9 | 2016_09_Asomata_english.xlsx
3 | 420 | 0 | 420 | 0 | 0 | 4 | 420 | 45 | 9.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.5 | 8000.000000000007 | 42.049 | 3859.83 | -960.0000000000127 | 3386.9999999999873 | 4347 | 10.35 | 83.42597328786587 | 3321.5 | 0 | 65.49999999998727 | 0 |  | 50.3125 | 4347 | 2016 | 9 | 2016_09_Asomata_english.xlsx
4 | 185 | 140 | 325 | 0 | 0 | 4 | 325 | 80 | 4.700000000004366 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 83.7 | 6080.000000000014 | 41.872 | 3652.74 | -1919.9999999999936 | 4764.343434343441 | 3250 | 10 | 88.00239808153478 | 4805 | 3434.3434343434346 | 19.343434343441004 | 60 |  | 37.61574074074074 | 3250 | 2016 | 9 | 2016_09_Asomata_english.xlsx
5 | 350 | 0 | 350 | 0 | 0 | 3 | 350 | 45 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.25 | 7400.000000000007 | 41.802 | 3570.84 | 1319.9999999999936 | 4819.999999999994 | 3500 | 10 | 86.85680473372781 | 4608 | 0 | 211.99999999999363 | 0 |  | 40.50925925925926 | 3500 | 2016 | 9 | 2016_09_Asomata_english.xlsx
6 | 0 | 320 | 320 | 0 | 0 | 3 | 320 | 54 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.3 | 7520 | 41.192 | 2857.14 | 119.99999999999272 | 3351.9999999999927 | 3232 | 10.1 | 85.89518526320718 | 3261.6 | 0 | 150.39999999999281 | 60 |  | 37.407407407407405 | 3232 | 2016 | 9 | 2016_09_Asomata_english.xlsx
7 | 310 | 15 | 325 | 0 | 0 | 3 | 325 | 40 | 7.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.5 | 8000.000000000007 | 41.78 | 3545.1 | 480.0000000000073 | 3731.5000000000073 | 3251.5 | 10.004615384615384 | 86.30604879196028 | 3445.6 | 0 | 345.90000000000737 | 60 |  | 37.633101851851855 | 3251.5 | 2016 | 9 | 2016_09_Asomata_english.xlsx
8 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 45 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.65 | 8360.00000000002 | 40.701 | 2282.67 | 360.00000000001273 | 1678.7500000000127 | 1318.75 | 10.55 | 81.5565914558597 | 1540.3 | 0 | 138.45000000001278 | 0 |  | 15.263310185185185 | 1318.75 | 2016 | 9 | 2016_09_Asomata_english.xlsx
9 | 220 | 0 | 220 | 0 | 0 | 3 | 220 | 39 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.55 | 8120 | 41.081 | 2727.27 | -240.00000000002 | 1959.99999999998 | 2200 | 10 | 86.24441833137486 | 1746.4 | 0 | 213.5999999999799 | 0 |  | 25.462962962962962 | 2200 | 2016 | 9 | 2016_09_Asomata_english.xlsx
10 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 40 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.8 | 8720 | 40.71 | 2293.2 | 600 | 1433 | 833 | 9.8 | 87.49046347510966 | 1311.2 | 0 | 121.8 | 0 |  | 9.641203703703704 | 833 | 2016 | 9 | 2016_09_Asomata_english.xlsx
11 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 35 | 2.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.3 | 7520 | 40.197 | 1692.99 | -1200 | 2730.2127659574467 | 1010 | 10.1 | 85.89518526320718 | 2671.8 | 2920.2127659574467 | 78.41276595744694 | 20 |  | 11.689814814814815 | 1010 | 2016 | 9 | 2016_09_Asomata_english.xlsx
12 | 105 | 0 | 105 | 0 | 0 | 4 | 105 | 40 | 2.6499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.6 | 8239.999999999993 | 40.2 | 1696.5000000000055 | 719.9999999999927 | 1748.9999999999927 | 1029 | 9.8 | 87.90121682475808 | 1494.8 | 0 | 254.19999999999254 | 0 |  | 11.909722222222221 | 1029 | 2016 | 9 | 2016_09_Asomata_english.xlsx
13 | 275 | 0 | 275 | 0 | 0 | 4 | 275 | 40 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.45 | 7880.000000000014 | 41.399 | 3099.33 | -359.9999999999791 | 2348.750000000021 | 2708.75 | 9.85 | 87.76404608586991 | 2263.8 | 0 | 84.95000000002074 | 0 |  | 31.35127314814815 | 2708.75 | 2016 | 9 | 2016_09_Asomata_english.xlsx
14 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 40 | 5.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.55 | 8120 | 41.58 | 3311.1 | 239.99999999998636 | 2259.9999999999864 | 2020 | 10.1 | 85.39051319938106 | 2234.8 | 0 | 25.199999999986176 | 0 |  | 23.37962962962963 | 2020 | 2016 | 9 | 2016_09_Asomata_english.xlsx
15 | 230 | 0 | 230 | 0 | 0 | 3 | 230 | 45 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.55 | 8120 | 41.769 | 3532.23 | 0 | 2323 | 2323 | 10.1 | 85.39051319938106 | 2248.4 | 0 | 134.6 | 60 |  | 26.886574074074073 | 2323 | 2016 | 9 | 2016_09_Asomata_english.xlsx
16 | 170 | 0 | 170 | 0 | 0 | 3 | 170 | 40 | 4.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 84.7 | 8480.000000000015 | 40.552 | 2108.34 | 360.00000000001455 | 2034.5000000000146 | 1674.5 | 9.85 | 87.25020506663179 | 1897.5 | 0 | 137.00000000001455 | 0 |  | 19.380787037037038 | 1674.5 | 2016 | 9 | 2016_09_Asomata_english.xlsx
17 | 120 | 0 | 120 | 0 | 0 | 4 | 120 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.85 | 8839.999999999993 | 40.942 | 2564.64 | 359.9999999999782 | 1529.9999999999782 | 1170 | 9.75 | 87.83651976184066 | 1318.65 | 0 | 211.34999999997808 | 0 |  | 13.541666666666666 | 1170 | 2016 | 9 | 2016_09_Asomata_english.xlsx
18 | 130 | 0 | 130 | 0 | 0 | 4 | 130 | 45 | 3.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.9 | 8960.00000000002 | 41.178 | 2840.7599999999916 | 120.00000000002728 | 1394.0000000000273 | 1274 | 9.8 | 87.2865230008087 | 1244.15 | 0 | 149.8500000000272 | 0 |  | 14.74537037037037 | 1274 | 2016 | 9 | 2016_09_Asomata_english.xlsx
19 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 55 | 3.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85 | 9200.000000000007 | 40.752 | 2342.34 | 239.99999999998727 | 1743.4999999999873 | 1503.5 | 9.7 | 87.9812994485735 | 1470 | 0 | 273.49999999998727 | 0 |  | 17.40162037037037 | 1503.5 | 2016 | 9 | 2016_09_Asomata_english.xlsx
20 | 275 | 0 | 275 | 0 | 0 | 4 | 275 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.5 | 8000.000000000007 | 41.399 | 3099.33 | -1200 | 1577.5 | 2777.5 | 10.1 | 85.49097262667443 | 1494.8 | 0 | 142.7 | 60 |  | 32.14699074074074 | 2777.5 | 2016 | 9 | 2016_09_Asomata_english.xlsx
21 | 170 | 0 | 170 | 0 | 0 | 4 | 170 | 40 | 3.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.5 | 8000.000000000007 | 41.05 | 2691 | 0 | 1683 | 1683 | 9.9 | 87.21806298276887 | 1583.6 | 0 | 99.39999999999986 | 0 |  | 19.479166666666668 | 1683 | 2016 | 9 | 2016_09_Asomata_english.xlsx
22 | 185 | 0 | 185 | 0 | 0 | 5 | 185 | 40 | 4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.5 | 8000.000000000007 | 41.352 | 3044.34 | 0 | 1850 | 1850 | 10 | 86.34588235294117 | 1656 | 0 | 194 | 0 |  | 21.412037037037038 | 1850 | 2016 | 9 | 2016_09_Asomata_english.xlsx
23 | 170 | 75 | 245 | 0 | 0 | 4 | 245 | 80 | 4.30000000000291 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.55 | 8120 | 41.801 | 3569.67 | 119.99999999999272 | 2594.4999999999927 | 2474.5 | 10.1 | 85.39051319938106 | 2649.9 | 0 | 44.59999999999263 | 100 |  | 28.640046296296298 | 2474.5 | 2016 | 9 | 2016_09_Asomata_english.xlsx
24 | 0 | 180 | 180 | 0 | 0 | 4 | 180 | 35 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.75 | 8600.000000000007 | 41.068 | 2712.06 | 480.0000000000073 | 2298.0000000000073 | 1818 | 10.1 | 84.9910254183313 | 2087.4 | 0 | 210.60000000000719 | 0 |  | 21.041666666666668 | 1818 | 2016 | 9 | 2016_09_Asomata_english.xlsx
25 | 80 | 185 | 265 | 0 | 0 | 4 | 265 | 70 | 2 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.45 | 7880.000000000014 | 41.6515 | 3394.754999999996 | -719.9999999999936 | 1930.0000000000064 | 2650 | 10 | 86.44758539458186 | 1854.2 | 0 | 75.80000000000655 | 0 |  | 30.671296296296298 | 2650 | 2016 | 9 | 2016_09_Asomata_english.xlsx
26 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 45 | 0 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.45 | 7880.000000000014 | 41.115 | 2767.05 | 0 | 1600 | 1600 | 10 | 86.44758539458186 | 1337.7 | 0 | 262.3 | 0 |  | 18.51851851851852 | 1600 | 2016 | 9 | 2016_09_Asomata_english.xlsx
27 | 175 | 0 | 175 | 0 | 0 | 4 | 175 | 40 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.45 | 7880.000000000014 | 40.403 | 1934.01 | 0 | 1750 | 1750 | 10 | 86.44758539458186 | 1653.75 | 0 | 96.25 | 0 |  | 20.25462962962963 | 1750 | 2016 | 9 | 2016_09_Asomata_english.xlsx
28 | 180 | 0 | 180 | 0 | 0 | 2 | 180 | 35 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.35 | 7639.999999999993 | 40.601 | 2165.67 | -240.00000000002092 | 1577.999999999979 | 1818 | 10.1 | 85.79377418261309 | 1503.8 | 0 | 74.19999999997913 | 0 |  | 21.041666666666668 | 1818 | 2016 | 9 | 2016_09_Asomata_english.xlsx
29 | 155 | 100 | 255 | 0 | 0 | 2 | 255 | 70 | 3.7000000000043656 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.3 | 7520 | 41.351 | 3043.17 | -119.99999999999272 | 2404.5000000000073 | 2524.5 | 9.9 | 87.63044153115075 | 2355 | 0 | 49.500000000007276 | 0 |  | 29.21875 | 2524.5 | 2016 | 9 | 2016_09_Asomata_english.xlsx
30 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.2 | 7280.000000000014 | 41 | 2632.5 | -239.99999999998636 | 1730.0000000000136 | 1970 | 9.85 | 88.28397526884307 | 1507.5 | 0 | 222.50000000001364 | 0 |  | 22.800925925925927 | 1970 | 2016 | 9 | 2016_09_Asomata_english.xlsx
1 | 60 | 165 | 225 | 0 | 0 | 4 | 225 | 75 | 1.0999999999985448 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.35 | 7639.999999999993 | 41.642 | 3383.6400000000085 | 359.9999999999791 | 2632.499999999979 | 2272.5 | 10.1 | 85.79377418261309 | 2612.2 | 0 | 80.29999999997881 | 60 |  | 26.302083333333332 | 2272.5 | 2016 | 10 | 2016_10_Asomata_english.xlsx
2 | 240 | 0 | 240 | 0 | 0 | 4 | 240 | 50 | 5.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.4 | 7760.00000000002 | 41.748 | 3507.66 | 120.00000000002728 | 2544.0000000000273 | 2424 | 10.1 | 85.69260227909582 | 2448 | 0 | 96.00000000002728 | 0 |  | 28.055555555555557 | 2424 | 2016 | 10 | 2016_10_Asomata_english.xlsx
3 | 370 | 150 | 520 | 0 | 0 | 3 | 520 | 90 | 7.75 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.6 | 8239.999999999993 | 41.821 | 3593.0699999999933 | 479.9999999999727 | 5627.999999999973 | 5148 | 9.9 | 87.01332574572012 | 5527.5 | 0 | 100.49999999997272 | 0 |  | 59.583333333333336 | 5148 | 2016 | 10 | 2016_10_Asomata_english.xlsx
4 | 0 | 265 | 265 | 0 | 0 | 3 | 265 | 55 | 0 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.6 | 8239.999999999993 | 40.95 | 2574 | 0 | 2597 | 2597 | 9.8 | 87.90121682475808 | 2453.75 | 0 | 143.25 | 0 |  | 30.05787037037037 | 2597 | 2016 | 10 | 2016_10_Asomata_english.xlsx
5 | 230 | 0 | 230 | 0 | 0 | 4 | 230 | 35 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.45 | 7880.000000000014 | 41.77 | 3533.4 | -359.9999999999791 | 1940.000000000021 | 2300 | 10 | 86.44758539458186 | 1773.9 | 0 | 166.10000000002105 | 0 |  | 26.62037037037037 | 2300 | 2016 | 10 | 2016_10_Asomata_english.xlsx
6 | 250 | 40 | 290 | 0 | 0 | 4 | 290 | 70 | 5.899999999994179 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 84.65 | 8360.00000000002 | 41.65 | 3393 | 480.00000000000637 | 3409.0000000000064 | 2929 | 10.1 | 85.19030097617029 | 3255.8 | 0 | 153.20000000000618 | 0 |  | 33.90046296296296 | 2929 | 2016 | 10 | 2016_10_Asomata_english.xlsx
7 | 245 | 55 | 300 | 0 | 0 | 3 | 300 | 89 | 6 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.6 | 8239.999999999993 | 41.215 | 2884.05 | -120.00000000002728 | 2819.9999999999727 | 2940 | 9.8 | 87.90121682475808 | 2660.7 | 0 | 159.2999999999729 | 0 |  | 34.02777777777778 | 2940 | 2016 | 10 | 2016_10_Asomata_english.xlsx
8 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 35 | 5.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.5 | 8000.000000000007 | 41.717 | 3471.39 | -239.99999999998545 | 1661.2500000000146 | 1901.25 | 9.75 | 88.55987933634992 | 1650 | 0 | 11.250000000014552 | 0 |  | 22.005208333333332 | 1901.25 | 2016 | 10 | 2016_10_Asomata_english.xlsx
9 | 190 | 55 | 245 | 0 | 0 | 4 | 245 | 108 | 4.19999999999709 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.8 | 8720 | 41.638 | 3378.96 | 719.9999999999927 | 3133.2499999999927 | 2413.25 | 9.85 | 87.04634944731724 | 2890.8 | 0 | 242.44999999999254 | 0 |  | 27.93113425925926 | 2413.25 | 2016 | 10 | 2016_10_Asomata_english.xlsx
10 | 300 | 0 | 300 | 0 | 0 | 3 | 300 | 54 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.5 | 8000.000000000007 | 41.231 | 2902.77 | -719.9999999999927 | 2280.0000000000073 | 3000 | 10 | 86.34588235294117 | 2117 | 0 | 223.00000000000728 | 60 |  | 34.72222222222222 | 3000 | 2016 | 10 | 2016_10_Asomata_english.xlsx
11 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 50 | 2.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.65 | 8360.00000000002 | 40.917 | 2535.39 | 360.00000000001273 | 1510.0000000000127 | 1150 | 10 | 86.04220398593199 | 1452.7 | 0 | 57.30000000001269 | 0 |  | 13.310185185185185 | 1150 | 2016 | 10 | 2016_10_Asomata_english.xlsx
12 | 190 | 0 | 190 | 0 | 0 | 4 | 190 | 50 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.5 | 8000.000000000007 | 41.403 | 3104.01 | -360.00000000001273 | 1492.4999999999873 | 1852.5 | 9.75 | 88.55987933634992 | 1333.55 | 0 | 158.9499999999873 | 0 |  | 21.44097222222222 | 1852.5 | 2016 | 10 | 2016_10_Asomata_english.xlsx
13 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 50 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.65 | 8360.00000000002 | 41.172 | 2833.74 | 360.00000000001273 | 2310.0000000000127 | 1950 | 10 | 86.04220398593199 | 2044 | 0 | 266.00000000001273 | 0 |  | 22.569444444444443 | 1950 | 2016 | 10 | 2016_10_Asomata_english.xlsx
14 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 50 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.55 | 8120 | 41.1 | 2749.5 | -240.00000000002 | 1656.24999999998 | 1896.25 | 10.25 | 84.14089593304864 | 1708.2 | 0 | 8.049999999979946 | 60 |  | 21.947337962962962 | 1896.25 | 2016 | 10 | 2016_10_Asomata_english.xlsx
15 | 140 | 80 | 220 | 0 | 0 | 4 | 220 | 80 | 3.6999999999970896 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84.6 | 8239.999999999993 | 41.217 | 2886.39 | 119.99999999999272 | 2275.9999999999927 | 2156 | 9.8 | 87.90121682475808 | 2181.95 | 0 | 94.0499999999929 | 0 |  | 24.953703703703702 | 2156 | 2016 | 10 | 2016_10_Asomata_english.xlsx
16 | 150 | 0 | 150 | 0 | 0 | 5 | 150 | 54 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.6 | 8239.999999999993 | 41.111 | 2762.3699999999935 | 0 | 1455 | 1455 | 9.7 | 88.80741493635354 | 1231.65 | 0 | 223.35 | 0 |  | 16.84027777777778 | 1455 | 2016 | 10 | 2016_10_Asomata_english.xlsx
17 | 225 | 0 | 225 | 0 | 0 | 4 | 225 | 54 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.65 | 8360.00000000002 | 41.503 | 3221.01 | 120.00000000002728 | 2392.5000000000273 | 2272.5 | 10.1 | 85.19030097617029 | 2343.3 | 0 | 109.20000000002756 | 60 |  | 26.302083333333332 | 2272.5 | 2016 | 10 | 2016_10_Asomata_english.xlsx
18 | 0 | 245 | 245 | 0 | 0 | 4 | 245 | 54 | 0 | 5.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.65 | 8360.00000000002 | 41.652 | 3395.34 | 0 | 2450 | 2450 | 10 | 86.04220398593199 | 2233.8 | 0 | 216.2 | 0 |  | 28.35648148148148 | 2450 | 2016 | 10 | 2016_10_Asomata_english.xlsx
19 | 230 | 115 | 345 | 0 | 0 | 5 | 345 | 108 | 4.700000000004366 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.55 | 8120 | 41.75 | 3510 | -240.00000000002 | 3175.49999999998 | 3415.5 | 9.9 | 87.11557407209581 | 2987.45 | 0 | 188.04999999997972 | 0 |  | 39.53125 | 3415.5 | 2016 | 10 | 2016_10_Asomata_english.xlsx
20 | 680 | 230 | 910 | 0 | 0 | 4 | 910 | 110 | 13.299999999995634 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.65 | 8360.00000000002 | 41.85 | 3627 | 240.00000000002 | 9067.00000000002 | 8827 | 9.7 | 88.70330307828041 | 9057.6 | 0 | 9.400000000019645 | 0 |  | 102.16435185185185 | 8827 | 2016 | 10 | 2016_10_Asomata_english.xlsx
21 | 605 | 310 | 915 | 0 | 0 | 5 | 915 | 110 | 13.700000000004366 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 84.65 | 8360.00000000002 | 41.63 | 3369.6 | 0 | 9150 | 9150 | 10 | 86.04220398593199 | 9003.75 | 0 | 146.25 | 0 |  | 105.90277777777777 | 9150 | 2016 | 10 | 2016_10_Asomata_english.xlsx
22 | 0 | 555 | 555 | 0 | 0 | 5 | 555 | 50 | 0 | 11.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.7 | 8480.000000000015 | 41.646 | 3388.32 | 119.99999999999454 | 5586.7499999999945 | 5466.75 | 9.85 | 87.25020506663179 | 5365 | 0 | 221.74999999999454 | 0 |  | 63.27256944444444 | 5466.75 | 2016 | 10 | 2016_10_Asomata_english.xlsx
23 | 135 | 170 | 305 | 0 | 0 | 4 | 305 | 107 | 3.1999999999970896 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480.000000000015 | 41.82 | 3591.9 | 0 | 3080.5 | 3080.5 | 10.1 | 85.09054652537853 | 2876.2 | 0 | 204.3 | 0 |  | 35.65393518518518 | 3080.5 | 2016 | 10 | 2016_10_Asomata_english.xlsx
24 | 0 | 505 | 505 | 0 | 0 | 4 | 505 | 50 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.3 | 7520 | 41.302 | 2985.84 | -960.0000000000146 | 4089.9999999999854 | 5050 | 10 | 86.75413711583924 | 3991.05 | 0 | 98.94999999998572 | 0 |  | 58.449074074074076 | 5050 | 2016 | 10 | 2016_10_Asomata_english.xlsx
25 | 420 | 0 | 420 | 0 | 0 | 3 | 420 | 50 | 9.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.3 | 7520 | 41.301 | 2984.67 | 0 | 4158 | 4158 | 9.9 | 87.63044153115075 | 3807.3 | 0 | 350.7 | 0 |  | 48.125 | 4158 | 2016 | 10 | 2016_10_Asomata_english.xlsx
26 | 640 | 0 | 640 | 0 | 0 | 4 | 640 | 54 | 14.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.5 | 8000.000000000007 | 41.398 | 3098.16 | 480.0000000000073 | 6944.000000000007 | 6464 | 10.1 | 85.49097262667443 | 6852.4 | 0 | 91.60000000000764 | 0 |  | 74.81481481481481 | 6464 | 2016 | 10 | 2016_10_Asomata_english.xlsx
27 | 460 | 65 | 525 | 0 | 0 | 4 | 525 | 90 | 10.44999999999709 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.1 | 7039.999999999993 | 41.4 | 3100.5 | -960.0000000000146 | 4184.999999999985 | 5145 | 9.8 | 88.94517426923264 | 4121.8 | 0 | 63.199999999985266 | 0 |  | 59.548611111111114 | 5145 | 2016 | 10 | 2016_10_Asomata_english.xlsx
28 | 430 | 0 | 430 | 0 | 0 | 5 | 430 | 50 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.2 | 7280.000000000014 | 41.656 | 3400.0199999999936 | 240.00000000002092 | 4475.500000000021 | 4235.5 | 9.85 | 88.28397526884307 | 4270.25 | 0 | 205.25000000002092 | 0 |  | 49.02199074074074 | 4235.5 | 2016 | 10 | 2016_10_Asomata_english.xlsx
29 | 150 | 540 | 690 | 0 | 0 | 5 | 690 | 108 | 2.8000000000029104 | 11.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 29 | 84.55 | 8120 | 41.658 | 3402.36 | 839.9999999999864 | 7670.999999999986 | 6831 | 9.9 | 87.11557407209581 | 7519 | 0 | 151.99999999998636 | 0 |  | 79.0625 | 6831 | 2016 | 10 | 2016_10_Asomata_english.xlsx
30 | 275 | 205 | 480 | 0 | 0 | 5 | 480 | 110 | 5.099999999998545 | 3.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.55 | 8120 | 41.652 | 3395.34 | 0 | 4728 | 4728 | 9.85 | 87.55778510799479 | 4480 | 0 | 248 | 0 |  | 54.72222222222222 | 4728 | 2016 | 10 | 2016_10_Asomata_english.xlsx
31 | 505 | 245 | 750 | 0 | 0 | 4 | 750 | 110 | 11.599999999998545 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 84.15 | 7160.00000000002 | 41.799 | 3567.33 | -959.99999999998 | 6652.50000000002 | 7612.5 | 10.15 | 85.77622729052351 | 6672.2 | 0 | 40.30000000002019 | 60 |  | 88.10763888888889 | 7612.5 | 2016 | 10 | 2016_10_Asomata_english.xlsx
1 | 395 | 250 | 645 | 0 | 0 | 4 | 645 | 108 | 9.5 | 5.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.6 | 8239.999999999993 | 41.68 | 3428.1 | 1079.9999999999727 | 7465.499999999973 | 6385.5 | 9.9 | 87.01332574572012 | 7416.15 | 0 | 49.34999999997308 | 0 |  | 73.90625 | 6385.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
2 | 0 | 570 | 570 | 0 | 0 | 5 | 570 | 55 | 0 | 12.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.5 | 8000.000000000007 | 41.349 | 3040.83 | -239.99999999998545 | 5517.000000000015 | 5757 | 10.1 | 85.49097262667443 | 5423.9 | 0 | 153.10000000001492 | 60 |  | 66.63194444444444 | 5757 | 2016 | 11 | 2016_11_Asomata_english.xlsx
3 | 620 | 285 | 905 | 0 | 0 | 5 | 905 | 100 | 13.80000000000291 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.1 | 7039.999999999993 | 41.65 | 3393 | -960.0000000000146 | 8180.499999999985 | 9140.5 | 10.1 | 86.3032383998495 | 8128.8 | 0 | 111.69999999998527 | 60 |  | 105.79282407407408 | 9140.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
4 | 425 | 305 | 730 | 0 | 0 | 4 | 730 | 80 | 9.69999999999709 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84.5 | 8000.000000000007 | 42 | 3802.5 | 960.0000000000146 | 8187.000000000015 | 7227 | 9.9 | 87.21806298276887 | 8028 | 0 | 159.00000000001455 | 0 |  | 83.64583333333333 | 7227 | 2016 | 11 | 2016_11_Asomata_english.xlsx
5 | 275 | 170 | 445 | 0 | 0 | 4 | 445 | 40 | 7.80000000000291 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.7 | 8480.000000000015 | 40.7 | 2281.5 | 480.0000000000073 | 4885.500000000007 | 4405.5 | 9.9 | 86.80954746528516 | 4845.6 | 0 | 39.90000000000691 | 0 |  | 50.989583333333336 | 4405.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
6 | 290 | 0 | 290 | 0 | 0 | 4 | 290 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.65 | 8360.00000000002 | 41.007 | 2640.69 | -119.99999999999454 | 3378.659574468091 | 2871 | 9.9 | 86.91131715750706 | 3255.8 | 627.6595744680851 | 122.85957446809061 | 0 |  | 33.229166666666664 | 2871 | 2016 | 11 | 2016_11_Asomata_english.xlsx
7 | 455 | 0 | 455 | 0 | 0 | 6 | 455 | 40 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.1 | 9439.999999999993 | 41.081 | 2727.27 | 1079.9999999999727 | 5538.999999999973 | 4459 | 9.8 | 86.88148113073535 | 5415 | 0 | 123.99999999997272 | 0 |  | 51.6087962962963 | 4459 | 2016 | 11 | 2016_11_Asomata_english.xlsx
8 | 485 | 0 | 485 | 0 | 0 | 5 | 485 | 55 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.8 | 8720 | 41.6 | 3334.5 | -719.9999999999927 | 8395.32978723405 | 4801.5 | 9.9 | 86.60672141980554 | 8305.5 | 4313.829787234043 | 89.82978723404995 | 0 |  | 55.572916666666664 | 4801.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
9 | 0 | 515 | 515 | 0 | 0 | 4 | 515 | 45 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.85 | 8839.999999999993 | 41.3 | 2983.5 | 119.99999999999272 | 6241.468085106376 | 5047 | 9.8 | 87.38837425285168 | 6232.5 | 1074.468085106383 | 8.968085106375838 | 0 |  | 58.414351851851855 | 5047 | 2016 | 11 | 2016_11_Asomata_english.xlsx
10 | 475 | 0 | 475 | 0 | 0 | 4 | 475 | 45 | 11.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 41.5 | 3217.5 | -1319.9999999999927 | 3382.5000000000073 | 4702.5 | 9.9 | 87.63044153115075 | 3344.8 | 0 | 37.700000000007094 | 0 |  | 54.427083333333336 | 4702.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
11 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 45 | 9.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.3 | 7520 | 41.297 | 2979.99 | 0 | 4150 | 4150 | 10 | 86.75413711583924 | 3929.4 | 0 | 220.6 | 0 |  | 48.032407407407405 | 4150 | 2016 | 11 | 2016_11_Asomata_english.xlsx
12 | 270 | 0 | 270 | 0 | 0 | 5 | 270 | 40 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.85 | 8839.999999999993 | 40.15 | 1638 | 1319.9999999999927 | 4019.9999999999927 | 2700 | 10 | 85.64060676779464 | 3774 | 0 | 245.99999999999272 | 0 |  | 31.25 | 2700 | 2016 | 11 | 2016_11_Asomata_english.xlsx
13 | 230 | 0 | 230 | 0 | 0 | 5 | 230 | 45 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.4 | 7760.00000000002 | 41.2 | 2866.5 | -1079.9999999999727 | 4696.125000000027 | 2323 | 10.1 | 85.69260227909582 | 4662 | 3453.125 | 34.125000000027285 | 0 |  | 26.886574074074073 | 2323 | 2016 | 11 | 2016_11_Asomata_english.xlsx
14 | 440 | 0 | 440 | 0 | 0 | 5 | 440 | 45 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.05 | 6920 | 41.589 | 3321.63 | -840.00000000002 | 3603.99999999998 | 4444 | 10.1 | 86.4058581839159 | 3336.1 | 0 | 327.8999999999801 | 60 |  | 51.43518518518518 | 4444 | 2016 | 11 | 2016_11_Asomata_english.xlsx
15 | 190 | 250 | 440 | 0 | 0 | 4 | 440 | 85 | 4.400000000001455 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 15 | 84.25 | 7400.000000000007 | 41.201 | 2867.67 | 480.0000000000073 | 4880.000000000007 | 4400 | 10 | 86.85680473372781 | 4837.5 | 0 | 42.500000000007276 | 0 |  | 50.925925925925924 | 4400 | 2016 | 11 | 2016_11_Asomata_english.xlsx
16 | 160 | 275 | 435 | 0 | 0 | 5 | 435 | 45 | 3.8999999999941792 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 84.5 | 8000.000000000007 | 41.563 | 3291.21 | 600 | 4884.75 | 4284.75 | 9.85 | 87.66079426694536 | 4758.2 | 0 | 126.54999999999927 | 0 |  | 49.592013888888886 | 4284.75 | 2016 | 11 | 2016_11_Asomata_english.xlsx
17 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 54 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.15 | 7160.00000000002 | 41.36 | 3053.7 | -839.9999999999873 | 3705.0000000000127 | 4545 | 10.1 | 86.20086207909047 | 3592.8 | 0 | 112.20000000001255 | 0 |  | 52.604166666666664 | 4545 | 2016 | 11 | 2016_11_Asomata_english.xlsx
18 | 400 | 0 | 400 | 0 | 0 | 4 | 400 | 45 | 9.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.5 | 8000.000000000007 | 41.602 | 3336.84 | 839.9999999999873 | 4839.999999999987 | 4000 | 10 | 86.34588235294117 | 4845 | 0 | 54.99999999998727 | 60 |  | 46.2962962962963 | 4000 | 2016 | 11 | 2016_11_Asomata_english.xlsx
19 | 570 | 250 | 820 | 0 | 0 | 4 | 820 | 110 | 12.700000000004366 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.8 | 8720 | 41.779 | 3543.9300000000067 | 719.9999999999927 | 8919.999999999993 | 8200 | 10 | 85.74065420560747 | 8842.5 | 0 | 77.49999999999272 | 0 |  | 94.9074074074074 | 8200 | 2016 | 11 | 2016_11_Asomata_english.xlsx
20 | 440 | 0 | 440 | 0 | 0 | 4 | 440 | 45 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.5 | 8000.000000000007 | 41.219 | 2888.7300000000064 | -719.9999999999927 | 3724.0000000000073 | 4444 | 10.1 | 85.49097262667443 | 3598.9 | 0 | 125.10000000000719 | 0 |  | 51.43518518518518 | 4444 | 2016 | 11 | 2016_11_Asomata_english.xlsx
21 | 190 | 465 | 655 | 0 | 0 | 5 | 655 | 70 | 4.899999999994179 | 10.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 84.4 | 7760.00000000002 | 41.15 | 2808 | -239.99999999998727 | 6244.500000000013 | 6484.5 | 9.9 | 87.4237659615018 | 6234.2 | 0 | 10.300000000012915 | 0 |  | 75.05208333333333 | 6484.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
22 | 705 | 220 | 925 | 0 | 0 | 4 | 925 | 70 | 15.85000000000582 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.55 | 8120 | 41.62 | 3357.9 | 359.99999999998 | 9702.49999999998 | 9342.5 | 10.1 | 85.39051319938106 | 9614.1 | 0 | 88.39999999998145 | 0 |  | 108.13078703703704 | 9342.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
23 | 155 | 770 | 925 | 0 | 0 | 5 | 925 | 95 | 4.149999999994179 | 16.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.45 | 7880.000000000014 | 41.78 | 3545.1 | -239.99999999998636 | 8825.000000000015 | 9065 | 9.8 | 88.21182183120597 | 8752.7 | 0 | 132.30000000001382 | 60 |  | 104.91898148148148 | 9065 | 2016 | 11 | 2016_11_Asomata_english.xlsx
24 | 640 | 140 | 780 | 0 | 0 | 5 | 780 | 70 | 14.10000000000582 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.4 | 7760.00000000002 | 41.316 | 3002.22 | -119.99999999999363 | 7563.000000000006 | 7683 | 9.85 | 87.86754142323531 | 7554.4 | 0 | 8.60000000000673 | 0 |  | 88.92361111111111 | 7683 | 2016 | 11 | 2016_11_Asomata_english.xlsx
25 | 790 | 190 | 980 | 0 | 0 | 4 | 980 | 110 | 16.19999999999709 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 83.95 | 6680.000000000014 | 41.8 | 3568.5 | -1080.0000000000064 | 8621.999999999993 | 9702 | 9.9 | 88.36156559636892 | 8424.5 | 0 | 197.49999999999272 | 0 |  | 112.29166666666667 | 9702 | 2016 | 11 | 2016_11_Asomata_english.xlsx
26 | 765 | 0 | 765 | 0 | 0 | 5 | 765 | 45 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 83.8 | 6320 | 41.372 | 3067.74 | -360.00000000001364 | 7366.499999999986 | 7726.5 | 10.1 | 86.9226396323843 | 7402.2 | 0 | 24.29999999998654 | 60 |  | 89.42708333333333 | 7726.5 | 2016 | 11 | 2016_11_Asomata_english.xlsx
27 | 390 | 390 | 780 | 0 | 0 | 4 | 780 | 90 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 83.45 | 5480.000000000014 | 41.03 | 2667.6 | -839.9999999999864 | 7155.000000000014 | 7995 | 10.25 | 86.37382682632617 | 7182 | 0 | 33.00000000001364 | 60 |  | 92.53472222222223 | 7995 | 2016 | 11 | 2016_11_Asomata_english.xlsx
28 | 730 | 250 | 980 | 0 | 0 | 4 | 980 | 90 | 16 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 83.45 | 5480.000000000014 | 41.802 | 3570.84 | 0 | 9898 | 9898 | 10.1 | 87.65660643265774 | 9778.15 | 0 | 119.85 | 0 |  | 114.56018518518519 | 9898 | 2016 | 11 | 2016_11_Asomata_english.xlsx
29 | 785 | 120 | 905 | 0 | 0 | 4 | 905 | 100 | 17 | 3.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 83.5 | 5600.000000000007 | 41.7 | 3451.5 | 119.99999999999363 | 9848.749999999993 | 9728.75 | 10.75 | 82.25721490613617 | 9841.8 | 0 | 36.94999999999345 | 30 |  | 112.60127314814815 | 9728.75 | 2016 | 11 | 2016_11_Asomata_english.xlsx
30 | 660 | 0 | 660 | 0 | 0 | 4 | 660 | 55 | 13.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 83.95 | 6680.000000000014 | 40.851 | 2458.17 | 1080.0000000000064 | 7482.0000000000055 | 6402 | 9.7 | 90.18345354680953 | 7270.65 | 0 | 211.35000000000582 | 0 |  | 74.09722222222221 | 6402 | 2016 | 11 | 2016_11_Asomata_english.xlsx
1 | 715 | 250 | 965 | 0 | 0 | 5 | 965 | 100 | 15.849999999998545 | 6.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.2 | 7280.000000000014 | 41.83 | 3603.6 | 600 | 10105.25 | 9505.25 | 9.85 | 88.28397526884307 | 9900 | 0 | 205.25 | 0 |  | 110.0144675925926 | 9505.25 | 2016 | 12 | 2016_12_Asomata_english.xlsx
2 | 510 | 260 | 770 | 0 | 0 | 5 | 770 | 100 | 11.55000000000291 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 2 | 84.4 | 7760.00000000002 | 41.562 | 3290.04 | 480.00000000000637 | 8180.000000000006 | 7700 | 10 | 86.54952830188678 | 8038.55 | 0 | 141.45000000000528 | 0 |  | 89.12037037037037 | 7700 | 2016 | 12 | 2016_12_Asomata_english.xlsx
3 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 55 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.55 | 8120 | 41.141 | 2797.4699999999934 | 359.99999999998 | 4904.99999999998 | 4545 | 10.1 | 85.39051319938106 | 4777.5 | 0 | 127.49999999997999 | 0 |  | 52.604166666666664 | 4545 | 2016 | 12 | 2016_12_Asomata_english.xlsx
4 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 55 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.3 | 7520 | 41.29 | 2971.8 | -600 | 3945 | 4545 | 10.1 | 85.89518526320718 | 3832.5 | 0 | 112.5 | 0 |  | 52.604166666666664 | 4545 | 2016 | 12 | 2016_12_Asomata_english.xlsx
5 | 470 | 520 | 990 | 0 | 0 | 4 | 990 | 110 | 11.80000000000291 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 83.2 | 4880.000000000014 | 41.349 | 3040.83 | -2639.9999999999864 | 7507.500000000014 | 10147.5 | 10.25 | 86.89793985318494 | 7540.9 | 0 | 26.600000000014006 | 60 |  | 117.44791666666667 | 10147.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
6 | 250 | 530 | 780 | 0 | 0 | 4 | 780 | 110 | 6.299999999995634 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 83.5 | 5600.000000000007 | 41.86 | 3638.7 | 719.9999999999936 | 8855.399999999994 | 8135.4 | 10.43 | 84.78092619759961 | 8892 | 0 | 23.39999999999418 | 60 |  | 94.15972222222223 | 8135.4 | 2016 | 12 | 2016_12_Asomata_english.xlsx
7 | 255 | 160 | 415 | 0 | 0 | 4 | 415 | 110 | 5.30000000000291 | 3.5 | 0 | 5.2 | 0 | 0 | 0 | 5.2 | 0 | 0 | 2 | 2 | Συντήρηση Ρ60 Υ/Σ Ραχιάς από ΑΔΜΗΕ | 7 | 83.65 | 5960.00000000002 | 40.802 | 2400.84 | 360.00000000001273 | 4551.500000000013 | 4191.5 | 10.1 | 87.23568635374941 | 4489.5 | 0 | 62.00000000001273 | 0 |  | 48.51273148148148 | 4191.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
8 | 435 | 0 | 435 | 0 | 0 | 5 | 435 | 40 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.2 | 7280.000000000014 | 40.973 | 2600.91 | 1319.9999999999936 | 6795.132653061218 | 4393.5 | 10.1 | 86.09872835624795 | 6795 | 1081.6326530612243 | 5.132653061217752 | 5 |  | 50.85069444444444 | 4393.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
9 | 445 | 80 | 525 | 0 | 0 | 4 | 525 | 70 | 10.349999999998545 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 83.75 | 6200.000000000007 | 41.4 | 3100.5 | -1080.0000000000064 | 4117.499999999994 | 5197.5 | 9.9 | 88.78485453335753 | 4080.7 | 0 | 36.799999999993815 | 0 |  | 60.15625 | 5197.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
10 | 145 | 215 | 360 | 0 | 0 | 4 | 360 | 55 | 3.650000000001455 | 4.350000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 84.8 | 8720 | 41.9865 | 3786.704999999996 | 2519.9999999999927 | 6062.499999999993 | 3542.5 | 9.840277777777779 | 87.1323514862913 | 5869.2 | 0 | 193.2999999999929 | 0 |  | 41.001157407407405 | 3542.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
11 | 470 | 0 | 470 | 0 | 0 | 4 | 470 | 45 | 10.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 84 | 6800.000000000007 | 41.3 | 2983.5 | -1919.9999999999927 | 2827.0000000000073 | 4747 | 10.1 | 86.50872230080151 | 2759.4 | 0 | 127.60000000000719 | 60 |  | 54.942129629629626 | 4747 | 2016 | 12 | 2016_12_Asomata_english.xlsx
12 | 760 | 325 | 1085 | 0 | 0 | 6 | 1085 | 90 | 15.849999999998545 | 7.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.25 | 7400.000000000007 | 41.6 | 3334.5 | 600 | 11450 | 10850 | 10 | 86.85680473372781 | 11527.5 | 0 | 12.5 | 90 |  | 125.57870370370371 | 10850 | 2016 | 12 | 2016_12_Asomata_english.xlsx
13 | 150 | 570 | 720 | 0 | 0 | 6 | 720 | 90 | 3.2000000000043656 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 13 | 83.7 | 6080.000000000014 | 40.82 | 2421.9 | -1319.9999999999936 | 5952.000000000006 | 7272 | 10.1 | 87.13108720944037 | 5803.5 | 0 | 208.50000000000637 | 60 |  | 84.16666666666667 | 7272 | 2016 | 12 | 2016_12_Asomata_english.xlsx
14 | 270 | 875 | 1145 | 0 | 0 | 4 | 1145 | 100 | 5.299999999995634 | 16.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.4 | 7760.00000000002 | 41.76 | 3521.7 | 1680.0000000000064 | 13244.5 | 11564.5 | 10.1 | 85.69260227909582 | 13223.8 | 0 | 20.700000000006185 | 0 |  | 133.84837962962962 | 11564.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
15 | 600 | 665 | 1265 | 0 | 0 | 4 | 1265 | 110 | 11.900000000001455 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ ΜΟΝ. ΝοΙ | 15 | 83.4 | 5360.00000000002 | 41.58 | 3311.1 | -2400 | 10503 | 12903 | 10.2 | 86.90205550819361 | 10574.6 | 0 | 28.399999999999636 | 100 |  | 149.34027777777777 | 12903 | 2016 | 12 | 2016_12_Asomata_english.xlsx
16 | 625 | 715 | 1340 | 0 | 0 | 4 | 1340 | 110 | 11.599999999998545 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 83.65 | 5960.00000000002 | 41.098 | 2747.16 | 600 | 14134 | 13534 | 10.1 | 87.23568635374941 | 14222.05 | 0 | 11.950000000000728 | 100 |  | 156.6435185185185 | 13534 | 2016 | 12 | 2016_12_Asomata_english.xlsx
17 | 480 | 165 | 645 | 0 | 0 | 5 | 645 | 110 | 9.80000000000291 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 83.9 | 6560.00000000002 | 41.4 | 3100.5 | 600 | 6985.5 | 6385.5 | 9.9 | 88.46700899206864 | 6824.2 | 0 | 161.29999999999927 | 0 |  | 73.90625 | 6385.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
18 | 330 | 390 | 720 | 0 | 0 | 5 | 720 | 110 | 6.400000000001455 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84 | 6800.000000000007 | 41.75 | 3510 | 239.99999999998727 | 7511.999999999987 | 7272 | 10.1 | 86.50872230080151 | 7467.9 | 0 | 104.09999999998763 | 60 |  | 84.16666666666667 | 7272 | 2016 | 12 | 2016_12_Asomata_english.xlsx
19 | 890 | 520 | 1410 | 0 | 0 | 5 | 1410 | 110 | 18.69999999999709 | 11.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 84.55 | 8120 | 41.69 | 3439.8 | 1319.9999999999927 | 15843 | 14523 | 10.3 | 83.73244498191734 | 15836 | 0 | 66.99999999999272 | 60 |  | 168.09027777777777 | 14523 | 2016 | 12 | 2016_12_Asomata_english.xlsx
20 | 780 | 505 | 1285 | 0 | 0 | 5 | 1285 | 110 | 16.200000000004366 | 11.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 83.55 | 5720 | 41.7 | 3451.5 | -2400 | 10707 | 13107 | 10.2 | 86.58832967603408 | 10744.8 | 0 | 22.200000000000728 | 60 |  | 151.70138888888889 | 13107 | 2016 | 12 | 2016_12_Asomata_english.xlsx
21 | 350 | 265 | 615 | 0 | 0 | 5 | 615 | 95 | 7.299999999995634 | 5.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 82.8 | 3959.9999999999936 | 41.16 | 2819.7 | -1760.0000000000064 | 4789.749999999994 | 6549.75 | 10.65 | 84.4541102826107 | 4556 | 0 | 333.74999999999363 | 100 |  | 75.80729166666667 | 6549.75 | 2016 | 12 | 2016_12_Asomata_english.xlsx
22 | 775 | 280 | 1055 | 0 | 0 | 5 | 1055 | 108 | 17 | 6.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.5 | 8000.000000000007 | 41.78 | 3545.1 | 4040.0000000000136 | 14801 | 10761 | 10.2 | 84.65282583621685 | 14843.4 | 0 | 17.600000000013097 | 60 |  | 124.54861111111111 | 10761 | 2016 | 12 | 2016_12_Asomata_english.xlsx
23 | 810 | 550 | 1360 | 0 | 0 | 4 | 1360 | 109 | 15.55000000000291 | 11.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.7 | 6080.000000000014 | 41.32 | 3006.9 | -1919.9999999999936 | 11544 | 13464 | 9.9 | 88.89131119346946 | 11380.7 | 0 | 163.30000000000655 | 0 |  | 155.83333333333334 | 13464 | 2016 | 12 | 2016_12_Asomata_english.xlsx
24 | 325 | 280 | 605 | 0 | 0 | 4 | 605 | 110 | 6.25 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.4 | 7760.00000000002 | 41.6 | 3334.5 | 1680.0000000000064 | 7669.500000000006 | 5989.5 | 9.9 | 87.4237659615018 | 7636.65 | 0 | 32.85000000000673 | 0 |  | 69.32291666666667 | 5989.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
25 | 280 | 0 | 280 | 0 | 0 | 4 | 280 | 55 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.4 | 7760.00000000002 | 40.497 | 2043.99 | 0 | 2828 | 2828 | 10.1 | 85.69260227909582 | 2804.5 | 0 | 83.5 | 60 |  | 32.73148148148148 | 2828 | 2016 | 12 | 2016_12_Asomata_english.xlsx
26 | 220 | 0 | 220 | 0 | 0 | 4 | 220 | 45 | 5.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.1 | 7039.999999999993 | 41.47 | 3182.4 | -720.0000000000273 | 1413.9999999999727 | 2134 | 9.7 | 89.86213482870929 | 1265.4 | 0 | 148.59999999997262 | 0 |  | 24.699074074074073 | 2134 | 2016 | 12 | 2016_12_Asomata_english.xlsx
27 | 610 | 570 | 1180 | 0 | 0 | 4 | 1180 | 110 | 14 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 83 | 4400 | 41.3485 | 3040.245000000004 | -2639.9999999999927 | 9278.000000000007 | 11918 | 10.1 | 88.61869113740643 | 9303 | 0 | 35.000000000007276 | 60 |  | 137.9398148148148 | 11918 | 2016 | 12 | 2016_12_Asomata_english.xlsx
28 | 730 | 660 | 1390 | 0 | 0 | 6 | 1390 | 110 | 13.849999999998545 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.4 | 7760.00000000002 | 41.6985 | 3449.745000000004 | 3360.00000000002 | 17607.5 | 14247.5 | 10.25 | 84.43856419696272 | 17640 | 0 | 27.500000000021828 | 60 |  | 164.90162037037038 | 14247.5 | 2016 | 12 | 2016_12_Asomata_english.xlsx
29 | 520 | 140 | 660 | 0 | 0 | 5 | 660 | 70 | 12.400000000001455 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.7 | 8480.000000000015 | 41.269 | 2947.23 | 719.9999999999945 | 8362.553191489356 | 6600 | 10 | 85.94145199063232 | 8209.14 | 1042.5531914893618 | 153.4131914893569 | 0 |  | 76.38888888888889 | 6600 | 2016 | 12 | 2016_12_Asomata_english.xlsx
30 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.6 | 8239.999999999993 | 41.03 | 2667.6 | -240.00000000002183 | 3684.5106382978506 | 1616 | 10.1 | 85.29028959233953 | 3690.96 | 2308.5106382978724 | 53.55063829785058 | 60 |  | 18.703703703703702 | 1616 | 2016 | 12 | 2016_12_Asomata_english.xlsx
31 | 510 | 510 | 1020 | 0 | 0 | 5 | 1020 | 110 | 10.80000000000291 | 11.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84 | 6800.000000000007 | 41.33 | 3018.6 | -1439.9999999999854 | 8964.000000000015 | 10404 | 10.2 | 85.66059757236228 | 8967.3 | 0 | 56.70000000001528 | 60 |  | 120.41666666666667 | 10404 | 2016 | 12 | 2016_12_Asomata_english.xlsx
1 | 0 | 165 | 165 | 0 | 0 | 5 | 165 | 40 | 0 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 1 | 84 | 6800.000000000007 | 40.8 | 2398.5 | 0 | 1608.75 | 1608.75 | 9.75 | 89.61416361416362 | 1511.1 | 0 | 97.65000000000009 | 0 |  | 18.619791666666668 | 1608.75 | 2017 | 1 | 2017_01_Asomata_english.xlsx
2 | 360 | 220 | 580 | 0 | 0 | 4 | 580 | 108 | 7 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 2 | 84.2 | 7280.000000000014 | 41.75 | 3510 | 480.00000000000637 | 6280.000000000006 | 5800 | 10 | 86.95971563981043 | 6085.8 | 0 | 194.2000000000071 | 0 |  | 67.12962962962963 | 5800 | 2017 | 1 | 2017_01_Asomata_english.xlsx
3 | 860 | 360 | 1220 | 0 | 0 | 5 | 1220 | 110 | 16.599999999998545 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 83.9 | 6560.00000000002 | 41.752 | 3512.34 | -719.9999999999936 | 11602 | 12322 | 10.1 | 86.71518703182966 | 11606.4 | 0 | 55.60000000000582 | 60 |  | 142.61574074074073 | 12322 | 2017 | 1 | 2017_01_Asomata_english.xlsx
4 | 375 | 770 | 1145 | 0 | 0 | 4 | 1145 | 108 | 7.19999999999709 | 15.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 83.8 | 6320 | 41.15 | 2808 | -240.00000000002 | 11324.5 | 11564.5 | 10.1 | 86.9226396323843 | 11044.9 | 0 | 339.59999999998035 | 60 |  | 133.84837962962962 | 11564.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
5 | 245 | 80 | 325 | 0 | 0 | 4 | 325 | 100 | 5.5 | 2.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 83.8 | 6320 | 41.82 | 3591.9 | 0 | 3282.5 | 3282.5 | 10.1 | 86.9226396323843 | 3248 | 0 | 94.5 | 60 |  | 37.991898148148145 | 3282.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
6 | 165 | 10 | 175 | 0 | 0 | 6 | 175 | 55 | 3.5 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 83.75 | 6200.000000000007 | 41.14 | 2796.3 | -119.99999999999272 | 3993.0423280423356 | 1785 | 10.2 | 86.17353528237643 | 3960 | 2328.0423280423283 | 93.04232804233561 | 60 |  | 20.659722222222218 | 1785 | 2017 | 1 | 2017_01_Asomata_english.xlsx
7 | 205 | 520 | 725 | 0 | 0 | 5 | 725 | 110 | 3.8000000000029104 | 8.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 83.55 | 5720 | 41.56 | 3287.7 | -480.0000000000073 | 6842.499999999993 | 7322.5 | 10.1 | 87.44563987084629 | 6818.2 | 0 | 84.2999999999929 | 60 |  | 84.7511574074074 | 7322.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
8 | 745 | 650 | 1395 | 0 | 0 | 5 | 1395 | 110 | 15.099999999998545 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 83.4 | 5360.00000000002 | 41.799 | 3567.33 | -359.99999999998 | 14357.25 | 14717.25 | 10.55 | 84.01904892735305 | 14434.75 | 0 | 42.50000000002183 | 120 |  | 170.33854166666669 | 14717.25 | 2017 | 1 | 2017_01_Asomata_english.xlsx
9 | 780 | 825 | 1605 | 0 | 0 | 4 | 1605 | 110 | 14.30000000000291 | 19.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 83.4 | 5360.00000000002 | 41.6 | 3334.5 | 0 | 17305.182978723406 | 16948.8 | 10.56 | 83.93948543405062 | 17408.95 | 356.3829787234043 | 16.232978723404813 | 120 |  | 196.1666666666667 | 16948.8 | 2017 | 1 | 2017_01_Asomata_english.xlsx
10 | 915 | 860 | 1775 | 0 | 0 | 4 | 1775 | 110 | 17.099999999998545 | 12.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 83.75 | 6200.000000000007 | 41.141 | 2797.4699999999934 | 839.9999999999873 | 20940.558510638282 | 18903.75 | 10.65 | 82.53239998875489 | 21002.2 | 1196.8085106382978 | 8.358510638285225 | 70 |  | 218.79340277777777 | 18903.75 | 2017 | 1 | 2017_01_Asomata_english.xlsx
11 | 900 | 845 | 1745 | 0 | 0 | 8 | 1745 | 110 | 16.599999999998545 | 15.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 83.3 | 5120 | 40.8 | 2398.5 | -1080.0000000000073 | 16021 | 17101 | 9.8 | 90.66808321391511 | 15540 | 0 | 480.9999999999927 | 0 |  | 197.92824074074073 | 17101 | 2017 | 1 | 2017_01_Asomata_english.xlsx
12 | 550 | 170 | 720 | 0 | 0 | 5 | 720 | 110 | 10.900000000001455 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 83.9 | 6560.00000000002 | 41.5 | 3217.5 | 1440.00000000002 | 8640.00000000002 | 7200 | 10 | 87.58233890214795 | 8446.1 | 0 | 193.90000000001965 | 0 |  | 83.33333333333333 | 7200 | 2017 | 1 | 2017_01_Asomata_english.xlsx
13 | 825 | 630 | 1455 | 0 | 0 | 4 | 1455 | 110 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 13 | 84.25 | 7400.000000000007 | 41.45 | 3159 | 839.9999999999873 | 15390 | 14550 | 10 | 86.85680473372781 | 15235.1 | 0 | 154.8999999999869 | 0 |  | 168.40277777777777 | 14550 | 2017 | 1 | 2017_01_Asomata_english.xlsx
14 | 770 | 750 | 1520 | 0 | 0 | 4 | 1520 | 110 | 15.44999999999709 | 14.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.85 | 6439.999999999993 | 41.401 | 3101.67 | -960.0000000000146 | 14240 | 15200 | 10 | 87.68697729988054 | 14171.3 | 0 | 128.69999999998436 | 60 |  | 175.92592592592592 | 15200 | 2017 | 1 | 2017_01_Asomata_english.xlsx
15 | 540 | 0 | 540 | 0 | 0 | 4 | 540 | 55 | 11.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.5 | 5600.000000000007 | 41.498 | 3215.16 | -839.9999999999854 | 4614.000000000015 | 5454 | 10.1 | 87.55099606346177 | 4555.2 | 0 | 118.80000000001473 | 60 |  | 63.125 | 5454 | 2017 | 1 | 2017_01_Asomata_english.xlsx
16 | 985 | 905 | 1890 | 0 | 0 | 7 | 1890 | 110 | 18.299999999995634 | 16.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 83.85 | 6439.999999999993 | 40.6 | 2164.5 | 839.9999999999854 | 19740 | 18900 | 10 | 87.68697729988054 | 19584 | 0 | 155.99999999998545 | 0 |  | 218.75 | 18900 | 2017 | 1 | 2017_01_Asomata_english.xlsx
17 | 705 | 490 | 1195 | 0 | 0 | 5 | 1195 | 110 | 13.200000000004366 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.7 | 8480.000000000015 | 41.35 | 3042 | 2040.0000000000218 | 14169.25 | 12129.25 | 10.15 | 84.67138127155893 | 14192.9 | 0 | 36.35000000002219 | 60 |  | 140.38483796296296 | 12129.25 | 2017 | 1 | 2017_01_Asomata_english.xlsx
18 | 0 | 565 | 565 | 0 | 0 | 5 | 565 | 55 | 0 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84 | 6800.000000000007 | 41.103 | 2753.01 | -1680.0000000000073 | 6581.930851063822 | 6017.25 | 10.65 | 82.04113570310753 | 6629 | 2244.68085106383 | 12.930851063822047 | 60 |  | 69.64409722222223 | 6017.25 | 2017 | 1 | 2017_01_Asomata_english.xlsx
19 | 865 | 850 | 1715 | 0 | 0 | 4 | 1715 | 110 | 18.25 | 17.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84 | 6800.000000000007 | 41.733 | 3490.1099999999915 | 0 | 17150 | 17150 | 10 | 87.37380952380953 | 16936 | 0 | 214 | 0 |  | 198.49537037037038 | 17150 | 2017 | 1 | 2017_01_Asomata_english.xlsx
20 | 75 | 0 | 75 | 0 | 0 | 6 | 75 | 35 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 84.3 | 7520 | 39.718 | 1132.56 | 719.9999999999927 | 1462.4999999999927 | 742.5 | 9.9 | 87.63044153115075 | 1311.2 | 0 | 151.29999999999268 | 0 |  | 8.59375 | 742.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
21 | 160 | 95 | 255 | 0 | 0 | 4 | 255 | 110 | 3 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.7 | 6080.000000000014 | 40.844 | 2449.98 | -1439.9999999999864 | 1135.5000000000136 | 2575.5 | 10.1 | 87.13108720944037 | 1131.5 | 0 | 24.000000000013642 | 20 |  | 29.80902777777778 | 2575.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
22 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 83.8 | 6320 | 40.205 | 1702.35 | 239.99999999998636 | 918.9999999999864 | 679 | 9.7 | 90.5070783801115 | 735 | 0 | 183.99999999998636 | 0 |  | 7.858796296296297 | 679 | 2017 | 1 | 2017_01_Asomata_english.xlsx
23 | 365 | 210 | 575 | 0 | 0 | 6 | 575 | 110 | 7.099999999998545 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.05 | 6920 | 41.5 | 3217.5 | 600 | 6177.5 | 5577.5 | 9.7 | 89.96898635644853 | 6037.5 | 0 | 139.9999999999991 | 0 |  | 64.55439814814814 | 5577.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
24 | 390 | 325 | 715 | 0 | 0 | 5 | 715 | 110 | 7.30000000000291 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 83.7 | 6080.000000000014 | 41.21 | 2878.2 | -839.9999999999864 | 6631.750000000013 | 7471.75 | 10.45 | 84.21282113065529 | 6559 | 0 | 132.75000000001273 | 60 |  | 86.47858796296295 | 7471.75 | 2017 | 1 | 2017_01_Asomata_english.xlsx
25 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 55 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 83.7 | 6080.000000000014 | 40.94 | 2562.3 | 0 | 692.25 | 692.25 | 10.65 | 82.63135970097161 | 759.2 | 0 | 13.050000000000068 | 80 |  | 8.012152777777779 | 692.25 | 2017 | 1 | 2017_01_Asomata_english.xlsx
26 | 90 | 0 | 90 | 0 | 0 | 5 | 90 | 40 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 83.8 | 6320 | 40.812 | 2412.54 | 239.99999999998636 | 2825.7368421052497 | 891 | 9.9 | 88.67865255425065 | 2722.9 | 1694.7368421052631 | 102.83684210524962 | 0 |  | 10.3125 | 891 | 2017 | 1 | 2017_01_Asomata_english.xlsx
27 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 50 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.65 | 5960.00000000002 | 40.998 | 2630.16 | -359.99999999998 | 2608.589743589763 | 1225 | 9.8 | 89.90616654825193 | 2476.95 | 1743.5897435897434 | 131.63974358976338 | 0 |  | 14.17824074074074 | 1225 | 2017 | 1 | 2017_01_Asomata_english.xlsx
28 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 83.6 | 5839.999999999993 | 40.73 | 2316.599999999995 | -120.00000000002728 | 2276.595177664947 | 640.25 | 9.85 | 89.55730183522063 | 2174.4 | 1756.3451776649745 | 102.1951776649471 | 0 |  | 7.410300925925926 | 640.25 | 2017 | 1 | 2017_01_Asomata_english.xlsx
29 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 55 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.05 | 6920 | 40.599 | 2163.33 | 1080.0000000000073 | 1888.0000000000073 | 808 | 10.1 | 86.4058581839159 | 1827.1 | 0 | 60.90000000000737 | 0 |  | 9.351851851851851 | 808 | 2017 | 1 | 2017_01_Asomata_english.xlsx
30 | 90 | 0 | 90 | 0 | 0 | 5 | 90 | 55 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.25 | 7400.000000000007 | 40.5 | 2047.5 | 480.0000000000073 | 3143.7020725388675 | 886.5 | 9.85 | 88.17949719160184 | 2844.45 | 1777.20207253886 | 299.25207253886765 | 0 |  | 10.260416666666666 | 886.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
31 | 0 | 165 | 165 | 0 | 0 | 5 | 165 | 55 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 31 | 84 | 6800.000000000007 | 40.949 | 2572.83 | -600 | 3466.521276595745 | 1699.5 | 10.3 | 84.82894128525196 | 3504 | 2367.021276595745 | 22.521276595744894 | 60 |  | 19.670138888888893 | 1699.5 | 2017 | 1 | 2017_01_Asomata_english.xlsx
1 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 55 | 2.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.9 | 6560.00000000002 | 41.241 | 2914.47 | -239.99999999998727 | 2942.4487179487305 | 1464.5 | 10.1 | 86.71518703182966 | 2816.1 | 1717.9487179487178 | 126.34871794873061 | 0 |  | 16.95023148148148 | 1464.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
2 | 80 | 0 | 80 | 0 | 0 | 7 | 80 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 83.85 | 6439.999999999993 | 41.051 | 2692.17 | -120.00000000002728 | 2360.9696969696697 | 784 | 9.8 | 89.47650744885767 | 2347.5 | 1696.969696969697 | 13.469696969669712 | 0 |  | 9.074074074074074 | 784 | 2017 | 2 | 2017_02_Asomata_english.xlsx
3 | 60 | 0 | 60 | 0 | 0 | 3 | 60 | 35 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83 | 4400 | 40.74 | 2328.3 | -2039.9999999999927 | 796.0851063829859 | 618 | 10.3 | 86.89793985318494 | 880.4 | 2218.0851063829787 | 35.685106382985964 | 120 |  | 7.152777777777778 | 618 | 2017 | 2 | 2017_02_Asomata_english.xlsx
4 | 55 | 0 | 55 | 0 | 0 | 7 | 55 | 37 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 83.35 | 5239.999999999993 | 40.43 | 1965.6 | 839.9999999999927 | 1378.9999999999927 | 539 | 9.8 | 90.55844828862622 | 1147.5 | 0 | 231.49999999999272 | 0 |  | 6.238425925925926 | 539 | 2017 | 2 | 2017_02_Asomata_english.xlsx
5 | 65 | 0 | 65 | 0 | 0 | 10 | 65 | 35 | 1.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 83.4 | 5360.00000000002 | 40.21 | 1708.2 | 120.00000000002728 | 2481.7759067357783 | 646.75 | 9.95 | 89.08552423955527 | 2388.75 | 1715.0259067357513 | 93.02590673577834 | 0 |  | 7.485532407407407 | 646.75 | 2017 | 2 | 2017_02_Asomata_english.xlsx
6 | 65 | 0 | 65 | 0 | 0 | 5 | 65 | 36 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 83.8 | 6320 | 39.998 | 1460.16 | 959.99999999998 | 1609.99999999998 | 650 | 10 | 87.79186602870813 | 1428.2 | 0 | 181.79999999997995 | 0 |  | 7.523148148148148 | 650 | 2017 | 2 | 2017_02_Asomata_english.xlsx
7 | 185 | 0 | 185 | 0 | 0 | 5 | 185 | 55 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.4 | 7760.00000000002 | 40.802 | 2400.84 | 1440.00000000002 | 4981.6377551020605 | 1822.25 | 9.85 | 87.86754142323531 | 4780.4 | 1719.3877551020407 | 201.23775510205996 | 0 |  | 21.09085648148148 | 1822.25 | 2017 | 2 | 2017_02_Asomata_english.xlsx
8 | 85 | 0 | 85 | 0 | 0 | 7 | 85 | 55 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 85.1 | 9439.999999999993 | 40.754 | 2344.68 | 1679.9999999999727 | 2517.2499999999727 | 837.25 | 9.85 | 86.44045838387885 | 2443.6 | 0 | 73.6499999999728 | 0 |  | 9.690393518518519 | 837.25 | 2017 | 2 | 2017_02_Asomata_english.xlsx
9 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85.1 | 9439.999999999993 | 40.801 | 2399.67 | 0 | 950 | 950 | 10 | 85.14385150812066 | 788.4 | 0 | 161.6 | 0 |  | 10.99537037037037 | 950 | 2017 | 2 | 2017_02_Asomata_english.xlsx
10 | 70 | 0 | 70 | 0 | 0 | 7 | 70 | 55 | 1.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 85 | 9200.000000000007 | 40.7 | 2281.5 | -239.99999999998545 | 2760.3808290155584 | 689.5 | 9.85 | 86.6414827057018 | 2501.2 | 2310.880829015544 | 259.1808290155582 | 0 |  | 7.980324074074074 | 689.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
11 | 85 | 0 | 85 | 0 | 0 | 6 | 85 | 55 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85 | 9200.000000000007 | 40.713 | 2296.71 | 0 | 2563.964467005076 | 833 | 9.8 | 87.08353108685334 | 2506.6 | 1730.9644670050761 | 57.36446700507622 | 0 |  | 9.641203703703704 | 833 | 2017 | 2 | 2017_02_Asomata_english.xlsx
12 | 90 | 0 | 90 | 0 | 0 | 6 | 90 | 55 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.35 | 7639.999999999993 | 40.523 | 2074.41 | -1560.0000000000146 | 1726.6595744680703 | 909 | 10.1 | 85.79377418261309 | 1701 | 2377.659574468085 | 85.65957446807033 | 60 |  | 10.520833333333334 | 909 | 2017 | 2 | 2017_02_Asomata_english.xlsx
13 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 1.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.25 | 7400.000000000007 | 40.518 | 2068.56 | -239.99999999998545 | 3028.7883597883742 | 909 | 10.1 | 85.99683637002754 | 2914.5 | 2359.7883597883597 | 174.28835978837424 | 60 |  | 10.520833333333334 | 909 | 2017 | 2 | 2017_02_Asomata_english.xlsx
14 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.25 | 7400.000000000007 | 40.421 | 1955.07 | 0 | 2639.7959183673465 | 650 | 10 | 86.85680473372781 | 2405 | 1989.7959183673468 | 234.79591836734653 | 0 |  | 7.523148148148148 | 650 | 2017 | 2 | 2017_02_Asomata_english.xlsx
15 | 90 | 0 | 90 | 0 | 0 | 7 | 90 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84 | 6800.000000000007 | 40.5 | 2047.5 | -600 | 2681.3404255319147 | 909 | 10.1 | 86.50872230080151 | 2445.5 | 2372.3404255319147 | 295.84042553191466 | 60 |  | 10.520833333333334 | 909 | 2017 | 2 | 2017_02_Asomata_english.xlsx
16 | 65 | 0 | 65 | 0 | 0 | 7 | 65 | 36 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 83.7 | 6080.000000000014 | 40.352 | 1874.34 | -719.9999999999936 | 3458.4974093264314 | 650 | 10 | 88.00239808153478 | 3498.6 | 3528.497409326425 | 19.897409326431443 | 60 |  | 7.523148148148148 | 650 | 2017 | 2 | 2017_02_Asomata_english.xlsx
17 | 65 | 0 | 65 | 0 | 0 | 5 | 65 | 37 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.75 | 6200.000000000007 | 40.271 | 1779.57 | 119.99999999999363 | 2965.275510204075 | 656.5 | 10.1 | 87.02673860200392 | 2912.7 | 2188.7755102040815 | 112.57551020407527 | 60 |  | 7.59837962962963 | 656.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
18 | 60 | 0 | 60 | 0 | 0 | 4 | 60 | 40 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 83.85 | 6439.999999999993 | 40.25 | 1755 | 239.99999999998545 | 875.9999999999854 | 636 | 10.6 | 82.72356349045334 | 751.9 | 0 | 124.09999999998547 | 0 |  | 7.361111111111111 | 636 | 2017 | 2 | 2017_02_Asomata_english.xlsx
19 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.8 | 6320 | 40.35 | 1872 | -119.99999999999272 | 970.2005076142204 | 643.5 | 9.9 | 88.67865255425065 | 847.5 | 446.70050761421317 | 122.70050761422044 | 0 |  | 7.447916666666667 | 643.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
20 | 0 | 50 | 50 | 0 | 0 | 8 | 50 | 40 | 0 | 1.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.85 | 6439.999999999993 | 40.112 | 1593.54 | 119.99999999999272 | 637.4999999999927 | 517.5 | 10.35 | 84.72171719795222 | 700.8 | 0 | 16.69999999999277 | 80 |  | 5.989583333333333 | 517.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
21 | 65 | 0 | 65 | 0 | 0 | 6 | 65 | 35 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.1 | 7039.999999999993 | 40.019 | 1484.73 | 600 | 1243.5 | 643.5 | 9.9 | 88.04673816550302 | 877.5 | 0 | 366 | 0 |  | 7.447916666666667 | 643.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
22 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.3 | 7520 | 40.28 | 1790.1 | 480.0000000000073 | 1110.5000000000073 | 630.5 | 9.7 | 89.43725475859716 | 772.65 | 0 | 337.8500000000072 | 0 |  | 7.297453703703703 | 630.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
23 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.3 | 7520 | 40.42 | 1953.9 | 0 | 707 | 707 | 10.1 | 85.89518526320718 | 744.6 | 0 | 22.4 | 60 |  | 8.18287037037037 | 707 | 2017 | 2 | 2017_02_Asomata_english.xlsx
24 | 0 | 80 | 80 | 0 | 0 | 6 | 80 | 35 | 0 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.5 | 8000.000000000007 | 40.47 | 2012.4 | 480.0000000000073 | 1264.0000000000073 | 784 | 9.8 | 88.1080432172869 | 1050 | 0 | 214.00000000000728 | 0 |  | 9.074074074074074 | 784 | 2017 | 2 | 2017_02_Asomata_english.xlsx
25 | 0 | 60 | 60 | 0 | 0 | 7 | 60 | 55 | 0 | 1.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 84.6 | 8239.999999999993 | 40.351 | 1873.17 | 239.99999999998545 | 845.9999999999854 | 606 | 10.1 | 85.29028959233953 | 781.1 | 0 | 64.89999999998543 | 0 |  | 7.013888888888889 | 606 | 2017 | 2 | 2017_02_Asomata_english.xlsx
26 | 0 | 70 | 70 | 0 | 0 | 5 | 70 | 36 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600.000000000007 | 40.302 | 1815.84 | 360.00000000001455 | 1046.0000000000146 | 686 | 9.8 | 87.59279150256593 | 825 | 0 | 221.00000000001455 | 0 |  | 7.939814814814815 | 686 | 2017 | 2 | 2017_02_Asomata_english.xlsx
27 | 0 | 130 | 130 | 0 | 0 | 5 | 130 | 55 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.95 | 9080.000000000015 | 40.762 | 2354.04 | 480.0000000000073 | 1760.5000000000073 | 1280.5 | 9.85 | 86.74234589860717 | 1545.3 | 0 | 215.2000000000071 | 0 |  | 14.820601851851851 | 1280.5 | 2017 | 2 | 2017_02_Asomata_english.xlsx
28 | 0 | 80 | 80 | 0 | 0 | 6 | 80 | 36 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85 | 9200.000000000007 | 40.771 | 2364.57 | 119.99999999999272 | 903.9999999999927 | 784 | 9.8 | 87.08353108685334 | 755 | 0 | 148.99999999999272 | 0 |  | 9.074074074074074 | 784 | 2017 | 2 | 2017_02_Asomata_english.xlsx
1 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 36 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 85 | 9200.000000000007 | 40.749 | 2338.83 | 0 | 735 | 735 | 9.8 | 87.08353108685334 | 604 | 0 | 131 | 0 |  | 8.506944444444445 | 735 | 2017 | 3 | 2017_03_Asomata_english.xlsx
2 | 0 | 100 | 100 | 0 | 0 | 5 | 100 | 54 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.75 | 6200.000000000007 | 40.921 | 2540.07 | -3000 | 2763.1578947368416 | 1000 | 10 | 87.89700598802395 | 2606.4 | 4763.157894736842 | 156.75789473684154 | 0 |  | 11.574074074074074 | 1000 | 2017 | 3 | 2017_03_Asomata_english.xlsx
3 | 0 | 130 | 130 | 0 | 0 | 8 | 130 | 55 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 83.95 | 6680.000000000014 | 41.019 | 2654.73 | 480.00000000000637 | 1780.0000000000064 | 1300 | 10 | 87.47794994040524 | 1813 | 0 | 27.000000000006366 | 60 |  | 15.046296296296296 | 1300 | 2017 | 3 | 2017_03_Asomata_english.xlsx
4 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 55 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84 | 6800.000000000007 | 41.002 | 2634.84 | 119.99999999999363 | 851.2499999999936 | 731.25 | 9.75 | 89.61416361416362 | 714.4 | 0 | 136.84999999999366 | 0 |  | 8.463541666666666 | 731.25 | 2017 | 3 | 2017_03_Asomata_english.xlsx
5 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 55 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5 | 84.35 | 7639.999999999993 | 40.979 | 2607.93 | 839.9999999999854 | 1623.9999999999854 | 784 | 9.8 | 88.42011420861144 | 1260 | 0 | 363.99999999998545 | 0 |  | 9.074074074074074 | 784 | 2017 | 3 | 2017_03_Asomata_english.xlsx
6 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 54 | 0 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 84.4 | 7760.00000000002 | 41.189 | 2853.63 | 120.00000000002728 | 1424.8673469388027 | 886.5 | 9.85 | 87.86754142323531 | 1411.85 | 418.3673469387755 | 13.017346938802802 | 0 |  | 10.260416666666666 | 886.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
7 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 55 | 0 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 84.6 | 8239.999999999993 | 41.082 | 2728.44 | 479.9999999999727 | 1123.4999999999727 | 643.5 | 9.9 | 87.01332574572012 | 764.4 | 0 | 359.09999999997274 | 0 |  | 7.447916666666667 | 643.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
8 | 0 | 195 | 195 | 0 | 0 | 6 | 195 | 55 | 0 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.55 | 8120 | 41.842 | 3617.64 | -119.99999999999272 | 1849.5000000000073 | 1969.5 | 10.1 | 85.39051319938106 | 1518.4 | 0 | 391.1000000000074 | 60 |  | 22.79513888888889 | 1969.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
9 | 0 | 140 | 140 | 0 | 0 | 6 | 140 | 55 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 84.8 | 8720 | 41.783 | 3548.61 | 600 | 1965 | 1365 | 9.75 | 87.93913251857178 | 1406 | 0 | 559 | 0 |  | 15.79861111111111 | 1365 | 2017 | 3 | 2017_03_Asomata_english.xlsx
10 | 0 | 85 | 85 | 0 | 0 | 5 | 85 | 35 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.9 | 8960.00000000002 | 40.6945 | 2275.065 | 240.00000000002 | 1098.50000000002 | 858.5 | 10.1 | 84.6938540007847 | 717.1 | 0 | 441.4000000000201 | 60 |  | 9.936342592592593 | 858.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
11 | 0 | 85 | 85 | 0 | 0 | 5 | 85 | 55 | 0 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 11 | 85 | 9200.000000000007 | 40.585 | 2146.95 | 239.99999999998727 | 1081.4999999999873 | 841.5 | 9.9 | 86.20389945971341 | 1021.65 | 0 | 119.84999999998729 | 60 |  | 9.739583333333334 | 841.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
12 | 0 | 145 | 145 | 0 | 0 | 5 | 145 | 54 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85.05 | 9320 | 40.92 | 2538.9 | 119.99999999999272 | 2016.6398963730496 | 1435.5 | 9.9 | 86.10377878670562 | 1494.8 | 461.13989637305696 | 521.8398963730494 | 0 |  | 16.614583333333332 | 1435.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
13 | 0 | 70 | 70 | 0 | 0 | 6 | 70 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 85.1 | 9439.999999999993 | 40.752 | 2342.34 | 119.99999999999272 | 826.9999999999927 | 707 | 10.1 | 84.30084307734718 | 737.3 | 0 | 149.69999999999277 | 60 |  | 8.18287037037037 | 707 | 2017 | 3 | 2017_03_Asomata_english.xlsx
14 | 60 | 185 | 245 | 0 | 0 | 5 | 245 | 110 | 1.2000000000043656 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.9 | 8960.00000000002 | 41.652 | 3395.34 | -479.9999999999727 | 1921.0000000000273 | 2401 | 9.8 | 87.2865230008087 | 1383.2 | 0 | 537.8000000000272 | 0 |  | 27.78935185185185 | 2401 | 2017 | 3 | 2017_03_Asomata_english.xlsx
15 | 0 | 145 | 145 | 0 | 0 | 4 | 145 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 84.9 | 8960.00000000002 | 41.55 | 3276 | 0 | 1479 | 1479 | 10.2 | 83.8635220988162 | 1499.4 | 0 | 39.600000000000136 | 60 |  | 17.118055555555557 | 1479 | 2017 | 3 | 2017_03_Asomata_english.xlsx
16 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85.1 | 9439.999999999993 | 41.151 | 2809.17 | 479.9999999999727 | 1123.4999999999727 | 643.5 | 9.9 | 86.0038904122431 | 815.85 | 0 | 307.6499999999728 | 0 |  | 7.447916666666667 | 643.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
17 | 0 | 65 | 65 | 0 | 0 | 6 | 65 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 17 | 85.2 | 9680.000000000015 | 41.13 | 2784.6 | 240.00000000002183 | 877.0000000000218 | 637 | 9.8 | 86.68036659108087 | 727.5 | 0 | 149.50000000002183 | 0 |  | 7.372685185185185 | 637 | 2017 | 3 | 2017_03_Asomata_english.xlsx
18 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 55 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85 | 9200.000000000007 | 41.553 | 3279.5099999999916 | -480.0000000000073 | 1272.4921465968514 | 1386 | 9.9 | 86.20389945971341 | 1102.5 | 366.4921465968586 | 169.9921465968514 | 0 |  | 16.041666666666668 | 1386 | 2017 | 3 | 2017_03_Asomata_english.xlsx
19 | 0 | 70 | 70 | 0 | 0 | 8 | 70 | 55 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 84.9 | 8960.00000000002 | 40.958 | 2583.36 | -239.99999999998727 | 956.2040816326657 | 686 | 9.8 | 87.2865230008087 | 772.5 | 510.204081632653 | 183.70408163266575 | 0 |  | 7.939814814814815 | 686 | 2017 | 3 | 2017_03_Asomata_english.xlsx
20 | 0 | 110 | 110 | 0 | 0 | 5 | 110 | 55 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.8 | 8720 | 41.12 | 2772.9 | -240.00000000002 | 848.99999999998 | 1089 | 9.9 | 86.60672141980554 | 637.5 | 0 | 211.49999999998 | 0 |  | 12.604166666666666 | 1089 | 2017 | 3 | 2017_03_Asomata_english.xlsx
21 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 21 | 84.85 | 8839.999999999993 | 40.99 | 2620.8 | 119.99999999999272 | 798.9999999999927 | 679 | 9.7 | 88.28928532762335 | 729.6 | 0 | 69.39999999999281 | 0 |  | 7.858796296296297 | 679 | 2017 | 3 | 2017_03_Asomata_english.xlsx
22 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 54 | 0 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85.1 | 9439.999999999993 | 40.848 | 2454.66 | 600 | 1376 | 776 | 9.7 | 87.77716650321717 | 1004.15 | 0 | 371.85 | 0 |  | 8.981481481481481 | 776 | 2017 | 3 | 2017_03_Asomata_english.xlsx
23 | 0 | 65 | 65 | 0 | 0 | 6 | 65 | 36 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 85.15 | 9560.00000000002 | 40.752 | 2342.34 | 120.00000000002728 | 770.0000000000273 | 650 | 10 | 85.045191193511 | 786.45 | 0 | 43.55000000002735 | 60 |  | 7.523148148148148 | 650 | 2017 | 3 | 2017_03_Asomata_english.xlsx
24 | 70 | 105 | 175 | 0 | 0 | 4 | 175 | 110 | 1.6999999999970896 | 2.400000000001455 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.6 | 8239.999999999993 | 41.402 | 3102.84 | -1320.0000000000273 | 491.2499999999727 | 1811.25 | 10.35 | 83.23013766981926 | 540.2 | 0 | 11.049999999972783 | 60 |  | 20.963541666666668 | 1811.25 | 2017 | 3 | 2017_03_Asomata_english.xlsx
25 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 84.15 | 7160.00000000002 | 41.263 | 2940.21 | -1079.9999999999727 | 1043.091836734721 | 643.5 | 9.9 | 87.9422936362438 | 747.4 | 1479.5918367346937 | 295.69183673472094 | 0 |  | 7.447916666666667 | 643.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
26 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.4 | 7760.00000000002 | 41.103 | 2753.01 | 600 | 1286 | 686 | 9.8 | 88.31584520600691 | 1095 | 0 | 191 | 0 |  | 7.939814814814815 | 686 | 2017 | 3 | 2017_03_Asomata_english.xlsx
27 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.4 | 7760.00000000002 | 41.14 | 2796.3 | 0 | 909 | 909 | 10.1 | 85.69260227909582 | 912.5 | 0 | 56.5 | 60 |  | 10.520833333333334 | 909 | 2017 | 3 | 2017_03_Asomata_english.xlsx
28 | 0 | 95 | 95 | 0 | 0 | 5 | 95 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.45 | 7880.000000000014 | 41.2 | 2866.5 | 119.99999999999363 | 1582.0906735751232 | 959.5 | 10.1 | 85.5916687075068 | 1561.4 | 502.59067357512953 | 50.69067357512313 | 30 |  | 11.105324074074074 | 959.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
29 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 55 | 1.8000000000029104 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 |  | 29 | 84.45 | 7880.000000000014 | 40.637 | 2207.79 | 0 | 1649.75 | 931 | 9.8 | 88.21182183120597 | 1423.96 | 718.75 | 225.79 | 0 |  | 10.775462962962964 | 931 | 2017 | 3 | 2017_03_Asomata_english.xlsx
30 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.75 | 8600.000000000007 | 40.403 | 1934.01 | 719.9999999999936 | 1601.9999999999936 | 882 | 9.8 | 87.59279150256593 | 1178.1 | 0 | 423.8999999999935 | 0 |  | 10.208333333333334 | 882 | 2017 | 3 | 2017_03_Asomata_english.xlsx
31 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 35 | 0 | 2.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 31 | 85 | 9200.000000000007 | 40.207 | 1704.69 | 600 | 1477.5 | 877.5 | 9.75 | 87.53011329755516 | 1154.75 | 0 | 382.75 | 60 |  | 10.15625 | 877.5 | 2017 | 3 | 2017_03_Asomata_english.xlsx
1 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 35 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 85.15 | 9560.00000000002 | 40.143 | 1629.81 | 360.00000000001273 | 1370.0000000000127 | 1010 | 10.1 | 84.20315959753565 | 1381.65 | 0 | 8.35000000001287 | 20 |  | 11.689814814814815 | 1010 | 2017 | 4 | 2017_04_Asomata_english.xlsx
2 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 36 | 0 | 2.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.2 | 9680.000000000015 | 40.236 | 1738.62 | 119.99999999999454 | 1099.9999999999945 | 980 | 9.8 | 86.68036659108087 | 821.4 | 0 | 278.59999999999445 | 0 |  | 11.342592592592593 | 980 | 2017 | 4 | 2017_04_Asomata_english.xlsx
3 | 190 | 0 | 190 | 0 | 0 | 4 | 190 | 41 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85 | 9200.000000000007 | 40.842 | 2447.64 | -480.0000000000073 | 1438.9999999999927 | 1919 | 10.1 | 84.49689154962007 | 1447.5 | 0 | 11.499999999992724 | 20 |  | 22.21064814814815 | 1919 | 2017 | 4 | 2017_04_Asomata_english.xlsx
4 | 0 | 120 | 120 | 0 | 0 | 3 | 120 | 40 | 0 | 2.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85.15 | 9560.00000000002 | 40.7925 | 2389.724999999995 | 360.00000000001273 | 1536.0000000000127 | 1176 | 9.8 | 86.78080734031734 | 1307.2 | 0 | 228.8000000000127 | 0 |  | 13.61111111111111 | 1176 | 2017 | 4 | 2017_04_Asomata_english.xlsx
5 | 0 | 225 | 225 | 0 | 0 | 4 | 225 | 40 | 0 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 5 | 84.9 | 8960.00000000002 | 41.42 | 3123.9 | -600 | 1672.5 | 2272.5 | 10.1 | 84.6938540007847 | 1533 | 0 | 169.5 | 30 |  | 26.302083333333332 | 2272.5 | 2017 | 4 | 2017_04_Asomata_english.xlsx
6 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 55 | 0 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.9 | 8960.00000000002 | 41.681 | 3429.2699999999936 | 0 | 1691.25 | 1691.25 | 10.25 | 83.45443174711465 | 1606.5 | 0 | 84.75 | 0 |  | 19.57465277777778 | 1691.25 | 2017 | 4 | 2017_04_Asomata_english.xlsx
7 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 55 | 0 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 85.05 | 9320 | 41.639 | 3380.1300000000065 | 359.99999999998 | 1633.99999999998 | 1274 | 9.8 | 86.98238877432506 | 1387.5 | 0 | 246.49999999998 | 0 |  | 14.74537037037037 | 1274 | 2017 | 4 | 2017_04_Asomata_english.xlsx
8 | 65 | 95 | 160 | 0 | 0 | 4 | 160 | 55 | 1.25 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85 | 9200.000000000007 | 41.543 | 3267.81 | -119.99999999999272 | 1456.0000000000073 | 1576 | 9.85 | 86.6414827057018 | 1155.2 | 0 | 300.80000000000723 | 0 |  | 18.24074074074074 | 1576 | 2017 | 4 | 2017_04_Asomata_english.xlsx
9 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 55 | 2.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85 | 9200.000000000007 | 41.382 | 3079.44 | 0 | 2135.994764397906 | 1225 | 9.8 | 87.08353108685334 | 1795.45 | 910.9947643979058 | 340.54476439790574 | 0 |  | 14.17824074074074 | 1225 | 2017 | 4 | 2017_04_Asomata_english.xlsx
10 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 55 | 0 | 3.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 85 | 9200.000000000007 | 41.558 | 3285.36 | 0 | 1650 | 1650 | 10 | 85.34186046511628 | 1569.5 | 0 | 80.5 | 0 |  | 19.09722222222222 | 1650 | 2017 | 4 | 2017_04_Asomata_english.xlsx
11 | 0 | 205 | 205 | 0 | 0 | 4 | 205 | 55 | 0 | 4.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 85 | 9200.000000000007 | 41.928 | 3718.2599999999916 | 0 | 2029.5 | 2029.5 | 9.9 | 86.20389945971341 | 1781.8 | 0 | 247.7 | 0 |  | 23.489583333333332 | 2029.5 | 2017 | 4 | 2017_04_Asomata_english.xlsx
12 | 0 | 160 | 160 | 0 | 0 | 2 | 160 | 55 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.9 | 8960.00000000002 | 41.5635 | 3291.7949999999937 | -239.99999999998727 | 1376.0000000000127 | 1616 | 10.1 | 84.6938540007847 | 1365 | 0 | 71.00000000001273 | 60 |  | 18.703703703703702 | 1616 | 2017 | 4 | 2017_04_Asomata_english.xlsx
13 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 35 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 85 | 9200.000000000007 | 41.523 | 3244.41 | 239.99999999998727 | 1500.9999999999873 | 1261 | 9.7 | 87.9812994485735 | 1321.25 | 0 | 179.74999999998727 | 0 |  | 14.594907407407407 | 1261 | 2017 | 4 | 2017_04_Asomata_english.xlsx
14 | 0 | 40 | 40 | 0 | 0 | 4 | 40 | 35 | 0 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.85 | 8839.999999999993 | 40.746 | 2335.32 | -360.00000000001455 | 1801.6580310880684 | 400 | 10 | 85.64060676779464 | 1610 | 1761.658031088083 | 191.65803108806836 | 0 |  | 4.62962962962963 | 400 | 2017 | 4 | 2017_04_Asomata_english.xlsx
15 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 85.2 | 9680.000000000015 | 40.306 | 1820.52 | 840.0000000000218 | 1624.0000000000218 | 784 | 9.8 | 86.68036659108087 | 1411.85 | 0 | 212.15000000002192 | 0 |  | 9.074074074074074 | 784 | 2017 | 4 | 2017_04_Asomata_english.xlsx
16 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 55 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.75 | 8600.000000000007 | 40 | 1462.5 | -1080.0000000000073 | 4704.095744680844 | 757.5 | 10.1 | 84.9910254183313 | 4657.4 | 5026.595744680852 | 106.69574468084465 | 60 |  | 8.76736111111111 | 757.5 | 2017 | 4 | 2017_04_Asomata_english.xlsx
17 | 0 | 260 | 260 | 0 | 0 | 4 | 260 | 55 | 0 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.85 | 8839.999999999993 | 40.9 | 2515.5 | 239.99999999998545 | 3190.7853403141216 | 2600 | 10 | 85.64060676779464 | 2962.5 | 350.78534031413614 | 228.28534031412164 | 0 |  | 30.09259259259259 | 2600 | 2017 | 4 | 2017_04_Asomata_english.xlsx
18 | 0 | 185 | 185 | 0 | 0 | 4 | 185 | 55 | 0 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.85 | 8839.999999999993 | 40.964 | 2590.38 | 0 | 1868.5 | 1868.5 | 10.1 | 84.79267996811352 | 1817.7 | 0 | 80.8 | 30 |  | 21.62615740740741 | 1868.5 | 2017 | 4 | 2017_04_Asomata_english.xlsx
19 | 0 | 180 | 180 | 0 | 0 | 4 | 180 | 55 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 84.9 | 8960.00000000002 | 40.902 | 2517.84 | 120.00000000002728 | 1938.0000000000273 | 1818 | 10.1 | 84.6938540007847 | 2073.2 | 0 | 14.800000000027467 | 150 |  | 21.041666666666668 | 1818 | 2017 | 4 | 2017_04_Asomata_english.xlsx
20 | 0 | 185 | 185 | 0 | 0 | 4 | 185 | 40 | 0 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 84.9 | 8960.00000000002 | 40.85 | 2457 | 0 | 1813 | 1813 | 9.8 | 87.2865230008087 | 1584.1 | 0 | 288.9 | 60 |  | 20.983796296296298 | 1813 | 2017 | 4 | 2017_04_Asomata_english.xlsx
21 | 0 | 235 | 235 | 0 | 0 | 3 | 235 | 55 | 0 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.7 | 8480.000000000015 | 41.052 | 2693.34 | -480.00000000000546 | 1822.9999999999945 | 2303 | 9.8 | 87.6953591741146 | 1613.3 | 0 | 269.6999999999946 | 60 |  | 26.65509259259259 | 2303 | 2017 | 4 | 2017_04_Asomata_english.xlsx
22 | 55 | 275 | 330 | 0 | 0 | 4 | 330 | 110 | 1.1000000000058208 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 85.25 | 9800.000000000007 | 41.44 | 3147.3 | 1319.9999999999927 | 4553.999999999993 | 3234 | 9.8 | 86.5801580747906 | 4474.9 | 0 | 139.0999999999931 | 60 |  | 37.43055555555556 | 3234 | 2017 | 4 | 2017_04_Asomata_english.xlsx
23 | 0 | 150 | 150 | 0 | 0 | 4 | 150 | 55 | 0 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 85.3 | 9920 | 40.834 | 2438.2800000000066 | 119.99999999999272 | 1574.9999999999927 | 1455 | 9.7 | 87.37172924454181 | 913.55 | 0 | 721.4499999999928 | 60 |  | 16.84027777777778 | 1455 | 2017 | 4 | 2017_04_Asomata_english.xlsx
24 | 5 | 160 | 165 | 0 | 0 | 4 | 165 | 85 | 0.09999999999854481 | 3.1499999999941792 | 0 | 0 | 2.75 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 24 | 85 | 9200.000000000007 | 40.0438 | 1513.745999999996 | -719.9999999999927 | 1012.5000000000073 | 1732.5 | 10.5 | 81.27796234772978 | 1267.5 | 0 | 194.999999999993 | 60 |  | 20.052083333333332 | 1732.5 | 2017 | 4 | 2017_04_Asomata_english.xlsx
25 | 0 | 220 | 220 | 0 | 0 | 4 | 220 | 45 | 0 | 5.30000000000291 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 25 | 85.25 | 9800.000000000007 | 39.6908 | 1100.7360000000044 | 600 | 2756 | 2156 | 9.8 | 86.5801580747906 | 2394.4 | 0 | 421.6 | 60 |  | 24.953703703703702 | 2156 | 2017 | 4 | 2017_04_Asomata_english.xlsx
26 | 0 | 270 | 270 | 0 | 0 | 3 | 270 | 55 | 0 | 5.599999999998545 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 26 | 85.2 | 9680.000000000015 | 39.524 | 905.5800000000011 | -119.99999999999272 | 2499.0000000000073 | 2619 | 9.7 | 87.57397861779305 | 2055 | 0 | 504.0000000000073 | 60 |  | 30.3125 | 2619 | 2017 | 4 | 2017_04_Asomata_english.xlsx
27 | 0 | 180 | 180 | 0 | 0 | 3 | 180 | 55 | 0 | 4.400000000001455 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 27 | 84.9 | 8960.00000000002 | 38.7775 | 32.17500000000532 | -719.9999999999945 | 1188.0000000000055 | 1908 | 10.6 | 80.69886088754012 | 1349 | 0 | 100.999999999995 | 60 |  | 22.083333333333332 | 1908 | 2017 | 4 | 2017_04_Asomata_english.xlsx
28 | 0 | 210 | 210 | 0 | 0 | 4 | 210 | 45 | 0 | 5.19999999999709 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 28 | 84.9 | 8960.00000000002 | 40.25 | 1755 | 0 | 2121 | 2121 | 10.1 | 84.6938540007847 | 1876.1 | 0 | 304.9 | 60 |  | 24.54861111111111 | 2121 | 2017 | 4 | 2017_04_Asomata_english.xlsx
29 | 0 | 300 | 300 | 0 | 0 | 5 | 300 | 40 | 0 | 7.200000000004366 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 29 | 84.5 | 8000.000000000007 | 40.552 | 2108.34 | -960.0000000000127 | 2069.9999999999873 | 3030 | 10.1 | 85.49097262667443 | 2058.6 | 0 | 71.39999999998736 | 60 |  | 35.06944444444444 | 3030 | 2017 | 4 | 2017_04_Asomata_english.xlsx
30 | 0 | 275 | 275 | 0 | 0 | 4 | 275 | 55 | 0 | 6.5 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 30 | 84.75 | 8600.000000000007 | 40.378 | 1904.76 | 600 | 3281.25 | 2681.25 | 9.75 | 88.0419853051432 | 3124.4 | 0 | 216.85 | 60 |  | 31.03298611111111 | 2681.25 | 2017 | 4 | 2017_04_Asomata_english.xlsx
1 | 0 | 285 | 285 | 0 | 0 | 1 | 285 | 40 | 0 | 6.19999999999709 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 1 | 84.65 | 8360.00000000002 | 40.74 | 2328.3 | -239.99999999998727 | 3351.265957446821 | 2878.5 | 10.1 | 85.19030097617029 | 3321.5 | 712.7659574468086 | 89.76595744682118 | 60 |  | 33.31597222222222 | 2878.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
2 | 0 | 440 | 440 | 0 | 0 | 1 | 440 | 55 | 0 | 9.099999999998545 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 2 | 84 | 6800.000000000007 | 41.901 | 3686.67 | -1560.0000000000127 | 2927.9999999999873 | 4488 | 10.2 | 85.66059757236228 | 2934.6 | 0 | 53.39999999998736 | 60 |  | 51.94444444444444 | 4488 | 2017 | 5 | 2017_05_Asomata_english.xlsx
3 | 0 | 435 | 435 | 0 | 0 | 4 | 435 | 55 | 0 | 8.900000000001455 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 3 | 84.1 | 7039.999999999993 | 42.05 | 3861 | 239.99999999998545 | 4785.749999999985 | 4545.75 | 10.45 | 83.41269931468707 | 4732 | 0 | 113.74999999998545 | 60 |  | 52.61284722222222 | 4545.75 | 2017 | 5 | 2017_05_Asomata_english.xlsx
4 | 0 | 315 | 315 | 0 | 0 | 4 | 315 | 55 | 0 | 7.900000000001455 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 4 | 84.1 | 7039.999999999993 | 40.44 | 1977.3 | 0 | 3260.25 | 3260.25 | 10.35 | 84.21861911482898 | 3255 | 0 | 65.25 | 60 |  | 37.734375 | 3260.25 | 2017 | 5 | 2017_05_Asomata_english.xlsx
5 | 0 | 300 | 300 | 0 | 0 | 2 | 300 | 55 | 0 | 7.80000000000291 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 5 | 84.4 | 7760.00000000002 | 40.024 | 1490.58 | 720.0000000000273 | 3630.0000000000273 | 2910 | 9.7 | 89.22631783699669 | 3420.15 | 0 | 209.8500000000272 | 0 |  | 33.68055555555556 | 2910 | 2017 | 5 | 2017_05_Asomata_english.xlsx
6 | 0 | 390 | 390 | 0 | 0 | 2 | 390 | 45 | 0 | 8.89999999999418 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 6 | 84.65 | 8360.00000000002 | 39.897 | 1341.99 | 600 | 4422 | 3822 | 9.8 | 87.79816733258366 | 4379 | 0 | 43 | 0 |  | 44.236111111111114 | 3822 | 2017 | 5 | 2017_05_Asomata_english.xlsx
7 | 0 | 440 | 440 | 0 | 0 | 2 | 440 | 55 | 0 | 8.80000000000291 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 7 | 84.9 | 8960.00000000002 | 40.63 | 2199.6 | 600 | 6892.347826086956 | 4488 | 10.2 | 83.8635220988162 | 6702.4 | 1804.3478260869565 | 249.9478260869555 | 60 |  | 51.94444444444444 | 4488 | 2017 | 5 | 2017_05_Asomata_english.xlsx
8 | 220 | 245 | 465 | 0 | 0 | 4 | 465 | 55 | 4.5 | 4.900000000001455 | 0 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 8 | 84.75 | 8600.000000000007 | 41.053 | 2694.5099999999916 | -360.00000000001273 | 4336.499999999987 | 4696.5 | 10.1 | 84.9910254183313 | 4283.3 | 0 | 53.199999999987085 | 0 |  | 54.357638888888886 | 4696.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
9 | 175 | 185 | 360 | 0 | 0 | 4 | 360 | 55 | 3.400000000001455 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 85 | 9200.000000000007 | 40.79 | 2386.8 | 600 | 4146 | 3546 | 9.85 | 86.6414827057018 | 4015.55 | 0 | 130.45 | 0 |  | 41.041666666666664 | 3546 | 2017 | 5 | 2017_05_Asomata_english.xlsx
10 | 190 | 290 | 480 | 0 | 0 | 4 | 480 | 99 | 4.399999999994179 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.75 | 8600.000000000007 | 41.101 | 2750.67 | -600 | 4200 | 4800 | 10 | 85.84093567251462 | 4084.55 | 0 | 115.45 | 0 |  | 55.55555555555556 | 4800 | 2017 | 5 | 2017_05_Asomata_english.xlsx
11 | 0 | 510 | 510 | 0 | 0 | 3 | 510 | 55 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 84.5 | 8000.000000000007 | 41.311 | 2996.37 | -600 | 4551 | 5151 | 10.1 | 85.49097262667443 | 4514.9 | 0 | 66.10000000000036 | 30 |  | 59.61805555555556 | 5151 | 2017 | 5 | 2017_05_Asomata_english.xlsx
12 | 335 | 100 | 435 | 0 | 0 | 4 | 435 | 70 | 8 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.45 | 7880.000000000014 | 41.5 | 3217.5 | -119.99999999999363 | 6965.557853403148 | 4452.05 | 10.234597701149426 | 84.46603170818636 | 6840.1 | 2633.5078534031413 | 185.45785340314796 | 60 |  | 51.52835648148148 | 4452.05 | 2017 | 5 | 2017_05_Asomata_english.xlsx
13 | 480 | 0 | 480 | 0 | 0 | 3 | 480 | 45 | 10.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.5 | 8000.000000000007 | 41.89 | 3673.8 | 119.99999999999363 | 5159.999999999994 | 5040 | 10.5 | 82.2341736694678 | 4973.5 | 0 | 186.49999999999363 | 0 |  | 58.333333333333336 | 5040 | 2017 | 5 | 2017_05_Asomata_english.xlsx
14 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 45 | 8.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.2 | 7280.000000000014 | 41.65 | 3393 | -719.9999999999936 | 3430.0000000000064 | 4150 | 10 | 86.95971563981043 | 3270.75 | 0 | 159.25000000000637 | 0 |  | 48.032407407407405 | 4150 | 2017 | 5 | 2017_05_Asomata_english.xlsx
15 | 0 | 465 | 465 | 0 | 0 | 4 | 465 | 55 | 0 | 9.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84 | 6800.000000000007 | 41.5 | 3217.5 | -480.00000000000637 | 4216.499999999994 | 4696.5 | 10.1 | 86.50872230080151 | 4139.1 | 0 | 137.39999999999327 | 60 |  | 54.357638888888886 | 4696.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
16 | 0 | 440 | 440 | 0 | 0 | 4 | 440 | 55 | 0 | 9.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.15 | 7160.00000000002 | 41.602 | 3336.84 | 360.00000000001273 | 4804.000000000013 | 4444 | 10.1 | 86.20086207909047 | 4493.3 | 0 | 310.70000000001255 | 0 |  | 51.43518518518518 | 4444 | 2017 | 5 | 2017_05_Asomata_english.xlsx
17 | 0 | 435 | 435 | 0 | 0 | 3 | 435 | 45 | 0 | 9.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.5 | 8000.000000000007 | 41.81 | 3580.2 | 839.9999999999873 | 5233.499999999987 | 4393.5 | 10.1 | 85.49097262667443 | 5161.1 | 0 | 132.3999999999869 | 60 |  | 50.85069444444444 | 4393.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
18 | 0 | 380 | 380 | 0 | 0 | 3 | 380 | 55 | 0 | 8.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.5 | 8000.000000000007 | 41.172 | 2833.74 | 0 | 3800 | 3800 | 10 | 86.34588235294117 | 3720 | 0 | 80 | 0 |  | 43.98148148148148 | 3800 | 2017 | 5 | 2017_05_Asomata_english.xlsx
19 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 45 | 0 | 7.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.6 | 8239.999999999993 | 41.411 | 3113.37 | 239.99999999998545 | 3757.4999999999854 | 3517.5 | 10.5 | 82.04113570310754 | 3525.9 | 0 | 231.59999999998536 | 0 |  | 40.71180555555556 | 3517.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
20 | 0 | 290 | 290 | 0 | 0 | 3 | 290 | 45 | 0 | 6.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.3 | 7520 | 41.642 | 3383.6400000000085 | -719.9999999999927 | 2209.0000000000073 | 2929 | 10.1 | 85.89518526320718 | 2146.2 | 0 | 62.80000000000746 | 0 |  | 33.90046296296296 | 2929 | 2017 | 5 | 2017_05_Asomata_english.xlsx
21 | 25 | 245 | 270 | 0 | 0 | 4 | 270 | 85 | 0.75 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 84.4 | 7760.00000000002 | 41.58 | 3311.1 | 240.00000000002 | 2967.00000000002 | 2727 | 10.1 | 85.69260227909582 | 2788.6 | 0 | 178.4000000000201 | 0 |  | 31.5625 | 2727 | 2017 | 5 | 2017_05_Asomata_english.xlsx
22 | 0 | 360 | 360 | 0 | 0 | 3 | 360 | 55 | 0 | 8.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.5 | 5600.000000000007 | 41.401 | 3101.67 | -2160.0000000000127 | 3308.43243243242 | 3636 | 10.1 | 87.55099606346177 | 3262 | 1832.4324324324325 | 106.43243243241977 | 60 |  | 42.083333333333336 | 3636 | 2017 | 5 | 2017_05_Asomata_english.xlsx
23 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 45 | 0 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 83.8 | 6320 | 40.899 | 2514.33 | 719.9999999999927 | 2335.9999999999927 | 1616 | 10.1 | 86.9226396323843 | 2065.9 | 0 | 330.09999999999263 | 60 |  | 18.703703703703702 | 1616 | 2017 | 5 | 2017_05_Asomata_english.xlsx
24 | 80 | 100 | 180 | 0 | 0 | 4 | 180 | 55 | 1.6499999999941792 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.3 | 7520 | 40.7 | 2281.5 | 1200 | 3018 | 1818 | 10.1 | 85.89518526320718 | 2766.7 | 0 | 311.3 | 60 |  | 21.041666666666668 | 1818 | 2017 | 5 | 2017_05_Asomata_english.xlsx
25 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 45 | 4.850000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.2 | 7280.000000000014 | 40.75 | 2340 | -239.99999999998636 | 2017.5000000000136 | 2257.5 | 10.5 | 82.81877679981945 | 1946 | 0 | 131.50000000001364 | 60 |  | 26.12847222222222 | 2257.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
26 | 305 | 0 | 305 | 0 | 0 | 3 | 305 | 45 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.1 | 7039.999999999993 | 41.469 | 3181.2300000000064 | -240.00000000002092 | 2809.999999999979 | 3050 | 10 | 87.16627078384799 | 2657.2 | 0 | 152.79999999997926 | 0 |  | 35.300925925925924 | 3050 | 2017 | 5 | 2017_05_Asomata_english.xlsx
27 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 45 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.2 | 7280.000000000014 | 41.471 | 3183.5699999999933 | 240.00000000002092 | 2411.500000000021 | 2171.5 | 10.1 | 86.09872835624795 | 2263 | 0 | 148.50000000002092 | 0 |  | 25.13310185185185 | 2171.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
28 | 0 | 230 | 230 | 0 | 0 | 4 | 230 | 45 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.15 | 7160.00000000002 | 41.493 | 3209.31 | -119.99999999999363 | 2203.0000000000064 | 2323 | 10.1 | 86.20086207909047 | 2065.9 | 0 | 197.10000000000628 | 60 |  | 26.886574074074073 | 2323 | 2017 | 5 | 2017_05_Asomata_english.xlsx
29 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 45 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.05 | 6920 | 41.128 | 2782.26 | -240.00000000002 | 4096.45744680849 | 2070.5 | 10.1 | 86.4058581839159 | 4018 | 2265.9574468085107 | 138.4574468084902 | 60 |  | 23.96412037037037 | 2070.5 | 2017 | 5 | 2017_05_Asomata_english.xlsx
30 | 280 | 0 | 280 | 0 | 0 | 4 | 280 | 45 | 6.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 83.7 | 6080.000000000014 | 41.102 | 2751.84 | -839.9999999999864 | 2016.0000000000136 | 2856 | 10.2 | 86.27686086424978 | 2029.4 | 0 | 46.60000000001378 | 60 |  | 33.05555555555556 | 2856 | 2017 | 5 | 2017_05_Asomata_english.xlsx
31 | 370 | 0 | 370 | 0 | 0 | 2 | 370 | 55 | 8.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84 | 6800.000000000007 | 41.776 | 3540.42 | 719.9999999999936 | 4456.999999999994 | 3737 | 10.1 | 86.50872230080151 | 4234 | 0 | 222.99999999999363 | 0 |  | 43.25231481481482 | 3737 | 2017 | 5 | 2017_05_Asomata_english.xlsx
1 | 0 | 320 | 320 | 0 | 0 | 4 | 320 | 55 | 0 | 6.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 1 | 84.2 | 7280.000000000014 | 41.7 | 3451.5 | 480.00000000000637 | 3712.0000000000064 | 3232 | 10.1 | 86.09872835624795 | 3664.8 | 0 | 107.20000000000618 | 60 |  | 37.407407407407405 | 3232 | 2017 | 6 | 2017_06_Asomata_english.xlsx
2 | 0 | 325 | 325 | 0 | 0 | 4 | 325 | 45 | 0 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.3 | 7520 | 41.669 | 3415.23 | 239.99999999998636 | 3489.9999999999864 | 3250 | 10 | 86.75413711583924 | 3426.2 | 0 | 63.799999999986085 | 0 |  | 37.61574074074074 | 3250 | 2017 | 6 | 2017_06_Asomata_english.xlsx
3 | 0 | 360 | 360 | 0 | 0 | 4 | 360 | 45 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 3 | 84.4 | 7760.00000000002 | 41.435 | 3141.45 | 240.00000000002 | 3876.00000000002 | 3636 | 10.1 | 85.69260227909582 | 3701.1 | 0 | 234.9000000000201 | 60 |  | 42.083333333333336 | 3636 | 2017 | 6 | 2017_06_Asomata_english.xlsx
4 | 345 | 0 | 345 | 0 | 0 | 4 | 345 | 45 | 8.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.45 | 7880.000000000014 | 41.606 | 3341.52 | 119.99999999999363 | 3604.4999999999936 | 3484.5 | 10.1 | 85.5916687075068 | 3569.7 | 0 | 94.79999999999382 | 60 |  | 40.329861111111114 | 3484.5 | 2017 | 6 | 2017_06_Asomata_english.xlsx
5 | 315 | 0 | 315 | 0 | 0 | 2 | 315 | 45 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.5 | 8000.000000000007 | 41.125 | 2778.75 | 119.99999999999363 | 3269.9999999999936 | 3150 | 10 | 86.34588235294117 | 3076.85 | 0 | 193.14999999999327 | 0 |  | 36.458333333333336 | 3150 | 2017 | 6 | 2017_06_Asomata_english.xlsx
6 | 175 | 190 | 365 | 0 | 0 | 3 | 365 | 55 | 3.8000000000029104 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84.45 | 7880.000000000014 | 42.05 | 3861 | -119.99999999999363 | 3639.500000000007 | 3759.5 | 10.3 | 83.92969455784646 | 3525.9 | 0 | 113.60000000000673 | 0 |  | 43.51273148148149 | 3759.5 | 2017 | 6 | 2017_06_Asomata_english.xlsx
7 | 0 | 380 | 380 | 0 | 0 | 4 | 380 | 45 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 85 | 9200.000000000007 | 41.43 | 3135.6 | 1319.9999999999936 | 5157.999999999994 | 3838 | 10.1 | 84.49689154962007 | 4845.6 | 0 | 372.3999999999942 | 60 |  | 44.4212962962963 | 3838 | 2017 | 6 | 2017_06_Asomata_english.xlsx
8 | 0 | 380 | 380 | 0 | 0 | 4 | 380 | 55 | 0 | 8.19999999999709 | 0 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΥΔΡΑΥΛΙΚΟΥ ΚΥΚΛ. ΠΕΔΗΣΗΣ Μον. ΝοΙΙ | 8 | 85 | 9200.000000000007 | 41.107 | 2757.69 | 0 | 3800 | 3800 | 10 | 85.34186046511628 | 3628.1 | 0 | 171.9 | 0 |  | 43.98148148148148 | 3800 | 2017 | 6 | 2017_06_Asomata_english.xlsx
9 | 0 | 440 | 440 | 0 | 0 | 4 | 440 | 55 | 0 | 10.150000000001455 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΥΔΡΑΥΛΙΚΟΥ ΚΥΚΛ. ΠΕΔΗΣΗΣ Μον. ΝοΙΙ | 9 | 84.9 | 8960.00000000002 | 41.302 | 2985.84 | -239.99999999998727 | 4229.148936170225 | 4400 | 10 | 85.54079254079252 | 4134.4 | 69.14893617021276 | 94.74893617022553 | 0 |  | 50.925925925925924 | 4400 | 2017 | 6 | 2017_06_Asomata_english.xlsx
10 | 0 | 450 | 450 | 0 | 0 | 4 | 450 | 55 | 0 | 10.25 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΥΔΡΑΥΛΙΚΟΥ ΚΥΚΛ. ΠΕΔΗΣΗΣ Μον. ΝοΙΙ | 10 | 84.75 | 8600.000000000007 | 41.4 | 3100.5 | -360.00000000001273 | 4094.9999999999873 | 4455 | 9.9 | 86.70801583082284 | 3936.8 | 0 | 158.19999999998709 | 0 |  | 51.5625 | 4455 | 2017 | 6 | 2017_06_Asomata_english.xlsx
11 | 0 | 430 | 430 | 0 | 0 | 4 | 430 | 45 | 0 | 9.5 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΥΔΡΑΥΛΙΚΟΥ ΚΥΚΛ. ΠΕΔΗΣΗΣ Μον. ΝοΙΙ | 11 | 84.9 | 8960.00000000002 | 41.622 | 3360.24 | 360.00000000001273 | 4574.000000000013 | 4214 | 9.8 | 87.2865230008087 | 4386.55 | 0 | 187.45000000001255 | 0 |  | 48.773148148148145 | 4214 | 2017 | 6 | 2017_06_Asomata_english.xlsx
12 | 165 | 245 | 410 | 0 | 0 | 2 | 410 | 45 | 3.900000000001455 | 5.80000000000291 | 0 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ ΥΔΡΑΥΛΙΚΟΥ ΚΥΚΛ. ΠΕΔΗΣΗΣ Μον. ΝοΙΙ | 12 | 85 | 9200.000000000007 | 41.56 | 3287.7 | 239.99999999998727 | 4380.999999999987 | 4141 | 10.1 | 84.49689154962007 | 4312.5 | 0 | 128.49999999998727 | 60 |  | 47.92824074074074 | 4141 | 2017 | 6 | 2017_06_Asomata_english.xlsx
13 | 465 | 0 | 465 | 0 | 0 | 2 | 465 | 45 | 10.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85 | 9200.000000000007 | 41.63 | 3369.6 | 0 | 4580.25 | 4580.25 | 9.85 | 86.6414827057018 | 4522.45 | 0 | 57.80000000000018 | 0 |  | 53.01215277777778 | 4580.25 | 2017 | 6 | 2017_06_Asomata_english.xlsx
14 | 470 | 0 | 470 | 0 | 0 | 4 | 470 | 45 | 11.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.9 | 8960.00000000002 | 41.776 | 3540.42 | -239.99999999998727 | 4507.000000000013 | 4747 | 10.1 | 84.6938540007847 | 4512.9 | 0 | 54.1000000000131 | 60 |  | 54.942129629629626 | 4747 | 2017 | 6 | 2017_06_Asomata_english.xlsx
15 | 280 | 175 | 455 | 0 | 0 | 3 | 455 | 55 | 6 | 3.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.95 | 9080.000000000015 | 41.75 | 3510 | 119.99999999999454 | 4601.7499999999945 | 4481.75 | 9.85 | 86.74234589860717 | 4133.55 | 0 | 468.19999999999436 | 0 |  | 51.87210648148148 | 4481.75 | 2017 | 6 | 2017_06_Asomata_english.xlsx
16 | 310 | 190 | 500 | 0 | 0 | 3 | 500 | 55 | 5.69999999999709 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 85 | 9200.000000000007 | 41.802 | 3570.84 | 119.99999999999272 | 5019.999999999993 | 4900 | 9.8 | 87.08353108685334 | 4801.8 | 0 | 218.19999999999254 | 0 |  | 56.71296296296296 | 4900 | 2017 | 6 | 2017_06_Asomata_english.xlsx
17 | 245 | 295 | 540 | 0 | 0 | 4 | 540 | 45 | 5.80000000000291 | 6.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 85 | 9200.000000000007 | 42.06 | 3872.7 | 0 | 5292 | 5292 | 9.8 | 87.08353108685334 | 5043.4 | 0 | 248.6 | 0 |  | 61.25 | 5292 | 2017 | 6 | 2017_06_Asomata_english.xlsx
18 | 490 | 0 | 490 | 0 | 0 | 4 | 490 | 45 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 85 | 9200.000000000007 | 41.62 | 3357.9 | 0 | 4949 | 4949 | 10.1 | 84.49689154962007 | 4847.2 | 0 | 161.8 | 60 |  | 57.280092592592595 | 4949 | 2017 | 6 | 2017_06_Asomata_english.xlsx
19 | 330 | 230 | 560 | 0 | 0 | 4 | 560 | 45 | 7 | 5.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.2 | 9680.000000000015 | 41.8 | 3568.5 | 480.0000000000073 | 5968.000000000007 | 5488 | 9.8 | 86.68036659108087 | 5778.3 | 0 | 189.7000000000071 | 0 |  | 63.51851851851852 | 5488 | 2017 | 6 | 2017_06_Asomata_english.xlsx
20 | 90 | 500 | 590 | 0 | 0 | 4 | 590 | 100 | 1.75 | 10.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 85.2 | 9680.000000000015 | 42.141 | 3967.4699999999934 | 0 | 5752.5 | 5752.5 | 9.75 | 87.12488129154795 | 5405.8 | 0 | 346.7000000000007 | 0 |  | 66.57986111111111 | 5752.5 | 2017 | 6 | 2017_06_Asomata_english.xlsx
21 | 615 | 0 | 615 | 0 | 0 | 2 | 615 | 54 | 12.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.9 | 8960.00000000002 | 41.611 | 3347.3699999999935 | -719.9999999999945 | 5307.0000000000055 | 6027 | 9.8 | 87.2865230008087 | 5186.85 | 0 | 120.1500000000051 | 0 |  | 69.75694444444444 | 6027 | 2017 | 6 | 2017_06_Asomata_english.xlsx
22 | 510 | 235 | 745 | 0 | 0 | 3 | 745 | 110 | 10.19999999999709 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84.4 | 7760.00000000002 | 41.81 | 3580.2 | -1200 | 6324.5 | 7524.5 | 10.1 | 85.69260227909582 | 6372.2 | 0 | 12.300000000000182 | 60 |  | 87.08912037037037 | 7524.5 | 2017 | 6 | 2017_06_Asomata_english.xlsx
23 | 590 | 0 | 590 | 0 | 0 | 3 | 590 | 45 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.65 | 8360.00000000002 | 41.758 | 3519.36 | 600 | 6352.5 | 5752.5 | 9.75 | 88.24841434454564 | 6064.8 | 0 | 287.7000000000007 | 0 |  | 66.57986111111111 | 5752.5 | 2017 | 6 | 2017_06_Asomata_english.xlsx
24 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 45 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 24 | 84.55 | 8120 | 41.668 | 3414.06 | -240.00000000002 | 5073.74999999998 | 5313.75 | 9.75 | 88.45581367320499 | 4998.1 | 0 | 75.64999999997963 | 0 |  | 61.501736111111114 | 5313.75 | 2017 | 6 | 2017_06_Asomata_english.xlsx
25 | 570 | 0 | 570 | 0 | 0 | 3 | 570 | 54 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.1 | 7039.999999999993 | 41.391 | 3089.9699999999934 | -1080.0000000000073 | 4562.999999999993 | 5643 | 9.9 | 88.04673816550302 | 4343.5 | 0 | 219.49999999999272 | 0 |  | 65.3125 | 5643 | 2017 | 6 | 2017_06_Asomata_english.xlsx
26 | 585 | 0 | 585 | 0 | 0 | 4 | 585 | 55 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.2 | 7280.000000000014 | 41.698 | 3449.16 | 240.00000000002092 | 5973.000000000021 | 5733 | 9.8 | 88.73440371409225 | 5775 | 0 | 198.00000000002092 | 0 |  | 66.35416666666667 | 5733 | 2017 | 6 | 2017_06_Asomata_english.xlsx
27 | 590 | 0 | 590 | 0 | 0 | 3 | 590 | 54 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.2 | 7280.000000000014 | 41.752 | 3512.34 | 0 | 8267.510638297872 | 5959 | 10.1 | 86.09872835624795 | 8294.4 | 2308.5106382978724 | 33.110638297872356 | 60 |  | 68.9699074074074 | 5959 | 2017 | 6 | 2017_06_Asomata_english.xlsx
28 | 645 | 0 | 645 | 0 | 0 | 4 | 645 | 55 | 13.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.4 | 7760.00000000002 | 41.802 | 3570.84 | 480.00000000000637 | 6930.000000000006 | 6450 | 10 | 86.54952830188678 | 6608 | 0 | 322.00000000000637 | 0 |  | 74.65277777777777 | 6450 | 2017 | 6 | 2017_06_Asomata_english.xlsx
29 | 580 | 85 | 665 | 0 | 0 | 4 | 665 | 90 | 12.80000000000291 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29 | 84.4 | 7760.00000000002 | 41.751 | 3511.1699999999937 | 0 | 6716.5 | 6716.5 | 10.1 | 85.69260227909582 | 6523.2 | 0 | 253.3 | 60 |  | 77.73726851851852 | 6716.5 | 2017 | 6 | 2017_06_Asomata_english.xlsx
30 | 540 | 285 | 825 | 0 | 0 | 4 | 825 | 80 | 12.44999999999709 | 7.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 84.95 | 9080.000000000015 | 41.849 | 3625.83 | 1319.9999999999945 | 9652.499999999995 | 8332.5 | 10.1 | 84.59525812883966 | 9607.5 | 0 | 104.99999999999454 | 60 |  | 96.44097222222223 | 8332.5 | 2017 | 6 | 2017_06_Asomata_english.xlsx
1 | 85 | 660 | 745 | 0 | 0 | 4 | 745 | 80 | 2.3000000000029104 | 13.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.4 | 7760.00000000002 | 41.95 | 3744 | -1319.9999999999945 | 6130.0000000000055 | 7450 | 10 | 86.54952830188678 | 5978.7 | 0 | 151.30000000000564 | 0 |  | 86.22685185185185 | 7450 | 2017 | 7 | 2017_07_Asomata_english.xlsx
2 | 55 | 865 | 920 | 0 | 0 | 4 | 920 | 105 | 0.9499999999970896 | 15.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 84.8 | 8720 | 41.9 | 3685.5 | 959.99999999998 | 10068 | 9108 | 9.9 | 86.60672141980554 | 9971.8 | 0 | 126.19999999998072 | 30 |  | 105.41666666666667 | 9108 | 2017 | 7 | 2017_07_Asomata_english.xlsx
3 | 685 | 50 | 735 | 0 | 0 | 4 | 735 | 50 | 14.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.1 | 7039.999999999993 | 41.918 | 3706.56 | -1680.0000000000073 | 5780.249999999993 | 7460.25 | 10.15 | 85.87809929443152 | 5813.5 | 0 | 26.749999999992724 | 60 |  | 86.34548611111111 | 7460.25 | 2017 | 7 | 2017_07_Asomata_english.xlsx
4 | 670 | 0 | 670 | 0 | 0 | 4 | 670 | 50 | 13.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.55 | 8120 | 41.691 | 3440.97 | 1080.0000000000073 | 7646.000000000008 | 6566 | 9.8 | 88.00450850140291 | 7555.5 | 0 | 90.50000000000819 | 0 |  | 75.99537037037038 | 6566 | 2017 | 7 | 2017_07_Asomata_english.xlsx
5 | 710 | 0 | 710 | 0 | 0 | 2 | 710 | 50 | 15.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.75 | 8600.000000000007 | 41.549 | 3274.83 | 480.0000000000073 | 7402.500000000007 | 6922.5 | 9.75 | 88.0419853051432 | 7305.75 | 0 | 96.75000000000728 | 0 |  | 80.12152777777777 | 6922.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
6 | 635 | 0 | 635 | 0 | 0 | 2 | 635 | 50 | 13.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.4 | 7760.00000000002 | 41.049 | 2689.83 | -839.9999999999873 | 7713.166666666679 | 6286.5 | 9.9 | 87.4237659615018 | 7385.2 | 2266.6666666666665 | 327.966666666679 | 0 |  | 72.76041666666667 | 6286.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
7 | 410 | 360 | 770 | 0 | 0 | 3 | 770 | 80 | 8.30000000000291 | 9.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.1 | 7039.999999999993 | 41.902 | 3687.84 | -720.0000000000273 | 7056.999999999973 | 7777 | 10.1 | 86.3032383998495 | 7034.4 | 0 | 22.59999999997217 | 0 |  | 90.01157407407408 | 7777 | 2017 | 7 | 2017_07_Asomata_english.xlsx
8 | 445 | 290 | 735 | 0 | 0 | 3 | 735 | 55 | 8.69999999999709 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.55 | 8120 | 41.829 | 3602.43 | 1080.0000000000073 | 8577.000000000007 | 7497 | 10.2 | 84.55335130526947 | 8568 | 0 | 69.00000000000728 | 60 |  | 86.77083333333333 | 7497 | 2017 | 7 | 2017_07_Asomata_english.xlsx
9 | 710 | 0 | 710 | 0 | 0 | 3 | 710 | 55 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.15 | 9560.00000000002 | 42.05 | 3861 | 1440.00000000002 | 8540.00000000002 | 7100 | 10 | 85.045191193511 | 8423.1 | 0 | 116.90000000002146 | 0 |  | 82.17592592592592 | 7100 | 2017 | 7 | 2017_07_Asomata_english.xlsx
10 | 470 | 820 | 1290 | 0 | 0 | 4 | 1290 | 108 | 8.900000000001455 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 85.05 | 9320 | 41.9 | 3685.5 | -240.00000000002 | 12789 | 13029 | 10.1 | 84.3987534641966 | 12572 | 0 | 216.99999999998 | 0 |  | 150.79861111111111 | 13029 | 2017 | 7 | 2017_07_Asomata_english.xlsx
11 | 845 | 0 | 845 | 0 | 0 | 4 | 845 | 55 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.9 | 8960.00000000002 | 41.751 | 3511.1699999999937 | -359.99999999998 | 8005.50000000002 | 8365.5 | 9.9 | 86.40484095029548 | 7926.35 | 0 | 79.15000000001965 | 0 |  | 96.82291666666667 | 8365.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
12 | 895 | 0 | 895 | 0 | 0 | 4 | 895 | 55 | 16.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.7 | 8480.000000000015 | 42.019 | 3824.73 | -480.00000000000546 | 8380.499999999995 | 8860.5 | 9.9 | 86.80954746528516 | 8139.5 | 0 | 240.99999999999454 | 0 |  | 102.55208333333333 | 8860.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
13 | 430 | 385 | 815 | 0 | 0 | 4 | 815 | 55 | 8.30000000000291 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85.3 | 9920 | 41.901 | 3686.67 | 1439.9999999999854 | 9508.499999999985 | 8068.5 | 9.9 | 85.60664380525813 | 9390.6 | 0 | 117.89999999998508 | 0 |  | 93.38541666666667 | 8068.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
14 | 385 | 425 | 810 | 0 | 0 | 4 | 810 | 55 | 7.80000000000291 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.9 | 8960.00000000002 | 41.94 | 3732.3 | -959.99999999998 | 7059.00000000002 | 8019 | 9.9 | 86.40484095029548 | 6969.72 | 0 | 89.28000000001884 | 0 |  | 92.8125 | 8019 | 2017 | 7 | 2017_07_Asomata_english.xlsx
15 | 0 | 705 | 705 | 0 | 0 | 4 | 705 | 50 | 0 | 14.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.35 | 7639.999999999993 | 42.06 | 3872.7 | -1320.0000000000273 | 5729.999999999973 | 7050 | 10 | 86.65171192443921 | 5519.85 | 0 | 210.14999999997326 | 0 |  | 81.59722222222223 | 7050 | 2017 | 7 | 2017_07_Asomata_english.xlsx
16 | 625 | 10 | 635 | 0 | 0 | 4 | 635 | 50 | 12.849999999998545 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.15 | 7160.00000000002 | 41.78 | 3545.1 | -479.9999999999727 | 5808.500000000027 | 6288.5 | 9.903149606299213 | 87.9143243928197 | 5483.1 | 0 | 325.4000000000269 | 0 |  | 72.78356481481481 | 6288.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
17 | 0 | 665 | 665 | 0 | 0 | 1 | 665 | 50 | 0 | 13.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.45 | 7880.000000000014 | 41.91 | 3697.2 | 719.9999999999936 | 9787.563829787228 | 6716.5 | 10.1 | 85.5916687075068 | 9738.2 | 2351.063829787234 | 49.36382978722759 | 0 |  | 77.73726851851852 | 6716.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
18 | 305 | 230 | 535 | 0 | 0 | 2 | 535 | 50 | 6.25 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.6 | 8239.999999999993 | 41.792 | 3559.14 | 359.9999999999791 | 5763.499999999979 | 5403.5 | 10.1 | 85.29028959233953 | 5698 | 0 | 65.49999999997908 | 0 |  | 62.54050925925926 | 5403.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
19 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 50 | 0 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.95 | 9080.000000000015 | 41.82 | 3591.9 | 840.0000000000218 | 7905.051813471524 | 5635 | 9.8 | 87.18490888788575 | 7642.5 | 1430.0518134715026 | 262.55181347152393 | 0 |  | 65.2199074074074 | 5635 | 2017 | 7 | 2017_07_Asomata_english.xlsx
20 | 0 | 555 | 555 | 0 | 0 | 4 | 555 | 50 | 0 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.05 | 9320 | 41.73 | 3486.6 | 239.99999999998545 | 5678.999999999985 | 5439 | 9.8 | 86.98238877432506 | 5607.45 | 0 | 71.54999999998472 | 0 |  | 62.951388888888886 | 5439 | 2017 | 7 | 2017_07_Asomata_english.xlsx
21 | 560 | 0 | 560 | 0 | 0 | 4 | 560 | 50 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.5 | 8000.000000000007 | 41.87 | 3650.4 | -1319.9999999999927 | 4280.000000000007 | 5600 | 10 | 86.34588235294117 | 4039.9 | 0 | 240.10000000000764 | 0 |  | 64.81481481481481 | 5600 | 2017 | 7 | 2017_07_Asomata_english.xlsx
22 | 445 | 0 | 445 | 0 | 0 | 4 | 445 | 50 | 9.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.1 | 7039.999999999993 | 41.902 | 3687.84 | -960.0000000000146 | 3489.9999999999854 | 4450 | 10 | 87.16627078384799 | 3248.5 | 0 | 241.49999999998545 | 0 |  | 51.504629629629626 | 4450 | 2017 | 7 | 2017_07_Asomata_english.xlsx
23 | 275 | 250 | 525 | 0 | 0 | 4 | 525 | 54 | 5.450000000004366 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84 | 6800.000000000007 | 41.94 | 3732.3 | -239.99999999998545 | 4957.500000000015 | 5197.5 | 9.9 | 88.25637325637325 | 4704 | 0 | 253.50000000001455 | 0 |  | 60.15625 | 5197.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
24 | 295 | 405 | 700 | 0 | 0 | 4 | 700 | 108 | 5.349999999998545 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 84.45 | 7880.000000000014 | 41.899 | 3684.33 | 1080.0000000000064 | 8150.000000000006 | 7070 | 10.1 | 85.5916687075068 | 8023 | 0 | 127.00000000000637 | 0 |  | 81.82870370370371 | 7070 | 2017 | 7 | 2017_07_Asomata_english.xlsx
25 | 335 | 240 | 575 | 0 | 0 | 4 | 575 | 54 | 7.5 | 5.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.3 | 7520 | 41.703 | 3455.01 | -360.00000000001364 | 5389.999999999986 | 5750 | 10 | 86.75413711583924 | 5225.85 | 0 | 164.1499999999869 | 0 |  | 66.55092592592592 | 5750 | 2017 | 7 | 2017_07_Asomata_english.xlsx
26 | 275 | 185 | 460 | 0 | 0 | 1 | 460 | 45 | 5.94999999999709 | 4.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.15 | 7160.00000000002 | 41.241 | 2914.47 | -359.99999999998 | 4332.00000000002 | 4692 | 10.2 | 85.355755588119 | 4347.2 | 0 | 44.80000000002019 | 60 |  | 54.30555555555556 | 4692 | 2017 | 7 | 2017_07_Asomata_english.xlsx
27 | 0 | 480 | 480 | 0 | 0 | 2 | 480 | 45 | 0 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.45 | 7880.000000000014 | 40.909 | 2526.03 | 719.9999999999936 | 5567.999999999994 | 4848 | 10.1 | 85.5916687075068 | 5365.5 | 0 | 202.49999999999363 | 0 |  | 56.111111111111114 | 4848 | 2017 | 7 | 2017_07_Asomata_english.xlsx
28 | 575 | 0 | 575 | 0 | 0 | 3 | 575 | 55 | 13.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.3 | 7520 | 41.03 | 2667.6 | -360.00000000001364 | 5332.499999999986 | 5692.5 | 9.9 | 87.63044153115075 | 5186.85 | 0 | 145.649999999986 | 0 |  | 65.88541666666667 | 5692.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
29 | 440 | 245 | 685 | 0 | 0 | 4 | 685 | 55 | 9.049999999995634 | 5.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.6 | 8239.999999999993 | 41.648 | 3390.66 | 719.9999999999927 | 7706.999999999993 | 6987 | 10.2 | 84.45411028261071 | 7740 | 0 | 26.999999999992724 | 60 |  | 80.86805555555556 | 6987 | 2017 | 7 | 2017_07_Asomata_english.xlsx
30 | 255 | 425 | 680 | 0 | 0 | 3 | 680 | 80 | 5.650000000001455 | 9.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 30 | 84.65 | 8360.00000000002 | 41.9599 | 3755.582999999998 | 120.00000000002728 | 6886.000000000027 | 6766 | 9.95 | 86.47457687028341 | 6795 | 0 | 91.00000000002728 | 0 |  | 78.31018518518519 | 6766 | 2017 | 7 | 2017_07_Asomata_english.xlsx
31 | 0 | 625 | 625 | 0 | 0 | 3 | 625 | 50 | 0 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.85 | 8839.999999999993 | 41.7 | 3451.5 | 479.9999999999727 | 6792.499999999973 | 6312.5 | 10.1 | 84.79267996811352 | 6624.3 | 0 | 168.19999999997253 | 0 |  | 73.0613425925926 | 6312.5 | 2017 | 7 | 2017_07_Asomata_english.xlsx
1 | 325 | 355 | 680 | 0 | 0 | 3 | 680 | 55 | 6.400000000001455 | 7.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 85 | 9200.000000000007 | 41.7 | 3451.5 | 360.00000000001455 | 7160.000000000015 | 6800 | 10 | 85.34186046511628 | 6697 | 0 | 463.00000000001455 | 0 |  | 78.70370370370371 | 6800 | 2017 | 8 | 2017_08_Asomata_english.xlsx
2 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 85.2 | 9680.000000000015 | 41.549 | 3274.83 | 480.0000000000073 | 10785.5 | 6868 | 10.1 | 84.10570223689035 | 10672.2 | 3437.5 | 113.30000000000655 | 0 |  | 79.49074074074075 | 6868 | 2017 | 8 | 2017_08_Asomata_english.xlsx
3 | 355 | 370 | 725 | 0 | 0 | 4 | 725 | 55 | 7.400000000001455 | 6.850000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 85.1 | 9439.999999999993 | 41.752 | 3512.34 | -240.00000000002183 | 7009.999999999978 | 7250 | 10 | 85.14385150812066 | 6891.2 | 0 | 118.79999999997835 | 0 |  | 83.91203703703704 | 7250 | 2017 | 8 | 2017_08_Asomata_english.xlsx
4 | 75 | 730 | 805 | 0 | 0 | 4 | 805 | 109 | 1.4000000000014552 | 13.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.3 | 7520 | 41.9 | 3685.5 | -1919.9999999999927 | 6250.750000000007 | 8170.75 | 10.15 | 85.47205627176281 | 6248 | 0 | 62.750000000007276 | 60 |  | 94.56886574074075 | 8170.75 | 2017 | 8 | 2017_08_Asomata_english.xlsx
5 | 0 | 750 | 750 | 0 | 0 | 4 | 750 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 5 | 84.6 | 8239.999999999993 | 42 | 3802.5 | 719.9999999999927 | 8219.999999999993 | 7500 | 10 | 86.14319248826293 | 8179.6 | 0 | 40.39999999999236 | 0 |  | 86.80555555555556 | 7500 | 2017 | 8 | 2017_08_Asomata_english.xlsx
6 | 0 | 840 | 840 | 0 | 0 | 4 | 840 | 55 | 0 | 16.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.1 | 7039.999999999993 | 42.002 | 3804.84 | -1200 | 7284 | 8484 | 10.1 | 86.3032383998495 | 7241.6 | 0 | 42.399999999999636 | 0 |  | 98.19444444444444 | 8484 | 2017 | 8 | 2017_08_Asomata_english.xlsx
7 | 670 | 145 | 815 | 0 | 0 | 4 | 815 | 110 | 12.919999999998254 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.55 | 8120 | 42.002 | 3804.84 | 1080.0000000000073 | 9311.500000000007 | 8231.5 | 10.1 | 85.39051319938106 | 9297.52 | 0 | 73.98000000000684 | 60 |  | 95.27199074074075 | 8231.5 | 2017 | 8 | 2017_08_Asomata_english.xlsx
8 | 765 | 0 | 765 | 0 | 0 | 4 | 765 | 55 | 15.580000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.8 | 8720 | 42.01 | 3814.2 | 600 | 8250 | 7650 | 10 | 85.74065420560747 | 8178.75 | 0 | 71.25000000000091 | 0 |  | 88.54166666666667 | 7650 | 2017 | 8 | 2017_08_Asomata_english.xlsx
9 | 780 | 0 | 780 | 0 | 0 | 1 | 780 | 55 | 15.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.7 | 8480.000000000015 | 42.05 | 3861 | -239.99999999998545 | 7560.000000000015 | 7800 | 10 | 85.94145199063232 | 7423.5 | 0 | 136.50000000001455 | 0 |  | 90.27777777777777 | 7800 | 2017 | 8 | 2017_08_Asomata_english.xlsx
10 | 0 | 765 | 765 | 0 | 0 | 2 | 765 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 85.1 | 9439.999999999993 | 42.003 | 3806.01 | 959.9999999999782 | 8609.999999999978 | 7650 | 10 | 85.14385150812066 | 8453.4 | 0 | 156.59999999997854 | 0 |  | 88.54166666666667 | 7650 | 2017 | 8 | 2017_08_Asomata_english.xlsx
11 | 0 | 770 | 770 | 0 | 0 | 4 | 770 | 50 | 0 | 15.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 85 | 9200.000000000007 | 42.15 | 3978 | -239.99999999998545 | 7460.000000000015 | 7700 | 10 | 85.34186046511628 | 7377.8 | 0 | 82.20000000001346 | 0 |  | 89.12037037037037 | 7700 | 2017 | 8 | 2017_08_Asomata_english.xlsx
12 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 55 | 0 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.25 | 9800.000000000007 | 41.552 | 3278.34 | 600 | 7035 | 6435 | 9.9 | 85.7056110235301 | 6852.4 | 0 | 182.6 | 0 |  | 74.47916666666667 | 6435 | 2017 | 8 | 2017_08_Asomata_english.xlsx
13 | 415 | 305 | 720 | 0 | 0 | 3 | 720 | 70 | 9 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 85.3 | 9920 | 41.852 | 3629.34 | 119.99999999999272 | 7319.999999999993 | 7200 | 10 | 84.75057736720554 | 7088.3 | 0 | 231.69999999999345 | 0 |  | 83.33333333333333 | 7200 | 2017 | 8 | 2017_08_Asomata_english.xlsx
14 | 350 | 250 | 600 | 0 | 0 | 4 | 600 | 50 | 7.099999999998545 | 5.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.3 | 9920 | 41.471 | 3183.5699999999933 | 0 | 6060 | 6060 | 10.1 | 83.91146273980748 | 5669.45 | 0 | 390.5499999999993 | 0 |  | 70.13888888888889 | 6060 | 2017 | 8 | 2017_08_Asomata_english.xlsx
15 | 0 | 660 | 660 | 0 | 0 | 4 | 660 | 50 | 0 | 13.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 85.1 | 9439.999999999993 | 41.693 | 3443.31 | -480.0000000000073 | 6119.999999999993 | 6600 | 10 | 85.14385150812066 | 5752.4 | 0 | 367.5999999999931 | 0 |  | 76.38888888888889 | 6600 | 2017 | 8 | 2017_08_Asomata_english.xlsx
16 | 345 | 325 | 670 | 0 | 0 | 4 | 670 | 55 | 7.30000000000291 | 6.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 84.9 | 8960.00000000002 | 41.8 | 3568.5 | -479.9999999999727 | 6421.000000000028 | 6901 | 10.3 | 83.04931314640051 | 6188 | 0 | 233.0000000000282 | 0 |  | 79.87268518518519 | 6901 | 2017 | 8 | 2017_08_Asomata_english.xlsx
17 | 360 | 275 | 635 | 0 | 0 | 4 | 635 | 55 | 6.94999999999709 | 6.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.75 | 8600.000000000007 | 41.663 | 3408.2099999999914 | -360.00000000001273 | 6053.499999999987 | 6413.5 | 10.1 | 84.9910254183313 | 5883.8 | 0 | 169.699999999988 | 0 |  | 74.23032407407408 | 6413.5 | 2017 | 8 | 2017_08_Asomata_english.xlsx
18 | 305 | 270 | 575 | 0 | 0 | 4 | 575 | 50 | 6.150000000001455 | 6.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.85 | 8839.999999999993 | 41.22 | 2889.9 | 239.99999999998545 | 6162.499999999985 | 5922.5 | 10.3 | 83.14622016290741 | 6117.4 | 0 | 45.09999999998581 | 0 |  | 68.54745370370371 | 5922.5 | 2017 | 8 | 2017_08_Asomata_english.xlsx
19 | 10 | 620 | 630 | 0 | 0 | 4 | 630 | 50 | 0.2529999999969732 | 12.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.95 | 9080.000000000015 | 41.321 | 3008.0699999999933 | 240.00000000002183 | 6760.500000000022 | 6520.5 | 10.35 | 82.55189440592082 | 6570.9 | 0 | 189.6000000000222 | 0 |  | 75.46875 | 6520.5 | 2017 | 8 | 2017_08_Asomata_english.xlsx
20 | 630 | 0 | 630 | 0 | 0 | 4 | 630 | 50 | 13.597000000001572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.45 | 7880.000000000014 | 41.4 | 3100.5 | -1200 | 5037 | 6237 | 9.9 | 87.32079332786046 | 5103 | 0 | 3.9999999999990905 | 70 |  | 72.1875 | 6237 | 2017 | 8 | 2017_08_Asomata_english.xlsx
21 | 0 | 625 | 625 | 0 | 0 | 1 | 625 | 50 | 0 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.65 | 8360.00000000002 | 41.782 | 3547.44 | 480.00000000000637 | 6605.000000000006 | 6125 | 9.8 | 87.79816733258366 | 6420 | 0 | 185.00000000000637 | 0 |  | 70.89120370370371 | 6125 | 2017 | 8 | 2017_08_Asomata_english.xlsx
22 | 0 | 520 | 520 | 0 | 0 | 3 | 520 | 45 | 0 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.7 | 8480.000000000015 | 41.818 | 3589.56 | 119.99999999999454 | 5319.9999999999945 | 5200 | 10 | 85.94145199063232 | 5274.4 | 0 | 45.59999999999491 | 0 |  | 60.18518518518518 | 5200 | 2017 | 8 | 2017_08_Asomata_english.xlsx
23 | 0 | 515 | 515 | 0 | 0 | 3 | 515 | 45 | 0 | 11.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 84.75 | 8600.000000000007 | 41.74 | 3498.3 | 119.99999999999272 | 5321.499999999993 | 5201.5 | 10.1 | 84.9910254183313 | 5176.5 | 0 | 144.99999999999272 | 0 |  | 60.2025462962963 | 5201.5 | 2017 | 8 | 2017_08_Asomata_english.xlsx
24 | 0 | 500 | 500 | 0 | 0 | 4 | 500 | 45 | 0 | 11.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85 | 9200.000000000007 | 41.748 | 3507.66 | 600 | 5600 | 5000 | 10 | 85.34186046511628 | 5356.55 | 0 | 243.45 | 0 |  | 57.870370370370374 | 5000 | 2017 | 8 | 2017_08_Asomata_english.xlsx
25 | 110 | 465 | 575 | 0 | 0 | 3 | 575 | 50 | 2.0500000000029104 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.95 | 9080.000000000015 | 41.96 | 3755.7 | -119.99999999999272 | 5630.000000000007 | 5750 | 10 | 85.44121071012806 | 5542.8 | 0 | 87.2000000000071 | 0 |  | 66.55092592592592 | 5750 | 2017 | 8 | 2017_08_Asomata_english.xlsx
26 | 285 | 265 | 550 | 0 | 0 | 4 | 550 | 45 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 85.05 | 9320 | 42.119 | 3941.73 | 239.99999999998545 | 5602.499999999985 | 5362.5 | 9.75 | 87.4284523065011 | 5496.4 | 0 | 106.09999999998581 | 0 |  | 62.06597222222222 | 5362.5 | 2017 | 8 | 2017_08_Asomata_english.xlsx
27 | 500 | 0 | 500 | 0 | 0 | 3 | 500 | 50 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 85.4 | 10160 | 41.831 | 3604.77 | 840.00000000002 | 5715.00000000002 | 4875 | 9.75 | 86.72338414273898 | 5396 | 0 | 319.00000000002 | 0 |  | 56.423611111111114 | 4875 | 2017 | 8 | 2017_08_Asomata_english.xlsx
28 | 0 | 540 | 540 | 0 | 0 | 4 | 540 | 54 | 0 | 11.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.4 | 10160 | 41.7 | 3451.5 | 0 | 5400 | 5400 | 10 | 84.55529953917049 | 5305.8 | 0 | 94.19999999999982 | 0 |  | 62.5 | 5400 | 2017 | 8 | 2017_08_Asomata_english.xlsx
29 | 590 | 0 | 590 | 0 | 0 | 4 | 590 | 45 | 13.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.1 | 9439.999999999993 | 41.7 | 3451.5 | -720.0000000000273 | 5061.999999999973 | 5782 | 9.8 | 86.88148113073535 | 4825.3 | 0 | 236.69999999997253 | 0 |  | 66.92129629629629 | 5782 | 2017 | 8 | 2017_08_Asomata_english.xlsx
30 | 0 | 490 | 490 | 0 | 0 | 2 | 490 | 45 | 0 | 10.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.2 | 9680.000000000015 | 41.8788 | 3660.6960000000013 | 240.00000000002183 | 5140.000000000022 | 4900 | 10 | 84.94675925925925 | 4959.36 | 0 | 180.64000000002125 | 0 |  | 56.71296296296296 | 4900 | 2017 | 8 | 2017_08_Asomata_english.xlsx
31 | 460 | 10 | 470 | 0 | 0 | 3 | 470 | 85 | 10.150000000001455 | 0.20000000000436557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 85 | 9200.000000000007 | 41.947 | 3740.4900000000084 | -480.0000000000073 | 4125.999999999993 | 4606 | 9.8 | 87.08353108685334 | 3970.35 | 0 | 155.64999999999281 | 0 |  | 53.31018518518518 | 4606 | 2017 | 8 | 2017_08_Asomata_english.xlsx
1 | 0 | 410 | 410 | 0 | 0 | 4 | 410 | 45 | 0 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 1 | 85.25 | 9800.000000000007 | 41.81 | 3580.2 | 600 | 4638.5 | 4038.5 | 9.85 | 86.14066488659371 | 4522.5 | 0 | 116 | 0 |  | 46.741898148148145 | 4038.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
2 | 0 | 425 | 425 | 0 | 0 | 4 | 425 | 45 | 0 | 9.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.15 | 9560.00000000002 | 41.811 | 3581.37 | -239.99999999998727 | 3882.5000000000127 | 4122.5 | 9.7 | 87.67545483867114 | 3820.3 | 0 | 62.20000000001255 | 0 |  | 47.714120370370374 | 4122.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
3 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 45 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.15 | 9560.00000000002 | 41.945 | 3738.15 | 0 | 3956.5 | 3956.5 | 9.65 | 88.12973180674715 | 3932.1 | 0 | 24.399999999999636 | 0 |  | 45.792824074074076 | 3956.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
4 | 0 | 415 | 415 | 0 | 0 | 3 | 415 | 45 | 0 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.3 | 9920 | 41.902 | 3687.84 | 359.99999999998 | 4385.49999999998 | 4025.5 | 9.7 | 87.37172924454181 | 4125.25 | 0 | 260.24999999998 | 0 |  | 46.59143518518518 | 4025.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
5 | 405 | 75 | 480 | 0 | 0 | 3 | 480 | 108 | 8.19999999999709 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.8 | 8720 | 41.798 | 3566.16 | -1200 | 3504 | 4704 | 9.8 | 87.49046347510966 | 3246.5 | 0 | 257.5 | 0 |  | 54.44444444444444 | 4704 | 2017 | 9 | 2017_09_Asomata_english.xlsx
6 | 0 | 320 | 320 | 0 | 0 | 4 | 320 | 45 | 0 | 7.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.95 | 9080.000000000015 | 41.452 | 3161.34 | 360.00000000001455 | 3528.0000000000146 | 3168 | 9.9 | 86.30425324255359 | 3365.3 | 0 | 162.70000000001437 | 0 |  | 36.666666666666664 | 3168 | 2017 | 9 | 2017_09_Asomata_english.xlsx
7 | 350 | 0 | 350 | 0 | 0 | 4 | 350 | 54 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85 | 9200.000000000007 | 41.65 | 3393 | 119.99999999999272 | 3584.9999999999927 | 3465 | 9.9 | 86.20389945971341 | 3404 | 0 | 180.99999999999272 | 0 |  | 40.104166666666664 | 3465 | 2017 | 9 | 2017_09_Asomata_english.xlsx
8 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 45 | 0 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.7 | 8480.000000000015 | 41.504 | 3222.18 | -719.9999999999927 | 2663.5000000000073 | 3383.5 | 10.1 | 85.09054652537853 | 2679.1 | 0 | 44.40000000000737 | 60 |  | 39.160879629629626 | 3383.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
9 | 335 | 0 | 335 | 0 | 0 | 4 | 335 | 54 | 6.75 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 84.05 | 6920 | 41.58 | 3311.1 | -1560.0000000000146 | 1722.999999999986 | 3283 | 9.8 | 89.05093547526026 | 1573.2 | 0 | 149.79999999998608 | 0 |  | 37.99768518518519 | 3283 | 2017 | 9 | 2017_09_Asomata_english.xlsx
10 | 0 | 320 | 320 | 0 | 0 | 4 | 320 | 55 | 0 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 84.4 | 7760.00000000002 | 41.698 | 3449.16 | 840.00000000002 | 3944.00000000002 | 3104 | 9.7 | 89.22631783699669 | 3881.45 | 0 | 62.550000000019736 | 0 |  | 35.925925925925924 | 3104 | 2017 | 9 | 2017_09_Asomata_english.xlsx
11 | 330 | 0 | 330 | 0 | 0 | 4 | 330 | 45 | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.6 | 8239.999999999993 | 41.88 | 3662.1 | 479.9999999999727 | 3812.9999999999727 | 3333 | 10.1 | 85.29028959233953 | 3569.7 | 0 | 243.2999999999729 | 0 |  | 38.576388888888886 | 3333 | 2017 | 9 | 2017_09_Asomata_english.xlsx
12 | 0 | 290 | 290 | 0 | 0 | 4 | 290 | 40 | 0 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.75 | 8600.000000000007 | 41.7599 | 3521.582999999998 | 360.00000000001455 | 3173.0000000000146 | 2813 | 9.7 | 88.49580997166457 | 3100.6 | 0 | 72.40000000001419 | 0 |  | 32.557870370370374 | 2813 | 2017 | 9 | 2017_09_Asomata_english.xlsx
13 | 320 | 0 | 320 | 0 | 0 | 1 | 320 | 55 | 6.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.7 | 8480.000000000015 | 41.77 | 3533.4 | -119.99999999999272 | 3112.0000000000073 | 3232 | 10.1 | 85.09054652537853 | 3124.8 | 0 | 47.200000000007094 | 60 |  | 37.407407407407405 | 3232 | 2017 | 9 | 2017_09_Asomata_english.xlsx
14 | 75 | 285 | 360 | 0 | 0 | 1 | 360 | 70 | 2.099999999998545 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.5 | 8000.000000000007 | 41.6999 | 3451.3829999999975 | -480.0000000000073 | 3155.9999999999927 | 3636 | 10.1 | 85.49097262667443 | 2980.8 | 0 | 235.19999999999254 | 60 |  | 42.083333333333336 | 3636 | 2017 | 9 | 2017_09_Asomata_english.xlsx
15 | 450 | 0 | 450 | 0 | 0 | 1 | 450 | 45 | 10.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84 | 6800.000000000007 | 41.699 | 3450.33 | -1200 | 3255 | 4455 | 9.9 | 88.25637325637325 | 3182 | 0 | 73 | 0 |  | 51.5625 | 4455 | 2017 | 9 | 2017_09_Asomata_english.xlsx
16 | 0 | 215 | 215 | 0 | 0 | 1 | 215 | 45 | 0 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 83.7 | 6080.000000000014 | 40.951 | 2575.17 | -719.9999999999936 | 1451.5000000000064 | 2171.5 | 10.1 | 87.13108720944037 | 1314 | 0 | 137.50000000000637 | 0 |  | 25.13310185185185 | 2171.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
17 | 290 | 0 | 290 | 0 | 0 | 3 | 290 | 45 | 6.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 83.7 | 6080.000000000014 | 40.851 | 2458.17 | 0 | 2958 | 2958 | 10.2 | 86.27686086424978 | 2793 | 0 | 165 | 0 |  | 34.236111111111114 | 2958 | 2017 | 9 | 2017_09_Asomata_english.xlsx
18 | 0 | 305 | 305 | 0 | 0 | 3 | 305 | 45 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 83.9 | 6560.00000000002 | 41.183 | 2846.61 | 480.00000000000637 | 3499.5000000000064 | 3019.5 | 9.9 | 88.46700899206864 | 3400.25 | 0 | 99.25000000000637 | 0 |  | 34.947916666666664 | 3019.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
19 | 235 | 0 | 235 | 0 | 0 | 3 | 235 | 55 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.05 | 6920 | 40.7255 | 2311.335 | 359.99999999998 | 2756.99999999998 | 2397 | 10.2 | 85.55874192721085 | 2804.5 | 0 | 12.499999999979991 | 60 |  | 27.743055555555557 | 2397 | 2017 | 9 | 2017_09_Asomata_english.xlsx
20 | 0 | 230 | 230 | 0 | 0 | 4 | 230 | 50 | 0 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.35 | 7639.999999999993 | 40.083 | 1559.61 | 719.9999999999927 | 2996.9999999999927 | 2277 | 9.9 | 87.52698174185778 | 2535.75 | 0 | 461.2499999999927 | 0 |  | 26.354166666666668 | 2277 | 2017 | 9 | 2017_09_Asomata_english.xlsx
21 | 235 | 0 | 235 | 0 | 0 | 4 | 235 | 45 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.45 | 7880.000000000014 | 39.511 | 890.3700000000043 | 240.00000000002092 | 2543.000000000021 | 2303 | 9.8 | 88.21182183120597 | 2511.2 | 0 | 31.8000000000211 | 0 |  | 26.65509259259259 | 2303 | 2017 | 9 | 2017_09_Asomata_english.xlsx
22 | 0 | 255 | 255 | 0 | 0 | 4 | 255 | 45 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.75 | 8600.000000000007 | 40.12 | 1602.8999999999946 | 719.9999999999936 | 3295.4999999999936 | 2575.5 | 10.1 | 84.9910254183313 | 3263.4 | 0 | 32.099999999994 | 0 |  | 29.80902777777778 | 2575.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
23 | 320 | 0 | 320 | 0 | 0 | 4 | 320 | 45 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.8 | 8720 | 40.702 | 2283.84 | 119.99999999999272 | 3351.9999999999927 | 3232 | 10.1 | 84.89173683723513 | 3204.7 | 0 | 147.2999999999929 | 0 |  | 37.407407407407405 | 3232 | 2017 | 9 | 2017_09_Asomata_english.xlsx
24 | 0 | 225 | 225 | 0 | 0 | 4 | 225 | 45 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85 | 9200.000000000007 | 40.445 | 1983.15 | 480.0000000000073 | 2640.0000000000073 | 2160 | 9.6 | 88.89777131782945 | 2547.45 | 0 | 92.550000000007 | 0 |  | 25 | 2160 | 2017 | 9 | 2017_09_Asomata_english.xlsx
25 | 265 | 0 | 265 | 0 | 0 | 1 | 265 | 54 | 5.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 85.1 | 9439.999999999993 | 40.78 | 2375.1 | 239.99999999998545 | 2889.9999999999854 | 2650 | 10 | 85.14385150812066 | 2635.3 | 0 | 254.69999999998527 | 0 |  | 30.671296296296298 | 2650 | 2017 | 9 | 2017_09_Asomata_english.xlsx
26 | 90 | 335 | 425 | 0 | 0 | 1 | 425 | 109 | 1.9000000000014552 | 7.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.85 | 8839.999999999993 | 42.101 | 3920.67 | -600 | 3586.25 | 4186.25 | 9.85 | 86.94477844446158 | 3532.5 | 0 | 53.75 | 0 |  | 48.451967592592595 | 4186.25 | 2017 | 9 | 2017_09_Asomata_english.xlsx
27 | 180 | 55 | 235 | 0 | 0 | 1 | 235 | 109 | 4.05000000000291 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.75 | 8600.000000000007 | 41.791 | 3557.9699999999934 | -239.99999999998545 | 2133.5000000000146 | 2373.5 | 10.1 | 84.9910254183313 | 2117 | 0 | 16.500000000014552 | 0 |  | 27.471064814814813 | 2373.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
28 | 0 | 220 | 220 | 0 | 0 | 2 | 220 | 45 | 0 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85 | 9200.000000000007 | 41.308 | 2992.86 | 600 | 2767 | 2167 | 9.85 | 86.6414827057018 | 2592.6 | 0 | 174.4 | 0 |  | 25.08101851851852 | 2167 | 2017 | 9 | 2017_09_Asomata_english.xlsx
29 | 165 | 25 | 190 | 0 | 0 | 3 | 190 | 45 | 4.150000000001455 | 0.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 85 | 9200.000000000007 | 41.031 | 2668.7699999999936 | 0 | 1919 | 1919 | 10.1 | 84.49689154962007 | 1898 | 0 | 51 | 30 |  | 22.21064814814815 | 1919 | 2017 | 9 | 2017_09_Asomata_english.xlsx
30 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 55 | 0 | 4.149999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.05 | 9320 | 41.053 | 2694.5099999999916 | 119.99999999999272 | 2108.4999999999927 | 1988.5 | 9.7 | 87.87911443179235 | 2023.4 | 0 | 85.09999999999286 | 0 |  | 23.015046296296294 | 1988.5 | 2017 | 9 | 2017_09_Asomata_english.xlsx
1 | 220 | 0 | 220 | 0 | 0 | 3 | 220 | 54 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85 | 9200.000000000007 | 41.178 | 2840.7599999999916 | -119.99999999999272 | 2080.0000000000073 | 2200 | 10 | 85.34186046511628 | 1949.1 | 0 | 130.90000000000737 | 0 |  | 25.462962962962962 | 2200 | 2017 | 10 | 2017_10_Asomata_english.xlsx
2 | 165 | 165 | 330 | 0 | 0 | 3 | 330 | 108 | 3.3999999999941792 | 3.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.85 | 8839.999999999993 | 41.8 | 3568.5 | -360.00000000001455 | 2906.9999999999854 | 3267 | 9.9 | 86.50566340181277 | 2712.15 | 0 | 194.84999999998536 | 0 |  | 37.8125 | 3267 | 2017 | 10 | 2017_10_Asomata_english.xlsx
3 | 205 | 0 | 205 | 0 | 0 | 3 | 205 | 45 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.05 | 9320 | 41.499 | 3216.3300000000063 | 480.0000000000073 | 2550.5000000000073 | 2070.5 | 10.1 | 84.3987534641966 | 2575.2 | 0 | 35.300000000007 | 60 |  | 23.96412037037037 | 2070.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
4 | 185 | 175 | 360 | 0 | 0 | 2 | 360 | 105 | 4.30000000000291 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.9 | 8960.00000000002 | 41.962 | 3758.0400000000086 | -359.99999999998 | 3240.00000000002 | 3600 | 10 | 85.54079254079252 | 3109.8 | 0 | 190.20000000001983 | 60 |  | 41.666666666666664 | 3600 | 2017 | 10 | 2017_10_Asomata_english.xlsx
5 | 315 | 0 | 315 | 0 | 0 | 3 | 315 | 55 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.85 | 8839.999999999993 | 41.831 | 3604.77 | -120.00000000002728 | 2998.4999999999727 | 3118.5 | 9.9 | 86.50566340181277 | 2861.6 | 0 | 136.8999999999728 | 0 |  | 36.09375 | 3118.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
6 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 45 | 0 | 5.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 6 | 85.2 | 9680.000000000015 | 41.891 | 3674.9699999999934 | 840.0000000000218 | 3140.000000000022 | 2300 | 10 | 84.94675925925925 | 3087.9 | 0 | 52.10000000002219 | 0 |  | 26.62037037037037 | 2300 | 2017 | 10 | 2017_10_Asomata_english.xlsx
7 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 55 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.1 | 9439.999999999993 | 41.35 | 3042 | -240.00000000002183 | 1690.4999999999782 | 1930.5 | 9.9 | 86.0038904122431 | 1700.9 | 0 | 49.59999999997831 | 60 |  | 22.34375 | 1930.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
8 | 0 | 225 | 225 | 0 | 0 | 3 | 225 | 40 | 0 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.05 | 9320 | 41.811 | 3581.37 | -119.99999999999272 | 2929.0957446808584 | 2272.5 | 10.1 | 84.3987534641966 | 2803.2 | 776.5957446808511 | 125.89574468085857 | 0 |  | 26.302083333333332 | 2272.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
9 | 415 | 0 | 415 | 0 | 0 | 3 | 415 | 55 | 8.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.2 | 9680.000000000015 | 41.8 | 3568.5 | 360.00000000001455 | 4551.500000000015 | 4191.5 | 10.1 | 84.10570223689035 | 4387.3 | 0 | 224.20000000001437 | 60 |  | 48.51273148148148 | 4191.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
10 | 95 | 365 | 460 | 0 | 0 | 3 | 460 | 108 | 1.9000000000014552 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.6 | 8239.999999999993 | 41.649 | 3391.83 | -1440.0000000000218 | 3205.999999999978 | 4646 | 10.1 | 85.29028959233953 | 3153.6 | 0 | 82.39999999997826 | 30 |  | 53.773148148148145 | 4646 | 2017 | 10 | 2017_10_Asomata_english.xlsx
11 | 255 | 90 | 345 | 0 | 0 | 4 | 345 | 110 | 5.5 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 85 | 9200.000000000007 | 41.848 | 3624.66 | 960.0000000000146 | 4444.500000000015 | 3484.5 | 10.1 | 84.49689154962007 | 4314.3 | 0 | 190.20000000001437 | 60 |  | 40.329861111111114 | 3484.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
12 | 0 | 200 | 200 | 0 | 0 | 4 | 200 | 54 | 0 | 4.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.2 | 9680.000000000015 | 41.2 | 2866.5 | 480.0000000000073 | 2480.0000000000073 | 2000 | 10 | 84.94675925925925 | 2396.1 | 0 | 83.90000000000737 | 0 |  | 23.14814814814815 | 2000 | 2017 | 10 | 2017_10_Asomata_english.xlsx
13 | 235 | 0 | 235 | 0 | 0 | 4 | 235 | 40 | 5.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.9 | 8960.00000000002 | 41.598 | 3332.16 | -719.9999999999945 | 1594.7500000000055 | 2314.75 | 9.85 | 86.84344420385028 | 1510 | 0 | 84.75000000000546 | 0 |  | 26.791087962962962 | 2314.75 | 2017 | 10 | 2017_10_Asomata_english.xlsx
14 | 35 | 125 | 160 | 0 | 0 | 4 | 160 | 70 | 1 | 3.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85 | 9200.000000000007 | 41.599 | 3333.33 | 239.99999999998727 | 2468.272251308888 | 1600 | 10 | 85.34186046511628 | 2343.3 | 628.2722513089005 | 124.97225130888773 | 0 |  | 18.51851851851852 | 1600 | 2017 | 10 | 2017_10_Asomata_english.xlsx
15 | 165 | 0 | 165 | 0 | 0 | 3 | 165 | 55 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 85.2 | 9680.000000000015 | 41.35 | 3042 | 480.0000000000073 | 3103.404255319156 | 1650 | 10 | 84.94675925925925 | 2949.2 | 973.4042553191489 | 154.20425531915635 | 0 |  | 19.09722222222222 | 1650 | 2017 | 10 | 2017_10_Asomata_english.xlsx
16 | 0 | 155 | 155 | 0 | 0 | 3 | 155 | 45 | 0 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85 | 9200.000000000007 | 41.299 | 2982.33 | -480.0000000000073 | 2746.6923076923003 | 1519 | 9.8 | 87.08353108685334 | 2585.15 | 1707.6923076923076 | 161.5423076923007 | 0 |  | 17.58101851851852 | 1519 | 2017 | 10 | 2017_10_Asomata_english.xlsx
17 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 45 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.2 | 9680.000000000015 | 41.5 | 3217.5 | 480.0000000000073 | 3782.234042553199 | 1515 | 10.1 | 84.10570223689035 | 3817.9 | 1787.2340425531916 | 24.334042553199197 | 60 |  | 17.53472222222222 | 1515 | 2017 | 10 | 2017_10_Asomata_english.xlsx
18 | 0 | 145 | 145 | 0 | 0 | 1 | 145 | 45 | 0 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85.05 | 9320 | 41.352 | 3044.34 | -360.00000000001455 | 5504.893617021262 | 1450 | 10 | 85.24274099883856 | 5307.1 | 4414.893617021276 | 197.79361702126153 | 0 |  | 16.78240740740741 | 1450 | 2017 | 10 | 2017_10_Asomata_english.xlsx
19 | 135 | 75 | 210 | 0 | 0 | 1 | 210 | 108 | 2.7000000000043656 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.1 | 9439.999999999993 | 41.4 | 3100.5 | 119.99999999999272 | 5051.256410256403 | 2121 | 10.1 | 84.30084307734718 | 5066.2 | 2810.25641025641 | 15.056410256403069 | 30 |  | 24.54861111111111 | 2121 | 2017 | 10 | 2017_10_Asomata_english.xlsx
20 | 0 | 230 | 230 | 0 | 0 | 4 | 230 | 54 | 0 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.1 | 9439.999999999993 | 41.5285 | 3250.8450000000043 | 0 | 4769.808510638298 | 2323 | 10.1 | 84.30084307734718 | 4701.2 | 2446.808510638298 | 128.60851063829796 | 60 |  | 26.886574074074073 | 2323 | 2017 | 10 | 2017_10_Asomata_english.xlsx
21 | 100 | 85 | 185 | 0 | 0 | 4 | 185 | 80 | 2.099999999998545 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 85.1 | 9439.999999999993 | 41.654 | 3397.6800000000067 | 0 | 1850 | 1850 | 10 | 85.14385150812066 | 1694.6 | 0 | 155.4 | 0 |  | 21.412037037037038 | 1850 | 2017 | 10 | 2017_10_Asomata_english.xlsx
22 | 105 | 145 | 250 | 0 | 0 | 4 | 250 | 109 | 2.349999999998545 | 3.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.7 | 8480.000000000015 | 41.798 | 3566.16 | -959.9999999999782 | 1515.0000000000218 | 2475 | 9.9 | 86.80954746528516 | 1415.5 | 0 | 99.50000000002183 | 0 |  | 28.645833333333332 | 2475 | 2017 | 10 | 2017_10_Asomata_english.xlsx
23 | 150 | 0 | 150 | 0 | 0 | 1 | 150 | 54 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.85 | 8839.999999999993 | 41.822 | 3594.2400000000084 | 359.9999999999782 | 1874.9999999999782 | 1515 | 10.1 | 84.79267996811352 | 1540 | 0 | 334.9999999999782 | 0 |  | 17.53472222222222 | 1515 | 2017 | 10 | 2017_10_Asomata_english.xlsx
24 | 0 | 145 | 145 | 0 | 0 | 1 | 145 | 45 | 0 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.95 | 9080.000000000015 | 41.888 | 3671.46 | 240.00000000002183 | 3372.051282051304 | 1450 | 10 | 85.44121071012806 | 3257.95 | 1682.051282051282 | 114.10128205130422 | 0 |  | 16.78240740740741 | 1450 | 2017 | 10 | 2017_10_Asomata_english.xlsx
25 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 45 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85 | 9200.000000000007 | 41.774 | 3538.08 | 119.99999999999272 | 1685.4999999999927 | 1565.5 | 10.1 | 84.49689154962007 | 1460 | 0 | 285.4999999999927 | 60 |  | 18.119212962962962 | 1565.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
26 | 0 | 125 | 125 | 0 | 0 | 3 | 125 | 54 | 0 | 2.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85.1 | 9439.999999999993 | 41.58 | 3311.1 | 239.99999999998545 | 1489.9999999999854 | 1250 | 10 | 85.14385150812066 | 1367.1 | 0 | 122.89999999998554 | 0 |  | 14.467592592592593 | 1250 | 2017 | 10 | 2017_10_Asomata_english.xlsx
27 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 54 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 85.1 | 9439.999999999993 | 41.701 | 3452.67 | 0 | 1550 | 1550 | 10 | 85.14385150812066 | 1306.7 | 0 | 243.3 | 0 |  | 17.939814814814813 | 1550 | 2017 | 10 | 2017_10_Asomata_english.xlsx
28 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 44 | 0 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.2 | 9680.000000000015 | 41.063 | 2706.21 | 240.00000000002183 | 890.0000000000218 | 650 | 10 | 84.94675925925925 | 777 | 0 | 113.00000000002183 | 0 |  | 7.523148148148148 | 650 | 2017 | 10 | 2017_10_Asomata_english.xlsx
29 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 45 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.25 | 9800.000000000007 | 41.15 | 2808 | 119.99999999999272 | 952.9999999999928 | 833 | 9.8 | 86.5801580747906 | 686.2 | 0 | 266.7999999999929 | 0 |  | 9.641203703703704 | 833 | 2017 | 10 | 2017_10_Asomata_english.xlsx
30 | 0 | 220 | 220 | 0 | 0 | 3 | 220 | 54 | 0 | 4.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.85 | 8839.999999999993 | 41.8615 | 3640.454999999996 | -960.0000000000146 | 1217.9999999999854 | 2178 | 9.9 | 86.50566340181277 | 1080.4 | 0 | 137.59999999998536 | 0 |  | 25.208333333333332 | 2178 | 2017 | 10 | 2017_10_Asomata_english.xlsx
31 | 215 | 190 | 405 | 0 | 0 | 3 | 405 | 109 | 4 | 3.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 85 | 9200.000000000007 | 41.842 | 3617.64 | 360.00000000001455 | 4288.500000000015 | 3928.5 | 9.7 | 87.9812994485735 | 4093.95 | 0 | 194.55000000001473 | 0 |  | 45.46875 | 3928.5 | 2017 | 10 | 2017_10_Asomata_english.xlsx
1 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 55 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.1 | 9439.999999999993 | 41.4635 | 3174.795000000004 | 239.99999999998545 | 1539.9999999999854 | 1300 | 10 | 85.14385150812066 | 1408.9 | 0 | 131.09999999998558 | 0 |  | 15.046296296296296 | 1300 | 2017 | 11 | 2017_11_Asomata_english.xlsx
2 | 0 | 235 | 235 | 0 | 0 | 4 | 235 | 54 | 0 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85 | 9200.000000000007 | 41.782 | 3547.44 | -239.99999999998545 | 2133.5000000000146 | 2373.5 | 10.1 | 84.49689154962007 | 1942.5 | 0 | 191.00000000001455 | 0 |  | 27.471064814814813 | 2373.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
3 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 40 | 1.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85.1 | 9439.999999999993 | 41.147 | 2804.49 | 239.99999999998545 | 873.7499999999854 | 633.75 | 9.75 | 87.32702718781606 | 656.85 | 0 | 216.89999999998543 | 0 |  | 7.335069444444445 | 633.75 | 2017 | 11 | 2017_11_Asomata_english.xlsx
4 | 0 | 265 | 265 | 0 | 0 | 3 | 265 | 54 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85 | 9200.000000000007 | 41.702 | 3453.84 | -239.99999999998545 | 2383.5000000000146 | 2623.5 | 9.9 | 86.20389945971341 | 2190.4 | 0 | 253.10000000001446 | 60 |  | 30.364583333333332 | 2623.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
5 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 54 | 1.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.05 | 9320 | 40.7 | 2281.5 | 119.99999999999272 | 1941.3936170212694 | 656.5 | 10.1 | 84.3987534641966 | 1817.7 | 1164.8936170212767 | 123.69361702126935 | 0 |  | 7.59837962962963 | 656.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
6 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 54 | 0 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 85 | 9200.000000000007 | 40.967 | 2593.89 | -119.99999999999272 | 877.5000000000073 | 997.5 | 10.5 | 81.27796234772978 | 737.3 | 0 | 200.20000000000732 | 60 |  | 11.54513888888889 | 997.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
7 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 54 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85 | 9200.000000000007 | 41.702 | 3453.84 | 0 | 1813 | 1813 | 9.8 | 87.08353108685334 | 1631.55 | 0 | 181.45 | 0 |  | 20.983796296296298 | 1813 | 2017 | 11 | 2017_11_Asomata_english.xlsx
8 | 0 | 225 | 225 | 0 | 0 | 3 | 225 | 54 | 0 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.9 | 8960.00000000002 | 41.7765 | 3541.004999999996 | -239.99999999998727 | 3726.4948453608376 | 2250 | 10 | 85.54079254079252 | 3516.4 | 1716.4948453608247 | 210.09484536083755 | 0 |  | 26.041666666666668 | 2250 | 2017 | 11 | 2017_11_Asomata_english.xlsx
9 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 55 | 1.3499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.9 | 8960.00000000002 | 41.15 | 2808 | 0 | 787.5 | 787.5 | 10.5 | 81.46742146742146 | 657 | 0 | 130.5 | 0 |  | 9.114583333333334 | 787.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
10 | 0 | 135 | 135 | 0 | 0 | 3 | 135 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.35 | 7639.999999999993 | 41.492 | 3208.14 | -1320.0000000000273 | 3500.946808510611 | 1363.5 | 10.1 | 85.79377418261309 | 3343.4 | 3457.446808510638 | 217.54680851061084 | 60 |  | 15.78125 | 1363.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
11 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 45 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.55 | 8120 | 41.548 | 3273.66 | 480.0000000000073 | 1530.0000000000073 | 1050 | 10 | 86.24441833137486 | 1387 | 0 | 203.00000000000728 | 60 |  | 12.152777777777779 | 1050 | 2017 | 11 | 2017_11_Asomata_english.xlsx
12 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.6 | 8239.999999999993 | 41.278 | 2957.76 | 119.99999999999272 | 877.4999999999927 | 757.5 | 10.1 | 85.29028959233953 | 722.7 | 0 | 214.7999999999928 | 60 |  | 8.76736111111111 | 757.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
13 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 55 | 2.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.3 | 7520 | 41.732 | 3488.94 | -719.9999999999927 | 2518.07692307693 | 1515 | 10.1 | 85.89518526320718 | 2400 | 1723.076923076923 | 118.07692307693014 | 0 |  | 17.53472222222222 | 1515 | 2017 | 11 | 2017_11_Asomata_english.xlsx
14 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.15 | 7160.00000000002 | 41.35 | 3042 | -359.99999999998 | 2187.822580645181 | 757.5 | 10.1 | 86.20086207909047 | 2170 | 1790.3225806451612 | 77.822580645181 | 60 |  | 8.76736111111111 | 757.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
15 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.35 | 7639.999999999993 | 41.17 | 2831.4 | 479.9999999999727 | 2446.4489795918093 | 844 | 10.55 | 82.13432409899451 | 2249.9 | 1122.4489795918366 | 256.54897959180926 | 60 |  | 9.768518518518519 | 844 | 2017 | 11 | 2017_11_Asomata_english.xlsx
16 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 35 | 0 | 2.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.4 | 7760.00000000002 | 41.3 | 2983.5 | 120.00000000002728 | 2414.7368421052906 | 800 | 10 | 86.54952830188678 | 1547.6 | 1494.7368421052631 | 867.1368421052907 | 0 |  | 9.25925925925926 | 800 | 2017 | 11 | 2017_11_Asomata_english.xlsx
17 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 54 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.9 | 8960.00000000002 | 41.46 | 3170.7 | 1200 | 3063.157894736842 | 700 | 10 | 85.54079254079252 | 2354.2 | 1163.157894736842 | 708.9578947368418 | 0 |  | 8.101851851851851 | 700 | 2017 | 11 | 2017_11_Asomata_english.xlsx
18 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 55 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.95 | 9080.000000000015 | 41.46 | 3170.7 | 119.99999999999454 | 2470.5531914893563 | 808 | 10.1 | 84.59525812883966 | 2372.5 | 1542.5531914893618 | 98.05319148935632 | 0 |  | 9.351851851851851 | 808 | 2017 | 11 | 2017_11_Asomata_english.xlsx
19 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 35 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.7 | 8480.000000000015 | 41.75 | 3510 | -600 | 926.75 | 1526.75 | 9.85 | 87.25020506663179 | 823.2 | 0 | 103.55 | 0 |  | 17.67071759259259 | 1526.75 | 2017 | 11 | 2017_11_Asomata_english.xlsx
20 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 45 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.8 | 8720 | 41.2 | 2866.5 | 239.99999999998545 | 2153.2653061224346 | 750 | 10 | 85.74065420560747 | 1841.138 | 1163.265306122449 | 312.1273061224347 | 0 |  | 8.680555555555555 | 750 | 2017 | 11 | 2017_11_Asomata_english.xlsx
21 | 135 | 0 | 135 | 0 | 0 | 4 | 135 | 55 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.65 | 8360.00000000002 | 41.5785 | 3309.3449999999934 | -359.99999999998 | 2150.8684210526517 | 1363.5 | 10.1 | 85.19030097617029 | 2167.5 | 1147.3684210526317 | 43.368421052651684 | 60 |  | 15.78125 | 1363.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
22 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 55 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.8 | 8720 | 41.75 | 3510 | 359.99999999998 | 3720.880829015524 | 1050 | 10 | 85.74065420560747 | 3535.35 | 2310.880829015544 | 185.53082901552398 | 0 |  | 12.152777777777779 | 1050 | 2017 | 11 | 2017_11_Asomata_english.xlsx
23 | 120 | 0 | 120 | 0 | 0 | 4 | 120 | 54 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.6 | 8239.999999999993 | 41.6 | 3334.5 | -480.0000000000073 | 1866.0206185566938 | 1212 | 10.1 | 85.29028959233953 | 1932.8 | 1134.020618556701 | 13.220618556693807 | 80 |  | 14.027777777777779 | 1212 | 2017 | 11 | 2017_11_Asomata_english.xlsx
24 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 54 | 0 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.7 | 8480.000000000015 | 41.45 | 3159 | 240.00000000002183 | 2125.70512820515 | 757.5 | 10.1 | 85.09054652537853 | 1910.15 | 1128.2051282051282 | 215.5551282051499 | 0 |  | 8.76736111111111 | 757.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
25 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85 | 9200.000000000007 | 41.7 | 3451.5 | 719.9999999999927 | 1519.9999999999927 | 800 | 10 | 85.34186046511628 | 1306.7 | 0 | 213.29999999999268 | 0 |  | 9.25925925925926 | 800 | 2017 | 11 | 2017_11_Asomata_english.xlsx
26 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 35 | 0 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85.2 | 9680.000000000015 | 41.8 | 3568.5 | 480.0000000000073 | 1288.0000000000073 | 808 | 10.1 | 84.10570223689035 | 1255.6 | 0 | 92.40000000000737 | 60 |  | 9.351851851851851 | 808 | 2017 | 11 | 2017_11_Asomata_english.xlsx
27 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 54 | 1.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 85.3 | 9920 | 41.312 | 2997.54 | 239.99999999998545 | 2760.9234693877406 | 837.25 | 9.85 | 86.04119529665539 | 2634.95 | 1683.673469387755 | 125.9734693877408 | 0 |  | 9.690393518518519 | 837.25 | 2017 | 11 | 2017_11_Asomata_english.xlsx
28 | 0 | 235 | 235 | 0 | 0 | 4 | 235 | 55 | 0 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.25 | 9800.000000000007 | 41.84 | 3615.3 | -119.99999999999272 | 3418.4484536082546 | 2373.5 | 10.1 | 84.00847021118297 | 3189.9 | 1164.9484536082473 | 228.54845360825448 | 0 |  | 27.471064814814813 | 2373.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
29 | 250 | 0 | 250 | 0 | 0 | 3 | 250 | 55 | 5.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.05 | 9320 | 41.642 | 3383.6400000000085 | -480.0000000000073 | 2044.9999999999927 | 2525 | 10.1 | 84.3987534641966 | 1898 | 0 | 206.99999999999272 | 60 |  | 29.224537037037038 | 2525 | 2017 | 11 | 2017_11_Asomata_english.xlsx
30 | 0 | 235 | 235 | 0 | 0 | 5 | 235 | 54 | 0 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.2 | 9680.000000000015 | 41.621 | 3359.07 | 360.00000000001455 | 2686.5000000000146 | 2326.5 | 9.9 | 85.8048073325851 | 2464.2 | 0 | 222.30000000001428 | 0 |  | 26.927083333333332 | 2326.5 | 2017 | 11 | 2017_11_Asomata_english.xlsx
1 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85.1 | 9439.999999999993 | 40.721 | 2306.0699999999933 | -240.00000000002183 | 8187.712765957425 | 757.5 | 10.1 | 84.30084307734718 | 8073.8 | 7670.212765957447 | 173.91276595742602 | 60 |  | 8.76736111111111 | 757.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
2 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.35 | 10040 | 40.98 | 2609.1 | 600 | 5990.478723404255 | 757.5 | 10.1 | 83.81467904575926 | 5949.5 | 4632.978723404255 | 100.9787234042551 | 60 |  | 8.76736111111111 | 757.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
3 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 82.8 | 3959.9999999999936 | 40.9 | 2515.5 | -6080 | 3739.1409017713386 | 656.5 | 10.1 | 89.0530964861192 | 3759 | 9162.640901771338 | 40.14090177133858 | 60 |  | 7.59837962962963 | 656.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
4 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 83.75 | 6200.000000000007 | 41.13 | 2784.6 | 2240.0000000000136 | 6474.6153846153975 | 850 | 10 | 87.89700598802395 | 6177 | 3384.6153846153843 | 297.6153846153975 | 0 |  | 9.837962962962964 | 850 | 2017 | 12 | 2017_12_Asomata_english.xlsx
5 | 45 | 0 | 45 | 0 | 0 | 5 | 45 | 45 | 1.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.1 | 7039.999999999993 | 41.1 | 2749.5 | 839.9999999999854 | 3327.471204188467 | 477 | 10.6 | 82.23233092815849 | 3145.8 | 2010.4712041884816 | 181.67120418846707 | 0 |  | 5.520833333333333 | 477 | 2017 | 12 | 2017_12_Asomata_english.xlsx
6 | 0 | 85 | 85 | 0 | 0 | 2 | 85 | 55 | 0 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.45 | 7880.000000000014 | 41.111 | 2762.3699999999935 | 840.0000000000209 | 4531.762820512841 | 871.25 | 10.25 | 84.33910770203109 | 4460.3 | 2820.5128205128203 | 71.46282051284106 | 0 |  | 10.083912037037036 | 871.25 | 2017 | 12 | 2017_12_Asomata_english.xlsx
7 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 55 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.6 | 8239.999999999993 | 41.4 | 3100.5 | 359.9999999999791 | 1420.499999999979 | 1060.5 | 10.1 | 85.29028959233953 | 1250.6 | 0 | 169.89999999997895 | 0 |  | 12.274305555555555 | 1060.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
8 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.7 | 8480.000000000015 | 41.422 | 3126.24 | 240.00000000002183 | 922.5000000000218 | 682.5 | 9.75 | 88.1450789647511 | 767.35 | 0 | 155.1500000000218 | 0 |  | 7.899305555555555 | 682.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
9 | 110 | 0 | 110 | 0 | 0 | 3 | 110 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85.1 | 9439.999999999993 | 42 | 3802.5 | 959.9999999999782 | 2070.999999999978 | 1111 | 10.1 | 84.30084307734718 | 1854.2 | 0 | 216.79999999997813 | 0 |  | 12.858796296296296 | 1111 | 2017 | 12 | 2017_12_Asomata_english.xlsx
10 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.1 | 7039.999999999993 | 41.86 | 3638.7 | -2400 | 1567.6382978723404 | 707 | 10.1 | 86.3032383998495 | 1576.8 | 3260.6382978723404 | 50.83829787234049 | 60 |  | 8.18287037037037 | 707 | 2017 | 12 | 2017_12_Asomata_english.xlsx
11 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 36 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.25 | 7400.000000000007 | 41.6 | 3334.5 | 360.00000000001455 | 993.7500000000146 | 633.75 | 9.75 | 89.08390229100289 | 745 | 0 | 248.75000000001455 | 0 |  | 7.335069444444445 | 633.75 | 2017 | 12 | 2017_12_Asomata_english.xlsx
12 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.3 | 7520 | 41.563 | 3291.21 | 119.99999999999272 | 769.9999999999927 | 650 | 10 | 86.75413711583924 | 705.6 | 0 | 64.39999999999281 | 0 |  | 7.523148148148148 | 650 | 2017 | 12 | 2017_12_Asomata_english.xlsx
13 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 55 | 1.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.55 | 8120 | 41.74 | 3498.3 | 600 | 1250 | 650 | 10 | 86.24441833137486 | 1161.3 | 0 | 88.7 | 0 |  | 7.523148148148148 | 650 | 2017 | 12 | 2017_12_Asomata_english.xlsx
14 | 0 | 65 | 65 | 0 | 0 | 2 | 65 | 35 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.6 | 8239.999999999993 | 41.537 | 3260.79 | 119.99999999999272 | 769.9999999999927 | 650 | 10 | 86.14319248826293 | 661.5 | 0 | 108.49999999999272 | 0 |  | 7.523148148148148 | 650 | 2017 | 12 | 2017_12_Asomata_english.xlsx
15 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.65 | 8360.00000000002 | 41.5 | 3217.5 | 120.00000000002728 | 820.0000000000273 | 700 | 10 | 86.04220398593199 | 677.95 | 0 | 142.05000000002724 | 0 |  | 8.101851851851851 | 700 | 2017 | 12 | 2017_12_Asomata_english.xlsx
16 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.85 | 8839.999999999993 | 41.351 | 3043.17 | 479.9999999999727 | 1123.4999999999727 | 643.5 | 9.9 | 86.50566340181277 | 923.8 | 0 | 199.69999999997265 | 0 |  | 7.447916666666667 | 643.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
17 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 17 | 84.9 | 8960.00000000002 | 41.384 | 3081.78 | 120.00000000002728 | 855.0000000000273 | 735 | 9.8 | 87.2865230008087 | 762.2 | 0 | 92.80000000002724 | 0 |  | 8.506944444444445 | 735 | 2017 | 12 | 2017_12_Asomata_english.xlsx
18 | 105 | 255 | 360 | 0 | 0 | 3 | 360 | 70 | 2.9499999999970896 | 6.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.6 | 8239.999999999993 | 41.58 | 3311.1 | -720.0000000000273 | 2879.9999999999727 | 3600 | 10 | 86.14319248826293 | 2775 | 0 | 104.99999999997272 | 0 |  | 41.666666666666664 | 3600 | 2017 | 12 | 2017_12_Asomata_english.xlsx
19 | 285 | 140 | 425 | 0 | 0 | 3 | 425 | 108 | 7.349999999998545 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.5 | 8000.000000000007 | 41.611 | 3347.3699999999935 | -239.99999999998545 | 4052.5000000000146 | 4292.5 | 10.1 | 85.49097262667443 | 3989.7 | 0 | 122.80000000001428 | 60 |  | 49.68171296296296 | 4292.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
20 | 0 | 130 | 130 | 0 | 0 | 3 | 130 | 54 | 0 | 2.6499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.7 | 8480.000000000015 | 41.652 | 3395.34 | 480.0000000000073 | 1793.0000000000073 | 1313 | 10.1 | 85.09054652537853 | 1540.3 | 0 | 252.70000000000732 | 0 |  | 15.19675925925926 | 1313 | 2017 | 12 | 2017_12_Asomata_english.xlsx
21 | 95 | 0 | 95 | 0 | 0 | 0 | 95 | 35 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85 | 9200.000000000007 | 41.3 | 2983.5 | 719.9999999999927 | 1679.4999999999927 | 959.5 | 10.1 | 84.49689154962007 | 1642.5 | 0 | 96.99999999999272 | 60 |  | 11.105324074074074 | 959.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
22 | 0 | 315 | 315 | 0 | 0 | 8 | 315 | 55 | 0 | 7.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85 | 9200.000000000007 | 41.728 | 3484.26 | 0 | 3181.5 | 3181.5 | 10.1 | 84.49689154962007 | 3102.5 | 0 | 139 | 60 |  | 36.822916666666664 | 3181.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
23 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 55 | 2.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.15 | 9560.00000000002 | 41.438 | 3144.96 | 360.00000000001273 | 1536.0000000000127 | 1176 | 9.8 | 86.78080734031734 | 1332 | 0 | 204.00000000001273 | 0 |  | 13.61111111111111 | 1176 | 2017 | 12 | 2017_12_Asomata_english.xlsx
24 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 40 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.2 | 9680.000000000015 | 41.31 | 2995.2 | 119.99999999999454 | 1050.9999999999945 | 931 | 9.8 | 86.68036659108087 | 875.8 | 0 | 175.1999999999946 | 0 |  | 10.775462962962964 | 931 | 2017 | 12 | 2017_12_Asomata_english.xlsx
25 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.2 | 9680.000000000015 | 41.46 | 3170.7 | 0 | 783.75 | 783.75 | 10.45 | 81.28876484139641 | 708.1 | 0 | 75.65 | 0 |  | 9.071180555555555 | 783.75 | 2017 | 12 | 2017_12_Asomata_english.xlsx
26 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85 | 9200.000000000007 | 41.62 | 3357.9 | -480.0000000000073 | 1508.9183673469315 | 693 | 9.9 | 86.20389945971341 | 1480 | 1295.9183673469388 | 28.918367346931518 | 0 |  | 8.020833333333334 | 693 | 2017 | 12 | 2017_12_Asomata_english.xlsx
27 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 85 | 9200.000000000007 | 41.5 | 3217.5 | 0 | 650 | 650 | 10 | 85.34186046511628 | 657 | 0 | 53 | 60 |  | 7.523148148148148 | 650 | 2017 | 12 | 2017_12_Asomata_english.xlsx
28 | 0 | 120 | 120 | 0 | 0 | 3 | 120 | 35 | 0 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.1 | 9439.999999999993 | 41.97 | 3767.4 | 239.99999999998545 | 1421.9999999999854 | 1182 | 9.85 | 86.44045838387885 | 1080.25 | 0 | 341.74999999998545 | 0 |  | 13.680555555555555 | 1182 | 2017 | 12 | 2017_12_Asomata_english.xlsx
29 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.15 | 9560.00000000002 | 41.75 | 3510 | 120.00000000002728 | 813.0000000000273 | 693 | 9.9 | 85.90423352879898 | 630 | 0 | 183.00000000002728 | 0 |  | 8.020833333333334 | 693 | 2017 | 12 | 2017_12_Asomata_english.xlsx
30 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 35 | 0 | 2.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.4 | 10160 | 41.7 | 3451.5 | 600 | 5187.095744680852 | 1060.5 | 10.1 | 83.71811835561435 | 5110 | 3526.595744680851 | 77.09574468085157 | 0 |  | 12.274305555555555 | 1060.5 | 2017 | 12 | 2017_12_Asomata_english.xlsx
31 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 85.1 | 9439.999999999993 | 41.4 | 3100.5 | -720.0000000000273 | 3603.1666666666397 | 844 | 10.55 | 80.70507251954564 | 3577 | 3479.166666666667 | 86.16666666663968 | 60 |  | 9.768518518518519 | 844 | 2017 | 12 | 2017_12_Asomata_english.xlsx
1 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 85.05 | 9320 | 41.54 | 3264.3 | -119.99999999999272 | 5875.041666666673 | 656.5 | 10.1 | 84.3987534641966 | 5861.9 | 5338.541666666666 | 73.1416666666737 | 60 |  | 7.59837962962963 | 656.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
2 | 0 | 145 | 145 | 0 | 0 | 4 | 145 | 35 | 0 | 4.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.85 | 8839.999999999993 | 42.059 | 3871.53 | -480.0000000000073 | 1580.2446808510565 | 1464.5 | 10.1 | 84.79267996811352 | 1618.8 | 595.7446808510638 | 21.444680851056546 | 60 |  | 16.95023148148148 | 1464.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
3 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85 | 9200.000000000007 | 41.61 | 3346.2 | 360.00000000001455 | 1010.0000000000146 | 650 | 10 | 85.34186046511628 | 808.5 | 0 | 201.50000000001455 | 0 |  | 7.523148148148148 | 650 | 2018 | 1 | 2018_01_Asomata_english.xlsx
4 | 0 | 105 | 105 | 0 | 0 | 4 | 105 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85 | 9200.000000000007 | 41.9 | 3685.5 | 0 | 4085.8974358974356 | 1050 | 10 | 85.34186046511628 | 3759.5 | 3035.8974358974356 | 326.39743589743557 | 0 |  | 12.152777777777779 | 1050 | 2018 | 1 | 2018_01_Asomata_english.xlsx
5 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 40 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.15 | 9560.00000000002 | 41.9 | 3685.5 | 360.00000000001273 | 1000.2500000000127 | 640.25 | 9.85 | 86.34029562792995 | 862.5 | 0 | 137.75000000001273 | 0 |  | 7.410300925925926 | 640.25 | 2018 | 1 | 2018_01_Asomata_english.xlsx
6 | 80 | 45 | 125 | 0 | 0 | 4 | 125 | 45 | 2.099999999998545 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 85 | 9200.000000000007 | 41.753 | 3513.51 | -360.00000000001273 | 889.9999999999873 | 1250 | 10 | 85.34186046511628 | 908.9 | 0 | 41.09999999998729 | 60 |  | 14.467592592592593 | 1250 | 2018 | 1 | 2018_01_Asomata_english.xlsx
7 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 85.15 | 9560.00000000002 | 41.4 | 3100.5 | 360.00000000001273 | 997.0000000000127 | 637 | 9.8 | 86.78080734031734 | 797.15 | 0 | 199.85000000001276 | 0 |  | 7.372685185185185 | 637 | 2018 | 1 | 2018_01_Asomata_english.xlsx
8 | 240 | 0 | 240 | 0 | 0 | 4 | 240 | 55 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 85.25 | 9800.000000000007 | 41.69 | 3439.8 | 239.99999999998727 | 2603.9999999999873 | 2364 | 9.85 | 86.14066488659371 | 2322.6 | 0 | 281.39999999998736 | 0 |  | 27.36111111111111 | 2364 | 2018 | 1 | 2018_01_Asomata_english.xlsx
9 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 35 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.1 | 9439.999999999993 | 41.462 | 3173.0400000000086 | -360.00000000001455 | 1407.4999999999854 | 1767.5 | 10.1 | 84.30084307734718 | 1418.55 | 0 | 18.949999999985494 | 30 |  | 20.457175925925927 | 1767.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
10 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 55 | 0 | 1.3499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85.1 | 9439.999999999993 | 41.48 | 3194.1 | 0 | 4141.0360824742265 | 656.5 | 10.1 | 84.30084307734718 | 4174.8 | 3484.5360824742265 | 26.23608247422635 | 60 |  | 7.59837962962963 | 656.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
11 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 38 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85.3 | 9920 | 41.7 | 3451.5 | 480.0000000000073 | 4818.680851063837 | 844 | 10.55 | 80.33230082199577 | 4584.4 | 3494.68085106383 | 234.28085106383696 | 0 |  | 9.768518518518519 | 844 | 2018 | 1 | 2018_01_Asomata_english.xlsx
12 | 0 | 190 | 190 | 0 | 0 | 4 | 190 | 55 | 0 | 4.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.2 | 9680.000000000015 | 41.701 | 3452.67 | -239.99999999998545 | 1660.0000000000146 | 1900 | 10 | 84.94675925925925 | 1547.6 | 0 | 112.40000000001464 | 0 |  | 21.99074074074074 | 1900 | 2018 | 1 | 2018_01_Asomata_english.xlsx
13 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 85.3 | 9920 | 40.87 | 2480.4 | 239.99999999998545 | 1098.4999999999854 | 858.5 | 10.1 | 83.91146273980748 | 1036.6 | 0 | 121.89999999998554 | 60 |  | 9.936342592592593 | 858.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
14 | 0 | 510 | 510 | 0 | 0 | 3 | 510 | 54 | 0 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.25 | 7400.000000000007 | 41.63 | 3369.6 | -2519.9999999999927 | 7668.234042553198 | 5151 | 10.1 | 85.99683637002754 | 7621.2 | 5037.234042553191 | 47.03404255319856 | 0 |  | 59.61805555555556 | 5151 | 2018 | 1 | 2018_01_Asomata_english.xlsx
15 | 535 | 130 | 665 | 0 | 0 | 4 | 665 | 108 | 10.450000000004366 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84.6 | 8239.999999999993 | 41.6 | 3334.5 | 839.9999999999854 | 7556.499999999985 | 6716.5 | 10.1 | 85.29028959233953 | 7397.85 | 0 | 218.64999999998508 | 60 |  | 77.73726851851852 | 6716.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
16 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 35 | 0 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.1 | 7039.999999999993 | 40.8 | 2398.5 | -1200 | 2166.3829787234044 | 1010 | 10.1 | 86.3032383998495 | 2117 | 2356.3829787234044 | 109.38297872340445 | 60 |  | 11.689814814814815 | 1010 | 2018 | 1 | 2018_01_Asomata_english.xlsx
17 | 215 | 0 | 215 | 0 | 0 | 6 | 215 | 35 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.5 | 8000.000000000007 | 40.97 | 2597.4 | 960.0000000000146 | 4865.319148936185 | 2150 | 10 | 86.34588235294117 | 4708.5 | 1755.3191489361702 | 156.81914893618523 | 0 |  | 24.88425925925926 | 2150 | 2018 | 1 | 2018_01_Asomata_english.xlsx
18 | 115 | 215 | 330 | 0 | 0 | 4 | 330 | 110 | 2.7999999999956344 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.35 | 7639.999999999993 | 41.742 | 3500.64 | -360.00000000001455 | 2972.9999999999854 | 3333 | 10.1 | 85.79377418261309 | 2890.8 | 0 | 82.19999999998572 | 0 |  | 38.576388888888886 | 3333 | 2018 | 1 | 2018_01_Asomata_english.xlsx
19 | 175 | 0 | 175 | 0 | 0 | 4 | 175 | 55 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.6 | 8239.999999999993 | 42.069 | 3883.2300000000064 | 600 | 2367.5 | 1767.5 | 10.1 | 85.29028959233953 | 2204.6 | 0 | 162.9 | 0 |  | 20.457175925925927 | 1767.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
20 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 84.8 | 8720 | 41.6 | 3334.5 | 480.0000000000073 | 1849.2893401015301 | 750 | 10 | 85.74065420560747 | 1646.4 | 619.2893401015228 | 202.88934010153025 | 0 |  | 8.680555555555555 | 750 | 2018 | 1 | 2018_01_Asomata_english.xlsx
21 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.1 | 9439.999999999993 | 41.22 | 2889.9 | 719.9999999999927 | 1402.4999999999927 | 682.5 | 9.75 | 87.32702718781606 | 1348.45 | 0 | 54.04999999999268 | 0 |  | 7.899305555555555 | 682.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
22 | 330 | 0 | 330 | 0 | 0 | 4 | 330 | 55 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.5 | 8000.000000000007 | 41.8 | 3568.5 | -1439.9999999999854 | 4116.41025641027 | 3300 | 10 | 86.34588235294117 | 4108.65 | 2256.4102564102564 | 67.76025641027081 | 60 |  | 38.19444444444444 | 3300 | 2018 | 1 | 2018_01_Asomata_english.xlsx
23 | 155 | 0 | 155 | 0 | 0 | 6 | 155 | 55 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.8 | 8720 | 41.55 | 3276 | 719.9999999999927 | 2231.2499999999927 | 1511.25 | 9.75 | 87.93913251857178 | 1969.8 | 0 | 261.44999999999277 | 0 |  | 17.491319444444443 | 1511.25 | 2018 | 1 | 2018_01_Asomata_english.xlsx
24 | 315 | 245 | 560 | 0 | 0 | 3 | 560 | 108 | 6.799999999995634 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 84.95 | 9080.000000000015 | 41.652 | 3395.34 | 360.00000000001455 | 5960.000000000015 | 5600 | 10 | 85.44121071012806 | 5927.6 | 0 | 92.4000000000151 | 60 |  | 64.81481481481481 | 5600 | 2018 | 1 | 2018_01_Asomata_english.xlsx
25 | 165 | 380 | 545 | 0 | 0 | 4 | 545 | 110 | 3.25 | 7.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 25 | 84.1 | 7039.999999999993 | 41.601 | 3335.67 | -2040.0000000000218 | 7087.421052631556 | 5559 | 10.2 | 85.45712821945884 | 7094.47 | 3568.421052631579 | 52.951052631556195 | 60 |  | 64.34027777777777 | 5559 | 2018 | 1 | 2018_01_Asomata_english.xlsx
26 | 60 | 205 | 265 | 0 | 0 | 3 | 265 | 110 | 1.4000000000014552 | 4.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.95 | 9080.000000000015 | 41.89 | 3673.8 | 2040.0000000000218 | 4690.000000000022 | 2650 | 10 | 85.44121071012806 | 4476.15 | 0 | 213.8500000000222 | 0 |  | 30.671296296296298 | 2650 | 2018 | 1 | 2018_01_Asomata_english.xlsx
27 | 145 | 120 | 265 | 0 | 0 | 3 | 265 | 70 | 3.900000000001455 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.8 | 8720 | 41.85 | 3627 | -360.00000000001455 | 2316.4999999999854 | 2676.5 | 10.1 | 84.89173683723513 | 2292.2 | 0 | 24.29999999998563 | 0 |  | 30.97800925925926 | 2676.5 | 2018 | 1 | 2018_01_Asomata_english.xlsx
28 | 0 | 225 | 225 | 0 | 0 | 5 | 225 | 55 | 0 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.6 | 8239.999999999993 | 41.929 | 3719.4300000000067 | -480.0000000000073 | 1724.9999999999927 | 2205 | 9.8 | 87.90121682475808 | 1653.9 | 0 | 71.09999999999263 | 0 |  | 25.520833333333332 | 2205 | 2018 | 1 | 2018_01_Asomata_english.xlsx
29 | 265 | 115 | 380 | 0 | 0 | 3 | 380 | 110 | 5.5 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.95 | 9080.000000000015 | 41.78 | 3545.1 | 840.0000000000218 | 4583.000000000022 | 3743 | 9.85 | 86.74234589860717 | 4402.5 | 0 | 180.50000000002183 | 0 |  | 43.32175925925926 | 3743 | 2018 | 1 | 2018_01_Asomata_english.xlsx
30 | 80 | 165 | 245 | 0 | 0 | 3 | 245 | 70 | 1.8499999999985448 | 3.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 85.1 | 9439.999999999993 | 41.78 | 3545.1 | 359.9999999999782 | 2809.999999999978 | 2450 | 10 | 85.14385150812066 | 2649.2 | 0 | 160.79999999997835 | 0 |  | 28.35648148148148 | 2450 | 2018 | 1 | 2018_01_Asomata_english.xlsx
31 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 35 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 85.2 | 9680.000000000015 | 41.15 | 2808 | 240.00000000002183 | 1390.0000000000218 | 1150 | 10 | 84.94675925925925 | 1222.5 | 0 | 167.50000000002183 | 0 |  | 13.310185185185185 | 1150 | 2018 | 1 | 2018_01_Asomata_english.xlsx
1 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85 | 9200.000000000007 | 40.45 | 1989.0000000000055 | -480.0000000000073 | 1069.3061224489722 | 784 | 9.8 | 87.08353108685334 | 906 | 765.3061224489795 | 163.30612244897225 | 0 |  | 9.074074074074074 | 784 | 2018 | 2 | 2018_02_Asomata_english.xlsx
2 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 35 | 0 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85 | 9200.000000000007 | 40.6 | 2164.5 | 0 | 2404.8684210526317 | 757.5 | 10.1 | 84.49689154962007 | 2388.75 | 1647.3684210526314 | 76.11842105263167 | 60 |  | 8.76736111111111 | 757.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
3 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.3 | 7520 | 40.88 | 2492.1 | -1680.0000000000073 | 1258.5512820512745 | 656.5 | 10.1 | 85.89518526320718 | 1139.6 | 2282.0512820512818 | 178.95128205127435 | 60 |  | 7.59837962962963 | 656.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
4 | 0 | 145 | 145 | 0 | 0 | 4 | 145 | 35 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.95 | 9080.000000000015 | 41.72 | 3474.9 | 1560.0000000000146 | 7011.420212765972 | 1515.25 | 10.45 | 81.76192412452446 | 6840.1 | 3936.1702127659573 | 231.32021276597152 | 60 |  | 17.53761574074074 | 1515.25 | 2018 | 2 | 2018_02_Asomata_english.xlsx
5 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85 | 9200.000000000007 | 41.69 | 3439.8 | 119.99999999999272 | 805.9999999999927 | 686 | 9.8 | 87.08353108685334 | 692.85 | 0 | 113.1499999999927 | 0 |  | 7.939814814814815 | 686 | 2018 | 2 | 2018_02_Asomata_english.xlsx
6 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 35 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 85.1 | 9439.999999999993 | 41.73 | 3486.6 | 239.99999999998545 | 1552.9999999999854 | 1313 | 10.1 | 84.30084307734718 | 1460 | 0 | 92.99999999998545 | 0 |  | 15.19675925925926 | 1313 | 2018 | 2 | 2018_02_Asomata_english.xlsx
7 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 35 | 3.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.95 | 9080.000000000015 | 41.2 | 2866.5 | -359.9999999999782 | 852.0000000000218 | 1212 | 10.1 | 84.59525812883966 | 751.9 | 0 | 100.10000000002185 | 0 |  | 14.027777777777779 | 1212 | 2018 | 2 | 2018_02_Asomata_english.xlsx
8 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.9 | 8960.00000000002 | 41.32 | 3006.9 | -119.99999999999454 | 587.0000000000055 | 707 | 10.1 | 84.6938540007847 | 532.9 | 0 | 54.10000000000548 | 0 |  | 8.18287037037037 | 707 | 2018 | 2 | 2018_02_Asomata_english.xlsx
9 | 270 | 0 | 270 | 0 | 0 | 5 | 270 | 55 | 5.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.85 | 8839.999999999993 | 41.599 | 3333.33 | -120.00000000002728 | 2539.4999999999727 | 2659.5 | 9.85 | 86.94477844446158 | 2278.5 | 0 | 260.9999999999727 | 0 |  | 30.78125 | 2659.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
10 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 54 | 0 | 1.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85 | 9200.000000000007 | 41.2 | 2866.5 | 360.00000000001455 | 1067.0000000000146 | 707 | 10.1 | 84.49689154962007 | 817.6 | 0 | 309.40000000001453 | 60 |  | 8.18287037037037 | 707 | 2018 | 2 | 2018_02_Asomata_english.xlsx
11 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85.05 | 9320 | 41.2 | 2866.5 | 119.99999999999272 | 2087.415803108801 | 791.25 | 10.55 | 80.7988066339702 | 2029.4 | 1176.1658031088082 | 58.01580310880104 | 0 |  | 9.15798611111111 | 791.25 | 2018 | 2 | 2018_02_Asomata_english.xlsx
12 | 200 | 265 | 465 | 0 | 0 | 4 | 465 | 70 | 5.599999999998545 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 12 | 84.85 | 8839.999999999993 | 41.577 | 3307.59 | -480.0000000000073 | 4216.499999999993 | 4696.5 | 10.1 | 84.79267996811352 | 4035.15 | 0 | 181.3499999999931 | 0 |  | 54.357638888888886 | 4696.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
13 | 225 | 265 | 490 | 0 | 0 | 4 | 490 | 80 | 6 | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.45 | 7880.000000000014 | 41.54 | 3264.3 | -959.9999999999791 | 3964.500000000021 | 4924.5 | 10.05 | 86.01749790505657 | 3796.2 | 0 | 168.30000000002065 | 0 |  | 56.99652777777778 | 4924.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
14 | 90 | 340 | 430 | 0 | 0 | 3 | 430 | 70 | 2.5500000000029104 | 8.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.1 | 7039.999999999993 | 41.599 | 3333.33 | -840.0000000000209 | 3502.999999999979 | 4343 | 10.1 | 86.3032383998495 | 3518.3 | 0 | 24.699999999979354 | 40 |  | 50.2662037037037 | 4343 | 2018 | 2 | 2018_02_Asomata_english.xlsx
15 | 130 | 0 | 130 | 0 | 0 | 4 | 130 | 35 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.4 | 7760.00000000002 | 41.56 | 3287.7 | 720.0000000000273 | 1987.5000000000273 | 1267.5 | 9.75 | 88.76874697629414 | 1747.5 | 0 | 240.00000000002728 | 0 |  | 14.67013888888889 | 1267.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
16 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 40 | 0 | 1.6499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.45 | 7880.000000000014 | 41.27 | 2948.4 | 119.99999999999363 | 854.9999999999936 | 735 | 9.8 | 88.21182183120597 | 661.2 | 0 | 193.7999999999937 | 0 |  | 8.506944444444445 | 735 | 2018 | 2 | 2018_02_Asomata_english.xlsx
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.6 | 8239.999999999993 | 41.33 | 3018.6 | 359.9999999999791 | 1094.999999999979 | 735 | 9.8 | 87.90121682475808 | 968.5 | 0 | 126.49999999997908 | 0 |  | 8.506944444444445 | 735 | 2018 | 2 | 2018_02_Asomata_english.xlsx
18 | 0 | 130 | 130 | 0 | 0 | 3 | 130 | 35 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.7 | 8480.000000000015 | 41.807 | 3576.69 | 240.00000000002183 | 1553.0000000000218 | 1313 | 10.1 | 85.09054652537853 | 1241 | 0 | 312.0000000000218 | 0 |  | 15.19675925925926 | 1313 | 2018 | 2 | 2018_02_Asomata_english.xlsx
19 | 105 | 0 | 105 | 0 | 0 | 4 | 105 | 54 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.7 | 8480.000000000015 | 41.55 | 3276 | 0 | 1029 | 1029 | 9.8 | 87.6953591741146 | 800.3 | 0 | 228.7 | 0 |  | 11.909722222222221 | 1029 | 2018 | 2 | 2018_02_Asomata_english.xlsx
20 | 0 | 215 | 215 | 0 | 0 | 4 | 215 | 54 | 0 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.8 | 8720 | 41.85 | 3627 | 239.99999999998545 | 2368.4999999999854 | 2128.5 | 9.9 | 86.60672141980554 | 2000.75 | 0 | 367.74999999998545 | 0 |  | 24.635416666666668 | 2128.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
21 | 135 | 0 | 135 | 0 | 0 | 5 | 135 | 55 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.85 | 8839.999999999993 | 41.67 | 3416.4 | 119.99999999999272 | 1537.4999999999927 | 1417.5 | 10.5 | 81.5624826359949 | 1569.5 | 0 | 27.999999999992724 | 60 |  | 16.40625 | 1417.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
22 | 395 | 470 | 865 | 0 | 0 | 4 | 865 | 110 | 7.599999999998545 | 7.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84.3 | 7520 | 41.46 | 3170.7 | -1319.9999999999927 | 7416.500000000007 | 8736.5 | 10.1 | 85.89518526320718 | 7219.7 | 0 | 196.80000000000746 | 0 |  | 101.11689814814815 | 8736.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
23 | 95 | 315 | 410 | 0 | 0 | 4 | 410 | 90 | 2 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 23 | 83.9 | 6560.00000000002 | 40.656 | 2230.02 | -959.99999999998 | 3181.00000000002 | 4141 | 10.1 | 86.71518703182966 | 3139 | 0 | 102.00000000002001 | 60 |  | 47.92824074074074 | 4141 | 2018 | 2 | 2018_02_Asomata_english.xlsx
24 | 175 | 735 | 910 | 0 | 0 | 4 | 910 | 110 | 3.5 | 14.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83.3 | 5120 | 41.81 | 3580.2 | -1440.00000000002 | 7750.99999999998 | 9191 | 10.1 | 87.97497183132359 | 7739.55 | 0 | 71.44999999998072 | 60 |  | 106.37731481481481 | 9191 | 2018 | 2 | 2018_02_Asomata_english.xlsx
25 | 870 | 0 | 870 | 0 | 0 | 5 | 870 | 55 | 15.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.55 | 5720 | 41.9655 | 3762.1350000000025 | 600 | 9387 | 8787 | 10.1 | 87.44563987084629 | 9396 | 0 | 51 | 60 |  | 101.70138888888889 | 8787 | 2018 | 2 | 2018_02_Asomata_english.xlsx
26 | 170 | 465 | 635 | 0 | 0 | 3 | 635 | 110 | 3.099999999998545 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.45 | 7880.000000000014 | 41.3 | 2983.5 | 2160.0000000000136 | 8573.500000000015 | 6413.5 | 10.1 | 85.5916687075068 | 8263.6 | 0 | 369.900000000016 | 60 |  | 74.23032407407408 | 6413.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
27 | 285 | 710 | 995 | 0 | 0 | 5 | 995 | 108 | 5.900000000001455 | 14.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.2 | 7280.000000000014 | 41.602 | 3336.84 | -600 | 9350 | 9950 | 10 | 86.95971563981043 | 9208.2 | 0 | 141.79999999999927 | 0 |  | 115.16203703703704 | 9950 | 2018 | 2 | 2018_02_Asomata_english.xlsx
28 | 180 | 625 | 805 | 0 | 0 | 4 | 805 | 110 | 3.599999999998545 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.65 | 8360.00000000002 | 41.501 | 3218.6699999999937 | 1080.0000000000064 | 9210.500000000007 | 8130.5 | 10.1 | 85.19030097617029 | 9163.5 | 0 | 47.000000000007276 | 0 |  | 94.10300925925925 | 8130.5 | 2018 | 2 | 2018_02_Asomata_english.xlsx
1 | 510 | 505 | 1015 | 0 | 0 | 4 | 1015 | 110 | 10.10000000000582 | 10.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 1 | 84.55 | 8120 | 41.752 | 3512.34 | -240.00000000002 | 9909.99999999998 | 10150 | 10 | 86.24441833137486 | 9525.6 | 0 | 384.39999999998145 | 0 |  | 117.47685185185185 | 10150 | 2018 | 3 | 2018_03_Asomata_english.xlsx
2 | 405 | 655 | 1060 | 0 | 0 | 5 | 1060 | 110 | 8.19999999999709 | 13.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 2 | 83.4 | 5360.00000000002 | 41.379 | 3075.93 | -2759.99999999998 | 7946.00000000002 | 10706 | 10.1 | 87.76247189936385 | 7942.4 | 0 | 63.60000000002037 | 60 |  | 123.91203703703704 | 10706 | 2018 | 3 | 2018_03_Asomata_english.xlsx
3 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 55 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.3 | 5120 | 41.149 | 2806.83 | -240.00000000002 | 1779.99999999998 | 2020 | 10.1 | 87.97497183132359 | 1547.6 | 0 | 292.3999999999801 | 60 |  | 23.37962962962963 | 2020 | 2018 | 3 | 2018_03_Asomata_english.xlsx
4 | 185 | 220 | 405 | 0 | 0 | 4 | 405 | 110 | 4.30000000000291 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.35 | 7639.999999999993 | 42.053 | 3864.5099999999916 | 2519.9999999999927 | 6610.499999999993 | 4090.5 | 10.1 | 85.79377418261309 | 6600.7 | 0 | 69.799999999992 | 60 |  | 47.34375 | 4090.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
5 | 750 | 265 | 1015 | 0 | 0 | 3 | 1015 | 90 | 14.80000000000291 | 5.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.5 | 8000.000000000007 | 41.462 | 3173.0400000000086 | 360.00000000001455 | 10611.5 | 10251.5 | 10.1 | 85.49097262667443 | 10455 | 0 | 156.50000000001455 | 0 |  | 118.65162037037037 | 10251.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
6 | 185 | 350 | 535 | 0 | 0 | 3 | 535 | 110 | 3.849999999998545 | 7.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 83.4 | 5360.00000000002 | 40.54 | 2094.3 | -2639.9999999999873 | 2763.5000000000127 | 5403.5 | 10.1 | 87.76247189936385 | 2613.6 | 0 | 209.90000000001237 | 60 |  | 62.54050925925926 | 5403.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
7 | 700 | 300 | 1000 | 0 | 0 | 6 | 1000 | 100 | 14.849999999998545 | 6.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 7 | 83.1 | 4639.999999999993 | 42.031 | 3838.7699999999936 | -720.0000000000273 | 9379.999999999973 | 10100 | 10.1 | 88.40307388403076 | 9374.25 | 0 | 65.74999999997272 | 60 |  | 116.89814814814815 | 10100 | 2018 | 3 | 2018_03_Asomata_english.xlsx
8 | 385 | 770 | 1155 | 0 | 0 | 4 | 1155 | 108 | 8.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 8 | 83.3 | 5120 | 42.06 | 3872.7 | 480.0000000000073 | 12145.5 | 11665.5 | 10.1 | 87.97497183132359 | 12161.8 | 0 | 43.700000000008004 | 60 |  | 135.01736111111111 | 11665.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
9 | 375 | 580 | 955 | 0 | 0 | 4 | 955 | 100 | 8.94999999999709 | 14.430000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 83.35 | 5239.999999999993 | 41.931 | 3721.7699999999936 | 119.99999999999272 | 9669.999999999993 | 9550 | 10 | 88.7472793228537 | 9603.67 | 0 | 66.32999999999447 | 0 |  | 110.5324074074074 | 9550 | 2018 | 3 | 2018_03_Asomata_english.xlsx
10 | 580 | 650 | 1230 | 0 | 0 | 4 | 1230 | 100 | 13.05000000000291 | 14.269999999996799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.35 | 5239.999999999993 | 41.7 | 3451.5 | 0 | 12300 | 12300 | 10 | 88.7472793228537 | 12069.4 | 0 | 230.59999999999854 | 0 |  | 142.36111111111111 | 12300 | 2018 | 3 | 2018_03_Asomata_english.xlsx
11 | 275 | 890 | 1165 | 0 | 0 | 4 | 1165 | 100 | 5.80000000000291 | 18.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 83.3 | 5120 | 41.698 | 3449.16 | -119.99999999999272 | 11646.5 | 11766.5 | 10.1 | 87.97497183132359 | 11658.1 | 0 | 48.40000000000691 | 60 |  | 136.18634259259258 | 11766.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
12 | 420 | 580 | 1000 | 0 | 0 | 5 | 1000 | 100 | 8.69999999999709 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 83.7 | 6080.000000000014 | 41.421 | 3125.07 | 960.0000000000136 | 11060 | 10100 | 10.1 | 87.13108720944037 | 11070.4 | 0 | 49.6000000000131 | 60 |  | 116.89814814814815 | 10100 | 2018 | 3 | 2018_03_Asomata_english.xlsx
13 | 760 | 545 | 1305 | 0 | 0 | 4 | 1305 | 100 | 17.30000000000291 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 82.75 | 3850 | 41.903 | 3689.01 | -2230.0000000000136 | 10820 | 13050 | 10 | 90.05398773006135 | 10767 | 0 | 52.99999999998545 | 0 |  | 151.04166666666666 | 13050 | 2018 | 3 | 2018_03_Asomata_english.xlsx
14 | 255 | 770 | 1025 | 0 | 0 | 4 | 1025 | 90 | 5.799999999995634 | 16.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83 | 4400 | 41.749 | 3508.8300000000063 | 550 | 11312.5 | 10762.5 | 10.5 | 85.24274099883856 | 11256.95 | 0 | 115.54999999999927 | 60 |  | 124.56597222222223 | 10762.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
15 | 755 | 100 | 855 | 0 | 0 | 4 | 855 | 100 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 83.5 | 5600.000000000007 | 41.602 | 3336.84 | 1200.0000000000073 | 9835.500000000007 | 8635.5 | 10.1 | 87.55099606346177 | 9774.05 | 0 | 121.45000000000618 | 60 |  | 99.94791666666667 | 8635.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
16 | 390 | 480 | 870 | 0 | 0 | 4 | 870 | 110 | 8.80000000000291 | 10.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 16 | 82.5 | 3300 | 41.822 | 3594.2400000000084 | -2300.0000000000073 | 6617.499999999993 | 8917.5 | 10.25 | 88.3998795543511 | 6636 | 0 | 41.499999999992724 | 60 |  | 103.21180555555556 | 8917.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
17 | 805 | 230 | 1035 | 0 | 0 | 4 | 1035 | 100 | 17.099999999998545 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 83.6 | 5839.999999999993 | 41.998 | 3800.16 | 2539.9999999999927 | 12890 | 10350 | 10 | 88.21394230769232 | 12775.6 | 0 | 114.39999999999236 | 0 |  | 119.79166666666667 | 10350 | 2018 | 3 | 2018_03_Asomata_english.xlsx
18 | 135 | 815 | 950 | 0 | 0 | 3 | 950 | 80 | 3.25 | 16.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 83.5 | 5600.000000000007 | 41.712 | 3465.5400000000086 | -239.99999999998545 | 9355.000000000015 | 9595 | 10.1 | 87.55099606346177 | 9095.8 | 0 | 319.2000000000153 | 60 |  | 111.05324074074075 | 9595 | 2018 | 3 | 2018_03_Asomata_english.xlsx
19 | 810 | 160 | 970 | 0 | 0 | 4 | 970 | 108 | 15.55000000000291 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 84 | 6800.000000000007 | 41.631 | 3370.77 | 1200 | 10997 | 9797 | 10.1 | 86.50872230080151 | 10935.1 | 0 | 61.899999999999636 | 0 |  | 113.39120370370371 | 9797 | 2018 | 3 | 2018_03_Asomata_english.xlsx
20 | 265 | 895 | 1160 | 0 | 0 | 5 | 1160 | 108 | 5.19999999999709 | 17.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 83.85 | 6439.999999999993 | 41.59 | 3322.8 | -360.00000000001455 | 11240 | 11600 | 10 | 87.68697729988054 | 11069.1 | 0 | 170.8999999999869 | 0 |  | 134.25925925925927 | 11600 | 2018 | 3 | 2018_03_Asomata_english.xlsx
21 | 860 | 190 | 1050 | 0 | 0 | 3 | 1050 | 108 | 17 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.5 | 5600.000000000007 | 41.832 | 3605.94 | -839.9999999999854 | 9765.000000000015 | 10605 | 10.1 | 87.55099606346177 | 9803.9 | 0 | 21.100000000014916 | 60 |  | 122.74305555555556 | 10605 | 2018 | 3 | 2018_03_Asomata_english.xlsx
22 | 375 | 800 | 1175 | 0 | 0 | 5 | 1175 | 110 | 7.30000000000291 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 83 | 4400 | 41.628 | 3367.26 | -1200.0000000000073 | 10608.75 | 11808.75 | 10.05 | 89.05958014804028 | 10537.6 | 0 | 71.14999999999418 | 0 |  | 136.67534722222226 | 11808.75 | 2018 | 3 | 2018_03_Asomata_english.xlsx
23 | 485 | 505 | 990 | 0 | 0 | 3 | 990 | 109 | 9.89999999999418 | 10.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 23 | 83.3 | 5120 | 41.841 | 3616.47 | 720 | 10719 | 9999 | 10.1 | 87.97497183132359 | 10725 | 0 | 54 | 60 |  | 115.72916666666667 | 9999 | 2018 | 3 | 2018_03_Asomata_english.xlsx
24 | 305 | 795 | 1100 | 0 | 0 | 4 | 1100 | 100 | 7.400000000001455 | 17.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83.8 | 6320 | 41.74 | 3498.3 | 1200 | 12310 | 11110 | 10.1 | 86.9226396323843 | 12007.5 | 0 | 302.5 | 0 |  | 128.58796296296296 | 11110 | 2018 | 3 | 2018_03_Asomata_english.xlsx
25 | 65 | 995 | 1060 | 0 | 0 | 5 | 1060 | 70 | 1.5500000000029104 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 82.65 | 3630.0000000000127 | 41.07 | 2714.4 | -2689.9999999999873 | 8016.000000000013 | 10706 | 10.1 | 89.38170569824509 | 7905.9 | 0 | 170.1000000000131 | 60 |  | 123.91203703703704 | 10706 | 2018 | 3 | 2018_03_Asomata_english.xlsx
26 | 170 | 495 | 665 | 0 | 0 | 4 | 665 | 100 | 3.75 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 83.9 | 6560.00000000002 | 41.6 | 3334.5 | 2930.0000000000073 | 9646.500000000007 | 6716.5 | 10.1 | 86.71518703182966 | 9402.25 | 0 | 304.2500000000073 | 60 |  | 77.73726851851852 | 6716.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
27 | 805 | 415 | 1220 | 0 | 0 | 4 | 1220 | 100 | 17.099999999998545 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 27 | 83.5 | 5600.000000000007 | 41.802 | 3570.84 | -960.0000000000127 | 11362 | 12322 | 10.1 | 87.55099606346177 | 11179.35 | 0 | 182.64999999998872 | 0 |  | 142.61574074074073 | 12322 | 2018 | 3 | 2018_03_Asomata_english.xlsx
28 | 215 | 780 | 995 | 0 | 0 | 4 | 995 | 100 | 4.30000000000291 | 16.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 28 | 82.85 | 4069.9999999999873 | 41.299 | 2982.33 | -1530.00000000002 | 8419.99999999998 | 9950 | 10 | 89.83353733170136 | 8008.75 | 0 | 411.24999999998 | 0 |  | 115.16203703703704 | 9950 | 2018 | 3 | 2018_03_Asomata_english.xlsx
29 | 445 | 185 | 630 | 0 | 0 | 4 | 630 | 108 | 8.89999999999418 | 3.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.25 | 7400.000000000007 | 41.39 | 3088.8 | 3330.00000000002 | 9693.00000000002 | 6363 | 10.1 | 85.99683637002754 | 9428 | 0 | 325.00000000002 | 60 |  | 73.64583333333333 | 6363 | 2018 | 3 | 2018_03_Asomata_english.xlsx
30 | 620 | 365 | 985 | 0 | 0 | 4 | 985 | 108 | 11.900000000001455 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 30 | 83.8 | 6320 | 41.972 | 3769.74 | -1080.0000000000073 | 8868.499999999993 | 9948.5 | 10.1 | 86.9226396323843 | 8807.6 | 0 | 120.89999999999236 | 60 |  | 115.14467592592592 | 9948.5 | 2018 | 3 | 2018_03_Asomata_english.xlsx
31 | 810 | 405 | 1215 | 0 | 0 | 3 | 1215 | 109 | 16.099999999998545 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 31 | 82.35 | 2969.9999999999873 | 41.879 | 3660.93 | -3350.0000000000127 | 9103.749999999987 | 12453.75 | 10.25 | 88.72850364191376 | 9100 | 0 | 63.74999999998727 | 60 |  | 144.140625 | 12453.75 | 2018 | 3 | 2018_03_Asomata_english.xlsx
1 | 370 | 720 | 1090 | 0 | 0 | 4 | 1090 | 100 | 7.200000000004366 | 13.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 83.75 | 6200.000000000007 | 41.919 | 3707.73 | 3230.00000000002 | 14402.5 | 11172.5 | 10.25 | 85.7531765736819 | 14524.97 | 0 | 27.530000000020664 | 150 |  | 129.31134259259258 | 11172.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
2 | 655 | 830 | 1485 | 0 | 0 | 4 | 1485 | 100 | 13 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 82.7 | 3740.0000000000064 | 41.659 | 3403.53 | -2460 | 12612.75 | 15072.75 | 10.15 | 88.83213710799917 | 12633.9 | 0 | 38.849999999998545 | 60 |  | 174.453125 | 15072.75 | 2018 | 4 | 2018_04_Asomata_english.xlsx
3 | 835 | 285 | 1120 | 0 | 0 | 3 | 1120 | 109 | 16.099999999998545 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 83.9 | 6560.00000000002 | 41.761 | 3522.87 | 2820.0000000000136 | 14020 | 11200 | 10 | 87.58233890214795 | 13800 | 0 | 220.00000000001455 | 0 |  | 129.62962962962962 | 11200 | 2018 | 4 | 2018_04_Asomata_english.xlsx
4 | 605 | 860 | 1465 | 0 | 0 | 4 | 1465 | 105 | 12.349999999998545 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 82.5 | 3300 | 41.601 | 3335.67 | -3260.00000000002 | 11756.25 | 15016.25 | 10.25 | 88.3998795543511 | 11760.3 | 0 | 55.94999999998072 | 60 |  | 173.7991898148148 | 15016.25 | 2018 | 4 | 2018_04_Asomata_english.xlsx
5 | 525 | 305 | 830 | 0 | 0 | 4 | 830 | 55 | 10.150000000001455 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 82.9 | 4180.000000000013 | 41.851 | 3628.17 | 880.0000000000127 | 9304.500000000013 | 8424.5 | 10.15 | 88.39775012947594 | 9316.45 | 0 | 48.050000000012005 | 60 |  | 97.50578703703704 | 8424.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
6 | 310 | 625 | 935 | 0 | 0 | 4 | 935 | 108 | 5.80000000000291 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84 | 6800.000000000007 | 41.8315 | 3605.354999999996 | 2619.9999999999945 | 12063.5 | 9443.5 | 10.1 | 86.50872230080151 | 11929.05 | 0 | 134.44999999999527 | 0 |  | 109.29976851851852 | 9443.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
7 | 585 | 695 | 1280 | 0 | 0 | 3 | 1280 | 110 | 11.299999999995634 | 13.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.1 | 7039.999999999993 | 41.52 | 3240.9 | 239.99999999998545 | 13168 | 12928 | 10.1 | 86.3032383998495 | 13193.25 | 0 | 34.74999999998545 | 60 |  | 149.62962962962962 | 12928 | 2018 | 4 | 2018_04_Asomata_english.xlsx
8 | 105 | 135 | 240 | 0 | 0 | 4 | 240 | 70 | 2.7000000000043656 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 83.8 | 6320 | 41.631 | 3370.77 | -719.9999999999927 | 1704.0000000000073 | 2424 | 10.1 | 86.9226396323843 | 1742.4 | 0 | 21.600000000007185 | 60 |  | 28.055555555555557 | 2424 | 2018 | 4 | 2018_04_Asomata_english.xlsx
9 | 195 | 175 | 370 | 0 | 0 | 3 | 370 | 110 | 4.099999999998545 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 83.45 | 5480.000000000014 | 42.004 | 3807.18 | -839.9999999999864 | 3386.2473118279704 | 3737 | 10.1 | 87.65660643265774 | 3379.6 | 489.247311827957 | 66.6473118279705 | 60 |  | 43.25231481481482 | 3737 | 2018 | 4 | 2018_04_Asomata_english.xlsx
10 | 470 | 645 | 1115 | 0 | 0 | 3 | 1115 | 110 | 8.849999999998545 | 12.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 10 | 83.15 | 4760.00000000002 | 42.052 | 3863.34 | -719.9999999999936 | 10541.5 | 11261.5 | 10.1 | 88.29565824140128 | 10596.3 | 0 | 25.200000000006185 | 80 |  | 130.3414351851852 | 11261.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
11 | 800 | 645 | 1445 | 0 | 0 | 6 | 1445 | 110 | 16.44999999999709 | 13.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 82.8 | 3959.9999999999936 | 41.85 | 3627 | -800.0000000000264 | 13939 | 14739 | 10.2 | 88.18002691272588 | 13963.5 | 0 | 35.499999999970896 | 60 |  | 170.59027777777774 | 14739 | 2018 | 4 | 2018_04_Asomata_english.xlsx
12 | 710 | 590 | 1300 | 0 | 0 | 3 | 1300 | 105 | 14.80000000000291 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 83.1 | 4639.999999999993 | 41.92 | 3708.9 | 679.9999999999991 | 14330 | 13650 | 10.5 | 85.03533773606767 | 14326.35 | 0 | 63.650000000001455 | 60 |  | 157.98611111111111 | 13650 | 2018 | 4 | 2018_04_Asomata_english.xlsx
13 | 875 | 405 | 1280 | 0 | 0 | 4 | 1280 | 109 | 17 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 13 | 83.2 | 4880.000000000014 | 41.9 | 3685.5 | 240.00000000002092 | 13168 | 12928 | 10.1 | 88.18850331635105 | 12826.1 | 0 | 341.90000000002146 | 0 |  | 149.62962962962962 | 12928 | 2018 | 4 | 2018_04_Asomata_english.xlsx
14 | 5 | 510 | 515 | 0 | 0 | 4 | 515 | 100 | 0.19999999999708962 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.5 | 5600.000000000007 | 41.8 | 3568.5 | 719.9999999999936 | 5921.499999999994 | 5201.5 | 10.1 | 87.55099606346177 | 5818.1 | 0 | 103.39999999999327 | 0 |  | 60.2025462962963 | 5201.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
15 | 385 | 0 | 385 | 0 | 0 | 4 | 385 | 55 | 7.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.6 | 5839.999999999993 | 41.5128 | 3232.4759999999974 | 239.99999999998545 | 4128.499999999985 | 3888.5 | 10.1 | 87.34053693830923 | 4066.1 | 0 | 122.39999999998554 | 60 |  | 45.00578703703704 | 3888.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
16 | 0 | 395 | 395 | 0 | 0 | 3 | 395 | 54 | 0 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84 | 6800.000000000007 | 41.22 | 2889.9 | 960.0000000000146 | 4910.000000000015 | 3950 | 10 | 87.37380952380953 | 4891 | 0 | 19.000000000014552 | 0 |  | 45.717592592592595 | 3950 | 2018 | 4 | 2018_04_Asomata_english.xlsx
17 | 410 | 0 | 410 | 0 | 0 | 4 | 410 | 55 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84 | 6800.000000000007 | 40.86 | 2468.7 | 0 | 4100 | 4100 | 10 | 87.37380952380953 | 3920.1 | 0 | 189.9 | 10 |  | 47.4537037037037 | 4100 | 2018 | 4 | 2018_04_Asomata_english.xlsx
18 | 275 | 320 | 595 | 0 | 0 | 4 | 595 | 55 | 5.80000000000291 | 7.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 83.5 | 5600.000000000007 | 41.71 | 3463.2 | -1200 | 5047.5 | 6247.5 | 10.5 | 84.21572002294894 | 5130 | 0 | 37.5 | 120 |  | 72.30902777777777 | 6247.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
19 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 50 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 83.95 | 6680.000000000014 | 40.99 | 2620.8 | 1080.0000000000064 | 5450.010638297878 | 3811.5 | 9.9 | 88.36156559636892 | 5213.6 | 558.5106382978723 | 236.4106382978789 | 0 |  | 44.114583333333336 | 3811.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
20 | 255 | 85 | 340 | 0 | 0 | 3 | 340 | 50 | 5.349999999998545 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 83.4 | 5360.00000000002 | 41.402 | 3102.84 | -1319.9999999999936 | 2114.0000000000064 | 3434 | 10.1 | 87.76247189936385 | 2044 | 0 | 130.00000000000637 | 60 |  | 39.745370370370374 | 3434 | 2018 | 4 | 2018_04_Asomata_english.xlsx
21 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.7 | 8480.000000000015 | 39.415 | 778.05 | 3119.9999999999945 | 4547.042553191484 | 693 | 9.9 | 86.80954746528516 | 4314.3 | 734.0425531914893 | 232.74255319148415 | 0 |  | 8.020833333333334 | 693 | 2018 | 4 | 2018_04_Asomata_english.xlsx
22 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 35 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.1 | 4639.999999999993 | 40.82 | 2421.9 | -3840.000000000022 | 2428.6505376343866 | 1666.5 | 10.1 | 88.40307388403076 | 2436 | 4602.1505376344085 | 52.65053763438664 | 60 |  | 19.288194444444443 | 1666.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
23 | 290 | 30 | 320 | 0 | 0 | 3 | 320 | 50 | 6.099999999998545 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 83.45 | 5480.000000000014 | 41.71 | 3463.2 | 840.0000000000209 | 4040.000000000021 | 3200 | 10 | 88.53317249698432 | 3799.95 | 0 | 240.0500000000211 | 0 |  | 37.03703703703704 | 3200 | 2018 | 4 | 2018_04_Asomata_english.xlsx
24 | 380 | 720 | 1100 | 0 | 0 | 4 | 1100 | 108 | 8.900000000001455 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 24 | 84.1 | 7039.999999999993 | 41.72 | 3474.9 | 1559.999999999979 | 13055 | 11495 | 10.45 | 83.4126993146871 | 13075.8 | 0 | 39.19999999997708 | 60 |  | 133.04398148148147 | 11495 | 2018 | 4 | 2018_04_Asomata_english.xlsx
25 | 505 | 305 | 810 | 0 | 0 | 3 | 810 | 108 | 10.900000000001455 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 83.55 | 5720 | 42.062 | 3875.04 | -1319.9999999999927 | 7063.500000000007 | 8383.5 | 10.35 | 85.3334263473959 | 7077 | 0 | 46.500000000007276 | 60 |  | 97.03125 | 8383.5 | 2018 | 4 | 2018_04_Asomata_english.xlsx
26 | 5 | 100 | 105 | 0 | 0 | 3 | 105 | 55 | 0.09999999999854481 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.85 | 6439.999999999993 | 41.25 | 2925 | 719.9999999999927 | 1748.9999999999927 | 1029 | 9.8 | 89.47650744885767 | 1691.2 | 0 | 57.79999999999268 | 0 |  | 11.909722222222221 | 1029 | 2018 | 4 | 2018_04_Asomata_english.xlsx
27 | 475 | 0 | 475 | 0 | 0 | 3 | 475 | 50 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 83.85 | 6439.999999999993 | 41.538 | 3261.9599999999914 | 0 | 4750 | 4750 | 10 | 87.68697729988054 | 4492.25 | 0 | 257.75 | 0 |  | 54.976851851851855 | 4750 | 2018 | 4 | 2018_04_Asomata_english.xlsx
28 | 65 | 115 | 180 | 0 | 0 | 3 | 180 | 55 | 1.5500000000029104 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.2 | 7280.000000000014 | 41.86 | 3638.7 | 840.0000000000209 | 2577.000000000021 | 1737 | 9.65 | 90.11369496353412 | 2486.4 | 0 | 90.60000000002083 | 0 |  | 20.104166666666668 | 1737 | 2018 | 4 | 2018_04_Asomata_english.xlsx
29 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 55 | 3.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 83.75 | 6200.000000000007 | 41.53 | 3252.6 | -1080.0000000000064 | 2222.4864864864803 | 1616 | 10.1 | 87.02673860200392 | 2254 | 1686.4864864864865 | 28.486486486480317 | 60 |  | 18.703703703703702 | 1616 | 2018 | 4 | 2018_04_Asomata_english.xlsx
30 | 85 | 135 | 220 | 0 | 0 | 4 | 220 | 70 | 2.4500000000043656 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 83.9 | 6560.00000000002 | 41.75 | 3510 | 360.00000000001273 | 2560.0000000000127 | 2200 | 10 | 87.58233890214795 | 2445 | 0 | 115.00000000001273 | 0 |  | 25.462962962962962 | 2200 | 2018 | 4 | 2018_04_Asomata_english.xlsx
1 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 54 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.85 | 6439.999999999993 | 41.48 | 3194.1 | -120.00000000002728 | 3004.010638297845 | 1565.5 | 10.1 | 86.81878940582232 | 2993 | 1558.5106382978724 | 71.01063829784516 | 60 |  | 18.119212962962962 | 1565.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
2 | 10 | 185 | 195 | 0 | 0 | 4 | 195 | 35 | 0.09999999999854481 | 4.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 83.9 | 6560.00000000002 | 41.26 | 2936.7 | 120.00000000002728 | 2070.0000000000273 | 1950 | 10 | 87.58233890214795 | 1887 | 0 | 183.00000000002728 | 0 |  | 22.569444444444443 | 1950 | 2018 | 5 | 2018_05_Asomata_english.xlsx
3 | 255 | 0 | 255 | 0 | 0 | 3 | 255 | 40 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 83.9 | 6560.00000000002 | 41.32 | 3006.9 | 0 | 2575.5 | 2575.5 | 10.1 | 86.71518703182966 | 2584.2 | 0 | 11.300000000000182 | 20 |  | 29.80902777777778 | 2575.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
4 | 270 | 75 | 345 | 0 | 0 | 4 | 345 | 80 | 6.80000000000291 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.1 | 7039.999999999993 | 42.06 | 3872.7 | 479.9999999999727 | 3929.9999999999727 | 3450 | 10 | 87.16627078384799 | 3814.4 | 0 | 115.59999999997217 | 0 |  | 39.93055555555556 | 3450 | 2018 | 5 | 2018_05_Asomata_english.xlsx
5 | 290 | 0 | 290 | 0 | 0 | 5 | 290 | 40 | 7.19999999999709 | 0 | 0 | 0 | 0 | 0 | 16.3 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 5 | 83.8 | 6320 | 41.99 | 3790.8 | -719.9999999999927 | 2151.0000000000073 | 2871 | 9.9 | 88.67865255425065 | 1985.65 | 0 | 165.3500000000074 | 0 |  | 33.229166666666664 | 2871 | 2018 | 5 | 2018_05_Asomata_english.xlsx
6 | 335 | 0 | 335 | 0 | 0 | 8 | 335 | 40 | 8.44999999999709 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 6 | 84.1 | 7039.999999999993 | 42.042 | 3851.64 | 719.9999999999927 | 4103.499999999993 | 3383.5 | 10.1 | 86.3032383998495 | 3946.95 | 0 | 156.5499999999929 | 0 |  | 39.160879629629626 | 3383.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
7 | 400 | 0 | 400 | 0 | 0 | 2 | 400 | 40 | 10.05000000000291 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 7 | 84.25 | 7400.000000000007 | 41.72 | 3474.9 | 360.00000000001455 | 4400.000000000015 | 4040 | 10.1 | 85.99683637002754 | 4329.15 | 0 | 70.85000000001492 | 0 |  | 46.75925925925926 | 4040 | 2018 | 5 | 2018_05_Asomata_english.xlsx
8 | 265 | 0 | 265 | 0 | 0 | 3 | 265 | 54 | 5.900000000001455 | 0 | 0 | 0 | 3.35 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ & ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 8 | 84.25 | 7400.000000000007 | 41.601 | 3335.67 | 0 | 2610.25 | 2610.25 | 9.85 | 88.17949719160184 | 2287.15 | 0 | 323.1 | 0 |  | 30.21122685185185 | 2610.25 | 2018 | 5 | 2018_05_Asomata_english.xlsx
9 | 190 | 0 | 190 | 0 | 0 | 3 | 190 | 40 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 9 | 84.25 | 7400.000000000007 | 41.601 | 3335.67 | 0 | 1919 | 1919 | 10.1 | 85.99683637002754 | 1620.6 | 0 | 298.4 | 0 |  | 22.21064814814815 | 1919 | 2018 | 5 | 2018_05_Asomata_english.xlsx
10 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 40 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 10 | 84.3 | 7520 | 41.95 | 3744 | 119.99999999999272 | 2291.4999999999927 | 2171.5 | 10.1 | 85.89518526320718 | 2153.55 | 0 | 137.949999999993 | 0 |  | 25.13310185185185 | 2171.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
11 | 215 | 0 | 215 | 0 | 0 | 6 | 215 | 40 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 11 | 84.3 | 7520 | 41.82 | 3591.9 | 0 | 2128.5 | 2128.5 | 9.9 | 87.63044153115075 | 2056.2 | 0 | 72.29999999999973 | 0 |  | 24.635416666666668 | 2128.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
12 | 270 | 0 | 270 | 0 | 0 | 4 | 270 | 55 | 6.299999999995634 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 12 | 84.05 | 6920 | 41.892 | 3676.1400000000085 | -600 | 3424.872340425532 | 2727 | 10.1 | 86.4058581839159 | 3197.4 | 1297.872340425532 | 227.47234042553237 | 0 |  | 31.5625 | 2727 | 2018 | 5 | 2018_05_Asomata_english.xlsx
13 | 275 | 0 | 275 | 0 | 0 | 4 | 275 | 40 | 7.30000000000291 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 13 | 84.8 | 8720 | 41.631 | 3370.77 | 1800 | 5124.375 | 2777.5 | 10.1 | 84.89173683723513 | 5110.7 | 546.875 | 73.67499999999927 | 60 |  | 32.14699074074074 | 2777.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
14 | 295 | 0 | 295 | 0 | 0 | 8 | 295 | 40 | 6.650000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 14 | 84.6 | 8239.999999999993 | 41.002 | 2634.84 | -480.0000000000073 | 2499.4999999999927 | 2979.5 | 10.1 | 85.29028959233953 | 2255.7 | 0 | 243.7999999999929 | 0 |  | 34.4849537037037 | 2979.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
15 | 300 | 0 | 300 | 0 | 0 | 8 | 300 | 55 | 7.650000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 15 | 84.65 | 8360.00000000002 | 41.74 | 3498.3 | 120.00000000002728 | 3060.0000000000273 | 2940 | 9.8 | 87.79816733258366 | 2929.4 | 0 | 130.6000000000272 | 0 |  | 34.02777777777778 | 2940 | 2018 | 5 | 2018_05_Asomata_english.xlsx
16 | 325 | 0 | 325 | 0 | 0 | 8 | 325 | 55 | 7.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 16 | 84.75 | 8600.000000000007 | 41.8 | 3568.5 | 239.99999999998727 | 3522.4999999999873 | 3282.5 | 10.1 | 84.9910254183313 | 3292.3 | 0 | 230.19999999998754 | 0 |  | 37.991898148148145 | 3282.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
17 | 290 | 0 | 290 | 0 | 0 | 8 | 290 | 40 | 7.25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 17 | 84.7 | 8480.000000000015 | 42.094 | 3912.4800000000064 | -119.99999999999272 | 2736.5000000000073 | 2856.5 | 9.85 | 87.25020506663179 | 2567 | 0 | 169.50000000000728 | 0 |  | 33.061342592592595 | 2856.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
18 | 430 | 0 | 430 | 0 | 0 | 1 | 430 | 40 | 10.64999999999418 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 18 | 84.4 | 7760.00000000002 | 41.755 | 3515.85 | -719.9999999999945 | 3623.0000000000055 | 4343 | 10.1 | 85.69260227909582 | 3646.75 | 0 | 36.25000000000546 | 60 |  | 50.2662037037037 | 4343 | 2018 | 5 | 2018_05_Asomata_english.xlsx
19 | 250 | 0 | 250 | 0 | 0 | 1 | 250 | 40 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 19 | 84.6 | 8239.999999999993 | 41.848 | 3624.66 | 479.9999999999727 | 2929.9999999999727 | 2450 | 9.8 | 87.90121682475808 | 2640 | 0 | 289.9999999999727 | 0 |  | 28.35648148148148 | 2450 | 2018 | 5 | 2018_05_Asomata_english.xlsx
20 | 260 | 0 | 260 | 0 | 0 | 1 | 260 | 50 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 20 | 84.5 | 8000.000000000007 | 41.7 | 3451.5 | -239.99999999998545 | 2282.0000000000146 | 2522 | 9.7 | 89.01637355973318 | 2032.5 | 0 | 249.50000000001455 | 0 |  | 29.189814814814813 | 2522 | 2018 | 5 | 2018_05_Asomata_english.xlsx
21 | 260 | 0 | 260 | 0 | 0 | 1 | 260 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 21 | 84.65 | 8360.00000000002 | 41.63 | 3369.6 | 360.00000000001273 | 2960.0000000000127 | 2600 | 10 | 86.04220398593199 | 2801.05 | 0 | 158.95000000001255 | 0 |  | 30.09259259259259 | 2600 | 2018 | 5 | 2018_05_Asomata_english.xlsx
22 | 340 | 0 | 340 | 0 | 0 | 1 | 340 | 55 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 22 | 84.15 | 7160.00000000002 | 42 | 3802.5 | -1200 | 2234 | 3434 | 10.1 | 86.20086207909047 | 2102.4 | 0 | 131.6 | 0 |  | 39.745370370370374 | 3434 | 2018 | 5 | 2018_05_Asomata_english.xlsx
23 | 165 | 140 | 305 | 0 | 0 | 3 | 305 | 40 | 4.100000000005821 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 16.85 | 0 | 0 | 0 | 1 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 23 | 84.2 | 7280.000000000014 | 41.84 | 3615.3 | 119.99999999999363 | 3230.9999999999936 | 3111 | 10.2 | 85.25462317628474 | 3283.2 | 0 | 7.799999999993815 | 60 |  | 36.00694444444444 | 3111 | 2018 | 5 | 2018_05_Asomata_english.xlsx
24 | 0 | 320 | 320 | 0 | 0 | 4 | 320 | 40 | 0 | 8.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.4 | 7760.00000000002 | 41.62 | 3357.9 | 480.00000000000637 | 3712.0000000000064 | 3232 | 10.1 | 85.69260227909582 | 3693.8 | 0 | 78.20000000000618 | 60 |  | 37.407407407407405 | 3232 | 2018 | 5 | 2018_05_Asomata_english.xlsx
25 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 45 | 0 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.35 | 7639.999999999993 | 41.79 | 3556.8 | -120.00000000002728 | 3229.9999999999727 | 3350 | 10 | 86.65171192443921 | 3064.95 | 0 | 165.0499999999729 | 0 |  | 38.773148148148145 | 3350 | 2018 | 5 | 2018_05_Asomata_english.xlsx
26 | 0 | 310 | 310 | 0 | 0 | 4 | 310 | 40 | 0 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.6 | 8239.999999999993 | 41.94 | 3732.3 | 600 | 3731 | 3131 | 10.1 | 85.29028959233953 | 3686.5 | 0 | 44.5 | 0 |  | 36.238425925925924 | 3131 | 2018 | 5 | 2018_05_Asomata_english.xlsx
27 | 170 | 200 | 370 | 0 | 0 | 4 | 370 | 70 | 4.649999999994179 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.3 | 7520 | 42.028 | 3835.26 | -719.9999999999927 | 5576.585492227987 | 3737 | 10.1 | 85.89518526320718 | 5587.5 | 2559.585492227979 | 49.08549222798683 | 60 |  | 43.25231481481482 | 3737 | 2018 | 5 | 2018_05_Asomata_english.xlsx
28 | 0 | 340 | 340 | 0 | 0 | 4 | 340 | 55 | 0 | 7.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.25 | 7400.000000000007 | 41.62 | 3357.9 | -119.99999999999272 | 4361.87234042554 | 3434 | 10.1 | 85.99683637002754 | 4292.4 | 1047.872340425532 | 69.4723404255401 | 0 |  | 39.745370370370374 | 3434 | 2018 | 5 | 2018_05_Asomata_english.xlsx
29 | 0 | 405 | 405 | 0 | 0 | 5 | 405 | 53 | 0 | 9.400000000001455 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 29 | 84.3 | 7520 | 41.839 | 3614.13 | 119.99999999999272 | 4210.499999999993 | 4090.5 | 10.1 | 85.89518526320718 | 4149.65 | 0 | 60.84999999999309 | 0 |  | 47.34375 | 4090.5 | 2018 | 5 | 2018_05_Asomata_english.xlsx
30 | 0 | 390 | 390 | 0 | 0 | 3 | 390 | 40 | 0 | 9.39999999999418 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 30 | 84.65 | 8360.00000000002 | 41.951 | 3745.17 | 840.00000000002 | 4740.00000000002 | 3900 | 10 | 86.04220398593199 | 4699 | 0 | 41.00000000002001 | 0 |  | 45.138888888888886 | 3900 | 2018 | 5 | 2018_05_Asomata_english.xlsx
31 | 0 | 430 | 430 | 0 | 0 | 4 | 430 | 40 | 0 | 10.60000000000582 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 31 | 84.15 | 7160.00000000002 | 41.903 | 3689.01 | -1200 | 3143 | 4343 | 10.1 | 86.20086207909047 | 2911 | 0 | 292 | 60 |  | 50.2662037037037 | 4343 | 2018 | 5 | 2018_05_Asomata_english.xlsx
1 | 0 | 390 | 390 | 0 | 0 | 3 | 390 | 54 | 0 | 9.69999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 84 | 6800.000000000007 | 41.801 | 3569.67 | -360.00000000001273 | 3578.9999999999873 | 3939 | 10.1 | 86.50872230080151 | 3564 | 0 | 74.99999999998727 | 60 |  | 45.59027777777778 | 3939 | 2018 | 6 | 2018_06_Asomata_english.xlsx
2 | 0 | 410 | 410 | 0 | 0 | 3 | 410 | 40 | 0 | 10.599999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 83.75 | 6200.000000000007 | 41.9 | 3685.5 | -600 | 3541 | 4141 | 10.1 | 87.02673860200392 | 3594.12 | 0 | 6.879999999999654 | 60 |  | 47.92824074074074 | 4141 | 2018 | 6 | 2018_06_Asomata_english.xlsx
3 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 40 | 0 | 10.400000000001455 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 3 | 84.2 | 7280.000000000014 | 41.712 | 3465.5400000000086 | 1080.0000000000064 | 5196.000000000006 | 4116 | 9.8 | 88.73440371409225 | 4975.6 | 0 | 220.400000000006 | 0 |  | 47.638888888888886 | 4116 | 2018 | 6 | 2018_06_Asomata_english.xlsx
4 | 0 | 605 | 605 | 0 | 0 | 4 | 605 | 54 | 0 | 12.400000000001455 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 4 | 84 | 6800.000000000007 | 41.852 | 3629.34 | -480.00000000000637 | 5842.249999999994 | 6322.25 | 10.45 | 83.61130097972203 | 5883.8 | 0 | 18.44999999999436 | 60 |  | 73.17418981481481 | 6322.25 | 2018 | 6 | 2018_06_Asomata_english.xlsx
5 | 0 | 490 | 490 | 0 | 0 | 4 | 490 | 54 | 0 | 9.69999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 5 | 84.1 | 7039.999999999993 | 41.602 | 3336.84 | 239.99999999998545 | 5188.999999999985 | 4949 | 10.1 | 86.3032383998495 | 5169.6 | 0 | 79.39999999998508 | 60 |  | 57.280092592592595 | 4949 | 2018 | 6 | 2018_06_Asomata_english.xlsx
6 | 0 | 660 | 660 | 0 | 0 | 3 | 660 | 54 | 0 | 12.700000000004366 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 6 | 84.1 | 7039.999999999993 | 41.64 | 3381.3 | 0 | 6600 | 6600 | 10 | 87.16627078384799 | 6489.8 | 0 | 110.2 | 0 |  | 76.38888888888889 | 6600 | 2018 | 6 | 2018_06_Asomata_english.xlsx
7 | 0 | 705 | 705 | 0 | 0 | 2 | 705 | 55 | 0 | 13.69999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 7 | 84.4 | 7760.00000000002 | 41.761 | 3522.87 | 720.0000000000273 | 7840.500000000027 | 7120.5 | 10.1 | 85.69260227909582 | 7767.2 | 0 | 73.30000000002747 | 0 |  | 82.41319444444444 | 7120.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
8 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 53 | 0 | 12.30000000000291 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 8 | 84.45 | 7880.000000000014 | 41.751 | 3511.1699999999937 | 119.99999999999363 | 6533.499999999994 | 6413.5 | 10.1 | 85.5916687075068 | 6384.95 | 0 | 208.5499999999929 | 60 |  | 74.23032407407408 | 6413.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
9 | 0 | 590 | 590 | 0 | 0 | 4 | 590 | 55 | 0 | 13 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 9 | 83.75 | 6200.000000000007 | 42.001 | 3803.6699999999937 | -1680.0000000000064 | 4278.999999999994 | 5959 | 10.1 | 87.02673860200392 | 4118.4 | 0 | 220.5999999999931 | 60 |  | 68.9699074074074 | 5959 | 2018 | 6 | 2018_06_Asomata_english.xlsx
10 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 40 | 0 | 13.19999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 10 | 84.35 | 7639.999999999993 | 41.8 | 3568.5 | 1439.9999999999854 | 6691.999999999985 | 5252 | 10.1 | 85.79377418261309 | 6643 | 0 | 108.99999999998545 | 60 |  | 60.78703703703704 | 5252 | 2018 | 6 | 2018_06_Asomata_english.xlsx
11 | 0 | 540 | 540 | 0 | 0 | 2 | 540 | 55 | 0 | 11.900000000001455 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 11 | 84.4 | 7760.00000000002 | 41.852 | 3629.34 | 120.00000000002728 | 5601.000000000027 | 5481 | 10.15 | 85.27047123338599 | 5635.6 | 0 | 25.40000000002692 | 60 |  | 63.4375 | 5481 | 2018 | 6 | 2018_06_Asomata_english.xlsx
12 | 0 | 530 | 530 | 0 | 0 | 3 | 530 | 40 | 0 | 12.099999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 12 | 84.6 | 8239.999999999993 | 41.9015 | 3687.254999999996 | 479.9999999999727 | 5832.999999999973 | 5353 | 10.1 | 85.29028959233953 | 5646.75 | 0 | 186.24999999997272 | 0 |  | 61.95601851851852 | 5353 | 2018 | 6 | 2018_06_Asomata_english.xlsx
13 | 0 | 630 | 630 | 0 | 0 | 4 | 630 | 55 | 0 | 13.150000000001455 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 13 | 84.7 | 8480.000000000015 | 41.998 | 3800.16 | 240.00000000002183 | 6414.000000000022 | 6174 | 9.8 | 87.6953591741146 | 6243.1 | 0 | 170.90000000002146 | 0 |  | 71.45833333333333 | 6174 | 2018 | 6 | 2018_06_Asomata_english.xlsx
14 | 0 | 575 | 575 | 0 | 0 | 4 | 575 | 44 | 0 | 14.650000000001455 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 14 | 84.55 | 8120 | 41.7 | 3451.5 | -360.00000000001455 | 5447.499999999985 | 5807.5 | 10.1 | 85.39051319938106 | 5445 | 0 | 62.49999999998545 | 60 |  | 67.21643518518519 | 5807.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
15 | 445 | 110 | 555 | 0 | 0 | 4 | 555 | 100 | 10.85000000000582 | 2.3999999999941792 | 0 | 0 | 1 | 0 | 0 | 0 | 2.75 | 0 | 2 | 2 | ΒΛ. ΚΥΚΛ. ΨΥΞΗΣ ΝοΙ & ΒΛ. Δ/Κ Ρ25 | 15 | 84.75 | 8600.000000000007 | 41.998 | 3800.16 | 480.0000000000073 | 6085.500000000007 | 5605.5 | 10.1 | 84.9910254183313 | 5942.2 | 0 | 203.30000000000746 | 60 |  | 64.87847222222223 | 5605.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
16 | 70 | 495 | 565 | 0 | 0 | 4 | 565 | 75 | 2.099999999998545 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.4 | 7760.00000000002 | 42 | 3802.5 | -839.9999999999873 | 4866.500000000013 | 5706.5 | 10.1 | 85.69260227909582 | 4662 | 0 | 264.50000000001273 | 60 |  | 66.04745370370371 | 5706.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
17 | 0 | 540 | 540 | 0 | 0 | 4 | 540 | 50 | 0 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.5 | 8000.000000000007 | 41.898 | 3683.16 | 239.99999999998727 | 5693.999999999987 | 5454 | 10.1 | 85.49097262667443 | 5655 | 0 | 98.99999999998727 | 60 |  | 63.125 | 5454 | 2018 | 6 | 2018_06_Asomata_english.xlsx
18 | 250 | 315 | 565 | 0 | 0 | 4 | 565 | 45 | 5.94999999999709 | 6.950000000004366 | 0 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛ. ΚΥΚΛ. ΨΥΞΗΣ ΝοΙ (ΨΥΓΕΙΟ Νο5) | 18 | 84.5 | 8000.000000000007 | 41.9 | 3685.5 | 0 | 5537 | 5537 | 9.8 | 88.1080432172869 | 5345.4 | 0 | 191.6 | 0 |  | 64.08564814814815 | 5537 | 2018 | 6 | 2018_06_Asomata_english.xlsx
19 | 545 | 0 | 545 | 0 | 0 | 2 | 545 | 45 | 11.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.55 | 8120 | 41.998 | 3800.16 | 119.99999999999272 | 5569.999999999993 | 5450 | 10 | 86.24441833137486 | 5365 | 0 | 204.99999999999272 | 0 |  | 63.0787037037037 | 5450 | 2018 | 6 | 2018_06_Asomata_english.xlsx
20 | 0 | 530 | 530 | 0 | 0 | 4 | 530 | 45 | 0 | 12.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.3 | 7520 | 42.057 | 3869.19 | -600 | 4753 | 5353 | 10.1 | 85.89518526320718 | 4765.6 | 0 | 47.399999999999636 | 60 |  | 61.95601851851852 | 5353 | 2018 | 6 | 2018_06_Asomata_english.xlsx
21 | 125 | 555 | 680 | 0 | 0 | 3 | 680 | 90 | 3.1999999999970896 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 84.2 | 7280.000000000014 | 42.056 | 3868.0199999999936 | -239.99999999998636 | 6628.000000000014 | 6868 | 10.1 | 86.09872835624795 | 6445.95 | 0 | 242.05000000001382 | 60 |  | 79.49074074074075 | 6868 | 2018 | 6 | 2018_06_Asomata_english.xlsx
22 | 550 | 45 | 595 | 0 | 0 | 4 | 595 | 44 | 12.30000000000291 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.2 | 7280.000000000014 | 42.048 | 3858.66 | 0 | 5831 | 5831 | 9.8 | 88.73440371409225 | 5685 | 0 | 146 | 0 |  | 67.48842592592592 | 5831 | 2018 | 6 | 2018_06_Asomata_english.xlsx
23 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 45 | 12.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.3 | 7520 | 42.002 | 3804.84 | 239.99999999998636 | 5744.499999999986 | 5504.5 | 10.1 | 85.89518526320718 | 5438.5 | 0 | 305.99999999998636 | 0 |  | 63.70949074074074 | 5504.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
24 | 25 | 465 | 490 | 0 | 0 | 3 | 490 | 45 | 0.4000000000014552 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.3 | 7520 | 41.896 | 3680.82 | 0 | 5120.5 | 5120.5 | 10.45 | 83.01831302951125 | 4978.6 | 0 | 141.90000000000055 | 0 |  | 59.2650462962963 | 5120.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
25 | 520 | 0 | 520 | 0 | 0 | 4 | 520 | 53 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.2 | 7280.000000000014 | 41.8385 | 3613.545000000004 | -239.99999999998636 | 5012.000000000014 | 5252 | 10.1 | 86.09872835624795 | 4909.8 | 0 | 102.20000000001346 | 0 |  | 60.78703703703704 | 5252 | 2018 | 6 | 2018_06_Asomata_english.xlsx
26 | 10 | 545 | 555 | 0 | 0 | 4 | 555 | 50 | 0.1500000000014552 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.3 | 7520 | 41.942 | 3734.64 | 239.99999999998636 | 5789.999999999986 | 5550 | 10 | 86.75413711583924 | 5126.3 | 0 | 663.6999999999862 | 0 |  | 64.23611111111111 | 5550 | 2018 | 6 | 2018_06_Asomata_english.xlsx
27 | 560 | 10 | 570 | 0 | 0 | 3 | 570 | 45 | 16.150000000001455 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.6 | 8239.999999999993 | 41.93 | 3720.6 | 719.9999999999927 | 6419.999999999993 | 5700 | 10 | 86.14319248826293 | 6157.5 | 0 | 262.4999999999927 | 0 |  | 65.97222222222223 | 5700 | 2018 | 6 | 2018_06_Asomata_english.xlsx
28 | 0 | 155 | 155 | 0 | 0 | 4 | 155 | 45 | 0 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.6 | 8239.999999999993 | 40.83 | 2433.6 | 0 | 1565.5 | 1565.5 | 10.1 | 85.29028959233953 | 1241 | 0 | 384.5 | 60 |  | 18.119212962962962 | 1565.5 | 2018 | 6 | 2018_06_Asomata_english.xlsx
29 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 45 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.25 | 7400.000000000007 | 41.072 | 2716.7400000000084 | -839.9999999999854 | 2198.9487179487323 | 2121 | 10.1 | 85.99683637002754 | 2079.4 | 917.9487179487179 | 119.54871794873225 | 0 |  | 24.54861111111111 | 2121 | 2018 | 6 | 2018_06_Asomata_english.xlsx
30 | 0 | 265 | 265 | 0 | 0 | 4 | 265 | 40 | 0 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.3 | 7520 | 41.822 | 3594.2400000000084 | 119.99999999999272 | 2769.9999999999927 | 2650 | 10 | 86.75413711583924 | 2650.05 | 0 | 119.949999999993 | 0 |  | 30.671296296296298 | 2650 | 2018 | 6 | 2018_06_Asomata_english.xlsx
1 | 215 | 70 | 285 | 0 | 0 | 4 | 285 | 54 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.6 | 8239.999999999993 | 41.562 | 3290.04 | 719.9999999999927 | 3598.4999999999927 | 2878.5 | 10.1 | 85.29028959233953 | 3270.4 | 0 | 388.0999999999931 | 60 |  | 33.31597222222222 | 2878.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
2 | 145 | 445 | 590 | 0 | 0 | 3 | 590 | 70 | 3.599999999998545 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.1 | 7039.999999999993 | 41.872 | 3652.74 | -1200 | 4759 | 5959 | 10.1 | 86.3032383998495 | 4780.4 | 0 | 38.599999999999454 | 60 |  | 68.9699074074074 | 5959 | 2018 | 7 | 2018_07_Asomata_english.xlsx
3 | 480 | 90 | 570 | 0 | 0 | 3 | 570 | 89 | 10.19999999999709 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.1 | 7039.999999999993 | 41.66 | 3404.7 | 0 | 5700 | 5700 | 10 | 87.16627078384799 | 5549.25 | 0 | 150.75 | 0 |  | 65.97222222222223 | 5700 | 2018 | 7 | 2018_07_Asomata_english.xlsx
4 | 0 | 495 | 495 | 0 | 0 | 4 | 495 | 45 | 0 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.8 | 8720 | 42.049 | 3859.83 | 1680.0000000000073 | 6679.500000000007 | 4999.5 | 10.1 | 84.89173683723513 | 6555.4 | 0 | 124.10000000000764 | 0 |  | 57.864583333333336 | 4999.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
5 | 540 | 65 | 605 | 0 | 0 | 4 | 605 | 53 | 12.099999999998545 | 1.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.65 | 8360.00000000002 | 41.851 | 3628.17 | -359.99999999998 | 5750.50000000002 | 6110.5 | 10.1 | 85.19030097617029 | 5563.95 | 0 | 186.5500000000211 | 0 |  | 70.72337962962963 | 6110.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
6 | 0 | 485 | 485 | 0 | 0 | 3 | 485 | 53 | 0 | 11.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.9 | 8960.00000000002 | 41.999 | 3801.3300000000063 | 600 | 5498.5 | 4898.5 | 10.1 | 84.6938540007847 | 5368.05 | 0 | 130.45 | 0 |  | 56.695601851851855 | 4898.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
7 | 350 | 105 | 455 | 0 | 0 | 4 | 455 | 53 | 8.200000000004366 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.6 | 8239.999999999993 | 41.468 | 3180.06 | -720.0000000000273 | 3875.4999999999727 | 4595.5 | 10.1 | 85.29028959233953 | 3665.4 | 0 | 210.09999999997262 | 0 |  | 53.188657407407405 | 4595.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
8 | 0 | 355 | 355 | 0 | 0 | 3 | 355 | 45 | 0 | 8.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.7 | 8480.000000000015 | 41.261 | 2937.87 | 240.00000000002183 | 5027.627659574489 | 3585.5 | 10.1 | 85.09054652537853 | 4730.4 | 1202.127659574468 | 297.22765957448973 | 0 |  | 41.498842592592595 | 3585.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
9 | 435 | 10 | 445 | 0 | 0 | 4 | 445 | 45 | 9.849999999998545 | 0.10000000000582077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.4 | 7760.00000000002 | 41.6 | 3334.5 | -719.9999999999945 | 3774.5000000000055 | 4494.5 | 10.1 | 85.69260227909582 | 3577 | 0 | 197.50000000000546 | 0 |  | 52.019675925925924 | 4494.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
10 | 5 | 485 | 490 | 0 | 0 | 4 | 490 | 45 | 0.1500000000014552 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.65 | 8360.00000000002 | 41.652 | 3395.34 | 600 | 5500 | 4900 | 10 | 86.04220398593199 | 5210.28 | 0 | 289.72 | 0 |  | 56.71296296296296 | 4900 | 2018 | 7 | 2018_07_Asomata_english.xlsx
11 | 0 | 515 | 515 | 0 | 0 | 3 | 515 | 54 | 0 | 12.049999999995634 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Αποκατάσταση βλάβης υδραυλ. Κυκλ. Υδροληψίας | 11 | 84.85 | 8839.999999999993 | 41.853 | 3630.51 | 479.9999999999727 | 5681.499999999973 | 5201.5 | 10.1 | 84.79267996811352 | 5498.1 | 0 | 183.39999999997235 | 0 |  | 60.2025462962963 | 5201.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
12 | 475 | 0 | 475 | 0 | 0 | 4 | 475 | 45 | 10.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0 | 2 | 0 | Αποκατάσταση βλάβης υδραυλ. Κυκλ. Υδροληψίας | 12 | 84.8 | 8720 | 41.84 | 3615.3 | -119.99999999999272 | 4630.000000000007 | 4750 | 10 | 85.74065420560747 | 4241.3 | 0 | 388.7000000000071 | 0 |  | 54.976851851851855 | 4750 | 2018 | 7 | 2018_07_Asomata_english.xlsx
13 | 260 | 265 | 525 | 0 | 0 | 3 | 525 | 55 | 5.700000000004366 | 5.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.7 | 8480.000000000015 | 41.829 | 3602.43 | -239.99999999998545 | 5062.500000000015 | 5302.5 | 10.1 | 85.09054652537853 | 5078.85 | 0 | 43.6500000000151 | 60 |  | 61.37152777777778 | 5302.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
14 | 385 | 220 | 605 | 0 | 0 | 3 | 605 | 45 | 9.19999999999709 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.6 | 8239.999999999993 | 41.788 | 3554.4599999999914 | -240.00000000002183 | 5749.499999999978 | 5989.5 | 9.9 | 87.01332574572012 | 5439 | 0 | 310.4999999999782 | 0 |  | 69.32291666666667 | 5989.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
15 | 470 | 30 | 500 | 0 | 0 | 4 | 500 | 45 | 10.5 | 0.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.75 | 8600.000000000007 | 41.6 | 3334.5 | 360.00000000001455 | 5260.000000000015 | 4900 | 9.8 | 87.59279150256593 | 4950.6 | 0 | 309.4000000000142 | 0 |  | 56.71296296296296 | 4900 | 2018 | 7 | 2018_07_Asomata_english.xlsx
16 | 5 | 560 | 565 | 0 | 0 | 4 | 565 | 53 | 0.09999999999854481 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000.000000000007 | 41.847 | 3623.49 | -600 | 5106.5 | 5706.5 | 10.1 | 85.49097262667443 | 5058.5 | 0 | 108 | 60 |  | 66.04745370370371 | 5706.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
17 | 225 | 360 | 585 | 0 | 0 | 3 | 585 | 55 | 5.05000000000291 | 7.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.9 | 8960.00000000002 | 41.866 | 3645.72 | 960.0000000000127 | 6751.500000000013 | 5791.5 | 9.9 | 86.40484095029548 | 6681.75 | 0 | 69.75000000001364 | 0 |  | 67.03125 | 5791.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
18 | 35 | 753 | 788 | 0 | 0 | 4 | 788 | 55 | 1 | 14.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 85.25 | 9800.000000000007 | 41.8 | 3568.5 | 839.9999999999873 | 8719.999999999987 | 7880 | 10 | 84.84855491329479 | 8493.75 | 0 | 226.24999999998727 | 0 |  | 91.20370370370371 | 7880 | 2018 | 7 | 2018_07_Asomata_english.xlsx
19 | 305 | 435 | 740 | 0 | 0 | 4 | 740 | 108 | 6.150000000001455 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 85 | 9200.000000000007 | 41.983 | 3782.6099999999915 | -600 | 6689 | 7289 | 9.85 | 86.6414827057018 | 6445.4 | 0 | 243.59999999999945 | 0 |  | 84.36342592592592 | 7289 | 2018 | 7 | 2018_07_Asomata_english.xlsx
20 | 25 | 645 | 670 | 0 | 0 | 3 | 670 | 83 | 0.7999999999956344 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.9 | 8960.00000000002 | 41.9 | 3685.5 | -239.99999999998727 | 6527.000000000013 | 6767 | 10.1 | 84.6938540007847 | 6615.6 | 0 | 31.40000000001237 | 120 |  | 78.32175925925925 | 6767 | 2018 | 7 | 2018_07_Asomata_english.xlsx
21 | 625 | 35 | 660 | 0 | 0 | 0 | 660 | 90 | 12.80000000000291 | 0.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 21 | 84.25 | 7400.000000000007 | 41.662 | 3407.04 | -1560.0000000000127 | 5039.999999999987 | 6600 | 10 | 86.85680473372781 | 4812.7 | 0 | 227.29999999998654 | 0 |  | 76.38888888888889 | 6600 | 2018 | 7 | 2018_07_Asomata_english.xlsx
22 | 32 | 615 | 647 | 0 | 0 | 8 | 647 | 53 | 0.9000000000014552 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.25 | 7400.000000000007 | 41.85 | 3627 | 0 | 6534.7 | 6534.7 | 10.1 | 85.99683637002754 | 6449.3 | 0 | 145.40000000000055 | 60 |  | 75.63310185185185 | 6534.7 | 2018 | 7 | 2018_07_Asomata_english.xlsx
23 | 698 | 20 | 718 | 0 | 0 | 0 | 718 | 53 | 15.099999999998545 | 0.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.2 | 7280.000000000014 | 41.859 | 3637.5300000000066 | -119.99999999999363 | 7131.800000000007 | 7251.8 | 10.1 | 86.09872835624795 | 7027.2 | 0 | 164.60000000000673 | 60 |  | 83.93287037037037 | 7251.8 | 2018 | 7 | 2018_07_Asomata_english.xlsx
24 | 0 | 645 | 645 | 0 | 0 | 0 | 645 | 55 | 0 | 13.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.25 | 7400.000000000007 | 42.08 | 3896.1 | 119.99999999999363 | 6666.749999999994 | 6546.75 | 10.15 | 85.57320663421459 | 6664 | 0 | 62.74999999999363 | 60 |  | 75.77256944444444 | 6546.75 | 2018 | 7 | 2018_07_Asomata_english.xlsx
25 | 705 | 130 | 835 | 0 | 0 | 4 | 835 | 110 | 14.599999999998545 | 3.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.3 | 7520 | 42.05 | 3861 | 119.99999999999272 | 8553.499999999993 | 8433.5 | 10.1 | 85.89518526320718 | 8288 | 0 | 265.4999999999927 | 0 |  | 97.60995370370371 | 8433.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
26 | 0 | 620 | 620 | 0 | 0 | 9 | 620 | 55 | 0 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.3 | 7520 | 42 | 3802.5 | 0 | 6262 | 6262 | 10.1 | 85.89518526320718 | 6285.3 | 0 | 36.69999999999982 | 60 |  | 72.47685185185185 | 6262 | 2018 | 7 | 2018_07_Asomata_english.xlsx
27 | 655 | 110 | 765 | 0 | 0 | 4 | 765 | 90 | 13.900000000001455 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 83.5 | 5600.000000000007 | 42.05 | 3861 | -1919.9999999999927 | 5959.500000000008 | 7879.5 | 10.3 | 85.85097672242367 | 6000.6 | 0 | 18.90000000000782 | 60 |  | 91.19791666666667 | 7879.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
28 | 130 | 650 | 780 | 0 | 0 | 4 | 780 | 109 | 3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 28 | 83.3 | 5120 | 42.052 | 3863.34 | -480.0000000000073 | 7397.999999999993 | 7878 | 10.1 | 87.97497183132359 | 7363.59 | 0 | 94.40999999999258 | 60 |  | 91.18055555555556 | 7878 | 2018 | 7 | 2018_07_Asomata_english.xlsx
29 | 500 | 85 | 585 | 6 | 0 | 0 | 585 | 53 | 10.80000000000291 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.1 | 7039.999999999993 | 41.8 | 3568.5 | 1919.9999999999927 | 7828.499999999993 | 5908.5 | 10.1 | 86.3032383998495 | 7665 | 0 | 163.49999999999272 | 0 |  | 68.38541666666667 | 5908.5 | 2018 | 7 | 2018_07_Asomata_english.xlsx
30 | 123 | 685 | 808 | 0 | 0 | 6 | 808 | 80 | 3.099999999998545 | 13.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 83.5 | 5600.000000000007 | 41.999 | 3801.3300000000063 | -1439.9999999999854 | 6720.800000000015 | 8160.8 | 10.1 | 87.55099606346177 | 6775.56 | 0 | 5.240000000015243 | 60 |  | 94.45370370370371 | 8160.8 | 2018 | 7 | 2018_07_Asomata_english.xlsx
31 | 562 | 108 | 670 | 0 | 0 | 4 | 670 | 90 | 11 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 84 | 6800.000000000007 | 41.902 | 3687.84 | 1200 | 7967 | 6767 | 10.1 | 86.50872230080151 | 7865 | 0 | 162 | 60 |  | 78.32175925925925 | 6767 | 2018 | 7 | 2018_07_Asomata_english.xlsx
1 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.25 | 7400.000000000007 | 41.805 | 3574.35 | 600 | 7316.5 | 6716.5 | 10.1 | 85.99683637002754 | 7356.12 | 0 | 20.38000000000011 | 60 |  | 77.73726851851852 | 6716.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
2 | 267 | 368 | 635 | 0 | 0 | 4 | 635 | 54 | 5.400000000001455 | 7.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.8 | 6320 | 41.788 | 3554.4599999999914 | -1080.0000000000073 | 5587.499999999993 | 6667.5 | 10.5 | 83.61130097972203 | 5555.3 | 0 | 92.19999999999345 | 60 |  | 77.17013888888889 | 6667.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
3 | 648 | 67 | 715 | 0 | 0 | 4 | 715 | 106 | 12.75 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.15 | 7160.00000000002 | 41.798 | 3566.16 | 840.00000000002 | 8061.50000000002 | 7221.5 | 10.1 | 86.20086207909047 | 8043.8 | 0 | 17.700000000018917 | 0 |  | 83.58217592592592 | 7221.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
4 | 0 | 502 | 502 | 0 | 0 | 3 | 502 | 45 | 0 | 11.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.3 | 7520 | 41.41 | 3112.2 | 359.99999999998 | 5430.19999999998 | 5070.2 | 10.1 | 85.89518526320718 | 5415 | 0 | 75.19999999997981 | 60 |  | 58.682870370370374 | 5070.2 | 2018 | 8 | 2018_08_Asomata_english.xlsx
5 | 535 | 6 | 541 | 0 | 0 | 4 | 541 | 45 | 12.25 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480.000000000015 | 42.049 | 3859.83 | 960.0000000000146 | 6900.290476190491 | 5464.1 | 10.1 | 85.09054652537851 | 6898.7 | 476.1904761904762 | 61.590476190490335 | 60 |  | 63.241898148148145 | 5464.1 | 2018 | 8 | 2018_08_Asomata_english.xlsx
6 | 13 | 571 | 584 | 0 | 0 | 3 | 584 | 53 | 0.4000000000014552 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.45 | 7880.000000000014 | 41.77 | 3533.4 | -600.0000000000009 | 5298.4 | 5898.4 | 10.1 | 85.5916687075068 | 5100 | 0 | 198.39999999999873 | 0 |  | 68.26851851851852 | 5898.4 | 2018 | 8 | 2018_08_Asomata_english.xlsx
7 | 505 | 90 | 595 | 0 | 0 | 4 | 595 | 79 | 11.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.15 | 7160.00000000002 | 41.64 | 3381.3 | -719.9999999999936 | 5289.500000000006 | 6009.5 | 10.1 | 86.20086207909047 | 5299.8 | 0 | 19.700000000006185 | 30 |  | 69.55439814814815 | 6009.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
8 | 0 | 485 | 485 | 0 | 0 | 3 | 485 | 45 | 0 | 11.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.1 | 7039.999999999993 | 41.952 | 3746.34 | -120.00000000002728 | 4778.499999999973 | 4898.5 | 10.1 | 86.3032383998495 | 4708.5 | 0 | 129.99999999997272 | 60 |  | 56.695601851851855 | 4898.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
9 | 485 | 0 | 485 | 0 | 0 | 4 | 485 | 45 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 41.798 | 3566.16 | 480.0000000000073 | 5330.000000000007 | 4850 | 10 | 86.75413711583924 | 5224.6 | 0 | 105.40000000000782 | 0 |  | 56.13425925925926 | 4850 | 2018 | 8 | 2018_08_Asomata_english.xlsx
10 | 0 | 508 | 508 | 0 | 0 | 4 | 508 | 45 | 0 | 11.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.3 | 7520 | 41.76 | 3521.7 | 0 | 5080 | 5080 | 10 | 86.75413711583924 | 5050.95 | 0 | 29.050000000000182 | 0 |  | 58.7962962962963 | 5080 | 2018 | 8 | 2018_08_Asomata_english.xlsx
11 | 485 | 0 | 485 | 0 | 0 | 3 | 485 | 45 | 10.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.45 | 7880.000000000014 | 41.842 | 3617.64 | 360.00000000001364 | 5210.000000000014 | 4850 | 10 | 86.44758539458186 | 5110 | 0 | 100.00000000001364 | 0 |  | 56.13425925925926 | 4850 | 2018 | 8 | 2018_08_Asomata_english.xlsx
12 | 15 | 485 | 500 | 0 | 0 | 4 | 500 | 45 | 0.39999999999417923 | 10.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 83.9 | 6560.00000000002 | 41.809 | 3579.03 | -1319.9999999999936 | 3680.0000000000064 | 5000 | 10 | 87.58233890214795 | 3503.2 | 0 | 176.80000000000655 | 0 |  | 57.870370370370374 | 5000 | 2018 | 8 | 2018_08_Asomata_english.xlsx
13 | 517 | 0 | 517 | 0 | 0 | 3 | 517 | 45 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.9 | 6560.00000000002 | 41.698 | 3449.16 | 0 | 5221.7 | 5221.7 | 10.1 | 86.71518703182966 | 5168.4 | 0 | 113.3 | 60 |  | 60.436342592592595 | 5221.7 | 2018 | 8 | 2018_08_Asomata_english.xlsx
14 | 0 | 490 | 490 | 0 | 0 | 4 | 490 | 45 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84 | 6800.000000000007 | 41.4 | 3100.5 | 239.99999999998727 | 5188.999999999987 | 4949 | 10.1 | 86.50872230080151 | 5145 | 0 | 43.99999999998727 | 0 |  | 57.280092592592595 | 4949 | 2018 | 8 | 2018_08_Asomata_english.xlsx
15 | 471 | 5 | 476 | 0 | 0 | 3 | 476 | 45 | 10.900000000001455 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.55 | 5720 | 41.22 | 2889.9 | -1080.0000000000073 | 3821.799999999993 | 4901.8 | 10.297899159663865 | 85.76515937881608 | 3810 | 0 | 11.799999999992906 | 0 |  | 56.7337962962963 | 4901.8 | 2018 | 8 | 2018_08_Asomata_english.xlsx
16 | 0 | 532 | 532 | 0 | 0 | 4 | 532 | 45 | 0 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 83.6 | 5839.999999999993 | 41.33 | 3018.6 | 119.99999999999272 | 5439.999999999993 | 5320 | 10 | 88.21394230769232 | 5436 | 0 | 3.999999999992724 | 0 |  | 61.574074074074076 | 5320 | 2018 | 8 | 2018_08_Asomata_english.xlsx
17 | 528 | 5 | 533 | 0 | 0 | 3 | 533 | 55 | 11.900000000001455 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 83.7 | 6080.000000000014 | 41.31 | 2995.2 | 240.00000000002092 | 5570.000000000021 | 5330 | 10 | 88.00239808153478 | 5343.6 | 0 | 226.40000000002055 | 0 |  | 61.68981481481482 | 5330 | 2018 | 8 | 2018_08_Asomata_english.xlsx
18 | 7 | 573 | 580 | 0 | 0 | 4 | 580 | 50 | 0.19999999999708962 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.7 | 8480.000000000015 | 41.668 | 3414.06 | 2400 | 8113 | 5713 | 9.85 | 87.25020506663179 | 7905.3 | 0 | 207.70000000000164 | 0 |  | 66.12268518518519 | 5713 | 2018 | 8 | 2018_08_Asomata_english.xlsx
19 | 569 | 49 | 618 | 0 | 0 | 4 | 618 | 55 | 12.5 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.95 | 9080.000000000015 | 41.839 | 3614.13 | 600 | 6656.4 | 6056.4 | 9.8 | 87.18490888788575 | 6508.1 | 0 | 148.3 | 0 |  | 70.09722222222223 | 6056.4 | 2018 | 8 | 2018_08_Asomata_english.xlsx
20 | 39 | 651 | 690 | 0 | 0 | 3 | 690 | 55 | 1.1000000000058208 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.65 | 8360.00000000002 | 41.902 | 3687.84 | -719.9999999999945 | 6249 | 6969 | 10.1 | 85.1903009761703 | 6250.55 | 0 | 28.450000000004366 | 30 |  | 80.65972222222221 | 6969 | 2018 | 8 | 2018_08_Asomata_english.xlsx
21 | 601 | 230 | 831 | 0 | 0 | 4 | 831 | 109 | 11.799999999995634 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.5 | 8000.000000000007 | 41.901 | 3686.67 | -360.00000000001273 | 7949.999999999987 | 8310 | 10 | 86.34588235294117 | 7912.5 | 0 | 37.49999999998727 | 0 |  | 96.18055555555556 | 8310 | 2018 | 8 | 2018_08_Asomata_english.xlsx
22 | 250 | 675 | 925 | 0 | 0 | 4 | 925 | 109 | 5.700000000004366 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.9 | 8960.00000000002 | 41.902 | 3687.84 | 960.0000000000127 | 10302.5 | 9342.5 | 10.1 | 84.6938540007847 | 10209.15 | 0 | 93.3500000000131 | 0 |  | 108.13078703703704 | 9342.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
23 | 670 | 210 | 880 | 0 | 0 | 3 | 880 | 90 | 14.799999999995634 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480.000000000015 | 41.95 | 3744 | -480.00000000000546 | 8407.999999999995 | 8888 | 10.1 | 85.09054652537853 | 8321.65 | 0 | 146.3499999999931 | 60 |  | 102.87037037037037 | 8888 | 2018 | 8 | 2018_08_Asomata_english.xlsx
24 | 185 | 580 | 765 | 0 | 0 | 4 | 765 | 90 | 3.900000000001455 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.8 | 8720 | 41.902 | 3687.84 | 239.99999999998545 | 7889.999999999985 | 7650 | 10 | 85.74065420560747 | 7844.94 | 0 | 45.05999999998494 | 0 |  | 88.54166666666667 | 7650 | 2018 | 8 | 2018_08_Asomata_english.xlsx
25 | 540 | 0 | 540 | 0 | 0 | 3 | 540 | 45 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.7 | 8480.000000000015 | 41.702 | 3453.84 | -239.99999999998545 | 5160.000000000015 | 5400 | 10 | 85.94145199063232 | 5043.65 | 0 | 116.35000000001492 | 0 |  | 62.5 | 5400 | 2018 | 8 | 2018_08_Asomata_english.xlsx
26 | 45 | 480 | 525 | 0 | 0 | 4 | 525 | 46 | 1.1999999999970896 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.65 | 8360.00000000002 | 41.949 | 3742.83 | -119.99999999999454 | 5182.5000000000055 | 5302.5 | 10.1 | 85.19030097617029 | 4995 | 0 | 187.50000000000546 | 0 |  | 61.37152777777778 | 5302.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
27 | 107 | 380 | 487 | 0 | 0 | 0 | 487 | 90 | 2.2000000000043656 | 8.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 84.9 | 8960.00000000002 | 41.809 | 3579.03 | 600 | 5470 | 4870 | 10 | 85.54079254079252 | 5365.5 | 0 | 104.5 | 0 |  | 56.36574074074074 | 4870 | 2018 | 8 | 2018_08_Asomata_english.xlsx
28 | 0 | 500 | 500 | 0 | 0 | 0 | 500 | 45 | 0 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.8 | 8720 | 41.331 | 3019.77 | -240.00000000002 | 4759.99999999998 | 5000 | 10 | 85.74065420560747 | 4498.2 | 0 | 261.7999999999802 | 0 |  | 57.870370370370374 | 5000 | 2018 | 8 | 2018_08_Asomata_english.xlsx
29 | 363 | 140 | 503 | 0 | 0 | 10 | 503 | 90 | 8.599999999998545 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 29 | 84.8 | 8720 | 41.901 | 3686.67 | 0 | 5080.3 | 5080.3 | 10.1 | 84.89173683723516 | 4945.25 | 0 | 135.04999999999927 | 0 |  | 58.799768518518505 | 5080.3 | 2018 | 8 | 2018_08_Asomata_english.xlsx
30 | 0 | 595 | 595 | 0 | 0 | 4 | 595 | 45 | 0 | 13.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85 | 9200.000000000007 | 42.05 | 3861 | 480.0000000000073 | 6489.500000000007 | 6009.5 | 10.1 | 84.49689154962007 | 6193.8 | 0 | 295.7000000000071 | 0 |  | 69.55439814814815 | 6009.5 | 2018 | 8 | 2018_08_Asomata_english.xlsx
31 | 570 | 0 | 570 | 0 | 0 | 3 | 570 | 53 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.8 | 8720 | 41.799 | 3567.33 | -480.0000000000073 | 5276.999999999993 | 5757 | 10.1 | 84.89173683723513 | 5161.1 | 0 | 175.89999999999327 | 60 |  | 66.63194444444444 | 5757 | 2018 | 8 | 2018_08_Asomata_english.xlsx
1 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.85 | 8839.999999999993 | 41.702 | 3453.84 | 119.99999999999272 | 6634.499999999993 | 6514.5 | 10.1 | 84.79267996811352 | 6576.05 | 0 | 58.44999999999345 | 0 |  | 75.39930555555556 | 6514.5 | 2018 | 9 | 2018_09_Asomata_english.xlsx
2 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 55 | 0 | 10.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.85 | 8839.999999999993 | 41.752 | 3512.34 | 0 | 4998 | 4998 | 9.8 | 87.38837425285168 | 4952.8 | 0 | 45.19999999999982 | 0 |  | 57.84722222222222 | 4998 | 2018 | 9 | 2018_09_Asomata_english.xlsx
3 | 745 | 5 | 750 | 0 | 0 | 3 | 750 | 53 | 14.30000000000291 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.8 | 8720 | 41.87 | 3650.4 | -119.99999999999272 | 7455.000000000007 | 7575 | 10.1 | 84.89173683723513 | 7343.8 | 0 | 171.200000000008 | 60 |  | 87.67361111111111 | 7575 | 2018 | 9 | 2018_09_Asomata_english.xlsx
4 | 0 | 740 | 740 | 0 | 0 | 4 | 740 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.05 | 9320 | 41.978 | 3776.76 | 600 | 7815 | 7215 | 9.75 | 87.4284523065011 | 7725.65 | 0 | 89.34999999999945 | 0 |  | 83.50694444444444 | 7215 | 2018 | 9 | 2018_09_Asomata_english.xlsx
5 | 227 | 475 | 702 | 0 | 0 | 3 | 702 | 106 | 4.650000000001455 | 9.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 5 | 84 | 6800.000000000007 | 41.999 | 3801.3300000000063 | -2519.9999999999927 | 4570.200000000007 | 7090.2 | 10.1 | 86.50872230080151 | 4572 | 0 | 58.200000000007094 | 60 |  | 82.0625 | 7090.2 | 2018 | 9 | 2018_09_Asomata_english.xlsx
6 | 0 | 600 | 600 | 0 | 0 | 4 | 600 | 55 | 0 | 11.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.4 | 7760.00000000002 | 41.649 | 3391.83 | 960.0000000000127 | 7080.000000000013 | 6120 | 10.2 | 84.85247872733999 | 7142.65 | 0 | 27.350000000013097 | 90 |  | 70.83333333333333 | 6120 | 2018 | 9 | 2018_09_Asomata_english.xlsx
7 | 595 | 0 | 595 | 0 | 0 | 3 | 595 | 54 | 11.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.25 | 7400.000000000007 | 41.679 | 3426.9300000000067 | -360.00000000001273 | 5530.499999999987 | 5890.5 | 9.9 | 87.73414619568464 | 5550 | 0 | 40.49999999998727 | 60 |  | 68.17708333333333 | 5890.5 | 2018 | 9 | 2018_09_Asomata_english.xlsx
8 | 0 | 535 | 535 | 0 | 0 | 4 | 535 | 54 | 0 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.1 | 7039.999999999993 | 41.669 | 3415.23 | -360.00000000001455 | 5043.499999999985 | 5403.5 | 10.1 | 86.3032383998495 | 5090.7 | 0 | 12.79999999998563 | 60 |  | 62.54050925925926 | 5403.5 | 2018 | 9 | 2018_09_Asomata_english.xlsx
9 | 424 | 117 | 541 | 0 | 0 | 4 | 541 | 89 | 9.30000000000291 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.15 | 7160.00000000002 | 41.827 | 3600.09 | 120.00000000002728 | 5530.000000000027 | 5410 | 10 | 87.06287069988136 | 5433.08 | 0 | 96.92000000002736 | 0 |  | 62.61574074074074 | 5410 | 2018 | 9 | 2018_09_Asomata_english.xlsx
10 | 90 | 610 | 700 | 0 | 0 | 2 | 700 | 108 | 1.8499999999985448 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.4 | 7760.00000000002 | 41.758 | 3519.36 | 600 | 7670 | 7070 | 10.1 | 85.69260227909582 | 7504.4 | 0 | 165.6 | 0 |  | 81.82870370370371 | 7070 | 2018 | 9 | 2018_09_Asomata_english.xlsx
11 | 626 | 0 | 626 | 0 | 0 | 3 | 626 | 54 | 12.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.2 | 7280.000000000014 | 41.439 | 3146.13 | -480.00000000000637 | 5779.999999999994 | 6260 | 10 | 86.95971563981043 | 5571.3 | 0 | 208.69999999999436 | 0 |  | 72.45370370370371 | 6260 | 2018 | 9 | 2018_09_Asomata_english.xlsx
12 | 0 | 573 | 573 | 0 | 0 | 4 | 573 | 54 | 0 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.2 | 7280.000000000014 | 41.891 | 3674.9699999999934 | 0 | 5787.3 | 5787.3 | 10.1 | 86.09872835624795 | 5690.6 | 0 | 96.69999999999982 | 0 |  | 66.98263888888889 | 5787.3 | 2018 | 9 | 2018_09_Asomata_english.xlsx
13 | 558 | 70 | 628 | 0 | 0 | 3 | 628 | 110 | 11.599999999998545 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.7 | 8480.000000000015 | 41.841 | 3616.47 | 1200 | 7480 | 6280 | 10 | 85.94145199063232 | 7443.45 | 0 | 36.55000000000018 | 0 |  | 72.68518518518519 | 6280 | 2018 | 9 | 2018_09_Asomata_english.xlsx
14 | 105 | 570 | 675 | 0 | 0 | 4 | 675 | 90 | 2.900000000001455 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.3 | 7520 | 41.631 | 3370.77 | -960.0000000000146 | 5857.499999999985 | 6817.5 | 10.1 | 85.89518526320718 | 5740.35 | 0 | 117.149999999986 | 0 |  | 78.90625 | 6817.5 | 2018 | 9 | 2018_09_Asomata_english.xlsx
15 | 490 | 0 | 490 | 0 | 0 | 3 | 490 | 55 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.15 | 7160.00000000002 | 41.27 | 2948.4 | -359.99999999998 | 4589.00000000002 | 4949 | 10.1 | 86.20086207909047 | 4569.8 | 0 | 79.20000000002074 | 60 |  | 57.280092592592595 | 4949 | 2018 | 9 | 2018_09_Asomata_english.xlsx
16 | 0 | 455 | 455 | 0 | 0 | 4 | 455 | 54 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000.000000000007 | 41.901 | 3686.67 | 839.9999999999873 | 5435.499999999987 | 4595.5 | 10.1 | 85.49097262667443 | 5267.15 | 0 | 168.34999999998763 | 0 |  | 53.188657407407405 | 4595.5 | 2018 | 9 | 2018_09_Asomata_english.xlsx
17 | 225 | 355 | 580 | 0 | 0 | 3 | 580 | 108 | 4.5 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 17 | 84.15 | 7160.00000000002 | 41.65 | 3393 | -839.9999999999873 | 5018.000000000013 | 5858 | 10.1 | 86.20086207909047 | 4792.2 | 0 | 225.80000000001291 | 0 |  | 67.80092592592592 | 5858 | 2018 | 9 | 2018_09_Asomata_english.xlsx
18 | 0 | 425 | 425 | 0 | 0 | 3 | 425 | 55 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.3 | 7520 | 41.681 | 3429.2699999999936 | 359.99999999998 | 4652.49999999998 | 4292.5 | 10.1 | 85.89518526320718 | 4612.5 | 0 | 39.99999999997999 | 0 |  | 49.68171296296296 | 4292.5 | 2018 | 9 | 2018_09_Asomata_english.xlsx
19 | 472 | 0 | 472 | 0 | 0 | 4 | 472 | 54 | 10.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.05 | 6920 | 41.58 | 3311.1 | -600 | 4120 | 4720 | 10 | 87.26991676575506 | 4054.35 | 0 | 65.65000000000009 | 0 |  | 54.629629629629626 | 4720 | 2018 | 9 | 2018_09_Asomata_english.xlsx
20 | 0 | 468 | 468 | 0 | 0 | 3 | 468 | 55 | 0 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.7 | 6080.000000000014 | 41.707 | 3459.69 | -839.9999999999864 | 3886.800000000014 | 4726.8 | 10.1 | 87.13108720944037 | 3927.4 | 0 | 19.400000000013733 | 60 |  | 54.708333333333336 | 4726.8 | 2018 | 9 | 2018_09_Asomata_english.xlsx
21 | 434 | 0 | 434 | 0 | 0 | 4 | 434 | 55 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.6999 | 3451.3829999999975 | 1439.9999999999864 | 5736.599999999987 | 4296.6 | 9.9 | 87.63044153115075 | 5602.1 | 0 | 134.49999999998727 | 0 |  | 49.729166666666664 | 4296.6 | 2018 | 9 | 2018_09_Asomata_english.xlsx
22 | 0 | 482 | 482 | 0 | 0 | 3 | 482 | 55 | 0 | 9.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.2 | 7280.000000000014 | 41.829 | 3602.43 | -239.99999999998636 | 4628.2000000000135 | 4868.2 | 10.1 | 86.09872835624795 | 4658.35 | 0 | 29.850000000014006 | 60 |  | 56.344907407407405 | 4868.2 | 2018 | 9 | 2018_09_Asomata_english.xlsx
23 | 335 | 95 | 430 | 0 | 0 | 4 | 430 | 110 | 7.80000000000291 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.1 | 7039.999999999993 | 41.86 | 3638.7 | -240.00000000002092 | 4102.999999999979 | 4343 | 10.1 | 86.3032383998495 | 4146.4 | 0 | 16.599999999979445 | 60 |  | 50.2662037037037 | 4343 | 2018 | 9 | 2018_09_Asomata_english.xlsx
24 | 0 | 442 | 442 | 0 | 0 | 3 | 442 | 55 | 0 | 9.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.25 | 7400.000000000007 | 41.989 | 3789.63 | 360.00000000001455 | 4868.400000000014 | 4508.4 | 10.2 | 85.1537301311057 | 4679.3 | 0 | 189.10000000001492 | 0 |  | 52.18055555555556 | 4508.4 | 2018 | 9 | 2018_09_Asomata_english.xlsx
25 | 219 | 0 | 219 | 0 | 0 | 3 | 219 | 40 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.35 | 7639.999999999993 | 40.98 | 2609.1 | 239.99999999998545 | 2397.1499999999855 | 2157.15 | 9.85 | 87.97128114156266 | 2102.4 | 0 | 354.74999999998545 | 60 |  | 24.96701388888889 | 2157.15 | 2018 | 9 | 2018_09_Asomata_english.xlsx
26 | 0 | 298 | 298 | 0 | 0 | 4 | 298 | 40 | 0 | 7.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.5 | 8000.000000000007 | 41.36 | 3053.7 | 360.00000000001455 | 3310.200000000015 | 2950.2 | 9.9 | 87.21806298276887 | 3196.05 | 0 | 114.15000000001464 | 0 |  | 34.145833333333336 | 2950.2 | 2018 | 9 | 2018_09_Asomata_english.xlsx
27 | 335 | 0 | 335 | 0 | 0 | 3 | 335 | 54 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84 | 6800.000000000007 | 41.85 | 3627 | -1200 | 2183.5 | 3383.5 | 10.1 | 86.50872230080151 | 2196.75 | 0 | 46.75 | 60 |  | 39.160879629629626 | 3383.5 | 2018 | 9 | 2018_09_Asomata_english.xlsx
28 | 0 | 250 | 250 | 0 | 0 | 4 | 250 | 40 | 0 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.1 | 7039.999999999993 | 41.85 | 3627 | 239.99999999998545 | 2764.9999999999854 | 2525 | 10.1 | 86.3032383998495 | 2664.5 | 0 | 100.49999999998545 | 0 |  | 29.224537037037038 | 2525 | 2018 | 9 | 2018_09_Asomata_english.xlsx
29 | 290 | 0 | 290 | 0 | 0 | 3 | 290 | 40 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84 | 6800.000000000007 | 41.655 | 3398.85 | -239.99999999998545 | 2689.0000000000146 | 2929 | 10.1 | 86.50872230080151 | 2752.5 | 0 | 16.500000000014552 | 80 |  | 33.90046296296296 | 2929 | 2018 | 9 | 2018_09_Asomata_english.xlsx
30 | 0 | 210 | 210 | 0 | 0 | 3 | 210 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.55 | 8120 | 41.149 | 2806.83 | 1319.9999999999927 | 3377.9999999999927 | 2058 | 9.8 | 88.00450850140291 | 2997.35 | 0 | 380.6499999999928 | 0 |  | 23.819444444444443 | 2058 | 2018 | 9 | 2018_09_Asomata_english.xlsx
1 | 245 | 0 | 245 | 0 | 0 | 3 | 245 | 40 | 6.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84 | 6800.000000000007 | 41.39 | 3088.8 | -1319.9999999999927 | 1154.5000000000073 | 2474.5 | 10.1 | 86.50872230080151 | 1200 | 0 | 14.500000000007276 | 60 |  | 28.640046296296298 | 2474.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
2 | 0 | 190 | 190 | 0 | 0 | 3 | 190 | 40 | 0 | 5.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84 | 6800.000000000007 | 41.362 | 3056.04 | 0 | 1919 | 1919 | 10.1 | 86.50872230080151 | 1895.7 | 0 | 83.30000000000018 | 60 |  | 22.21064814814815 | 1919 | 2018 | 10 | 2018_10_Asomata_english.xlsx
3 | 175 | 0 | 175 | 0 | 0 | 4 | 175 | 40 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.3 | 7520 | 41.203 | 2870.01 | 719.9999999999927 | 2487.4999999999927 | 1767.5 | 10.1 | 85.89518526320718 | 2446.2 | 0 | 41.299999999992906 | 0 |  | 20.457175925925927 | 1767.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
4 | 0 | 385 | 385 | 0 | 0 | 4 | 385 | 54 | 0 | 8.64999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.7 | 8480.000000000015 | 41.801 | 3569.67 | 960.0000000000146 | 4810.000000000015 | 3850 | 10 | 85.94145199063232 | 4635.5 | 0 | 234.50000000001455 | 60 |  | 44.56018518518518 | 3850 | 2018 | 10 | 2018_10_Asomata_english.xlsx
5 | 190 | 0 | 190 | 0 | 0 | 3 | 190 | 40 | 4.850000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.85 | 8839.999999999993 | 40.782 | 2377.44 | 359.9999999999782 | 2278.999999999978 | 1919 | 10.1 | 84.79267996811352 | 2220 | 0 | 58.99999999997817 | 0 |  | 22.21064814814815 | 1919 | 2018 | 10 | 2018_10_Asomata_english.xlsx
6 | 0 | 150 | 150 | 0 | 0 | 4 | 150 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.9 | 8960.00000000002 | 40.602 | 2166.84 | 120.00000000002728 | 1635.0000000000273 | 1515 | 10.1 | 84.6938540007847 | 1547.75 | 0 | 87.25000000002728 | 0 |  | 17.53472222222222 | 1515 | 2018 | 10 | 2018_10_Asomata_english.xlsx
7 | 248 | 0 | 248 | 0 | 0 | 3 | 248 | 54 | 5.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.5 | 8000.000000000007 | 41.102 | 2751.84 | -960.0000000000127 | 1544.799999999987 | 2504.8 | 10.1 | 85.49097262667443 | 1518.4 | 0 | 86.39999999998713 | 60 |  | 28.990740740740737 | 2504.8 | 2018 | 10 | 2018_10_Asomata_english.xlsx
8 | 0 | 240 | 240 | 0 | 0 | 3 | 240 | 54 | 0 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.15 | 7160.00000000002 | 40.63 | 2199.6 | -839.9999999999873 | 1560.0000000000127 | 2400 | 10 | 87.06287069988136 | 1385.7 | 0 | 174.3000000000127 | 0 |  | 27.77777777777778 | 2400 | 2018 | 10 | 2018_10_Asomata_english.xlsx
9 | 172 | 0 | 172 | 0 | 0 | 3 | 172 | 40 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84 | 6800.000000000007 | 40.8 | 2398.5 | -360.00000000001273 | 1359.9999999999873 | 1720 | 10 | 87.37380952380953 | 1273.95 | 0 | 86.04999999998722 | 0 |  | 19.90740740740741 | 1720 | 2018 | 10 | 2018_10_Asomata_english.xlsx
10 | 0 | 155 | 155 | 0 | 0 | 4 | 155 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84 | 6800.000000000007 | 40.67 | 2246.4 | 0 | 1534.5 | 1534.5 | 9.9 | 88.25637325637325 | 1366.55 | 0 | 167.95 | 0 |  | 17.760416666666668 | 1534.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
11 | 180 | 0 | 180 | 0 | 0 | 3 | 180 | 40 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.95 | 6680.000000000014 | 41.02 | 2655.9 | -119.99999999999363 | 1698.0000000000064 | 1818 | 10.1 | 86.61183162416361 | 1744.05 | 0 | 13.950000000006412 | 60 |  | 21.041666666666668 | 1818 | 2018 | 10 | 2018_10_Asomata_english.xlsx
12 | 0 | 155 | 155 | 0 | 0 | 3 | 155 | 40 | 0 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.05 | 6920 | 41.15 | 2808 | 239.99999999998636 | 1789.9999999999864 | 1550 | 10 | 87.26991676575506 | 1668.55 | 0 | 121.4499999999864 | 0 |  | 17.939814814814813 | 1550 | 2018 | 10 | 2018_10_Asomata_english.xlsx
13 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 54 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.15 | 7160.00000000002 | 41.05 | 2691 | 240.00000000002 | 1401.50000000002 | 1161.5 | 10.1 | 86.20086207909047 | 1321.25 | 0 | 80.25000000002001 | 0 |  | 13.443287037037036 | 1161.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
14 | 0 | 145 | 145 | 0 | 0 | 4 | 145 | 55 | 0 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.2 | 7280.000000000014 | 40.9 | 2515.5 | 119.99999999999363 | 1584.4999999999936 | 1464.5 | 10.1 | 86.09872835624795 | 1518.4 | 0 | 126.09999999999377 | 60 |  | 16.95023148148148 | 1464.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
15 | 375 | 60 | 435 | 0 | 0 | 3 | 435 | 108 | 7.099999999998545 | 1.1500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84.15 | 7160.00000000002 | 41.42 | 3123.9 | -119.99999999999363 | 4273.500000000006 | 4393.5 | 10.1 | 86.20086207909047 | 4270.35 | 0 | 33.15000000000691 | 30 |  | 50.85069444444444 | 4393.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
16 | 0 | 310 | 310 | 0 | 0 | 4 | 310 | 54 | 0 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.25 | 7400.000000000007 | 41.27 | 2948.4 | 239.99999999998727 | 3370.9999999999873 | 3131 | 10.1 | 85.99683637002754 | 3393 | 0 | 7.999999999987267 | 30 |  | 36.238425925925924 | 3131 | 2018 | 10 | 2018_10_Asomata_english.xlsx
17 | 140 | 5 | 145 | 0 | 0 | 3 | 145 | 54 | 3.099999999998545 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.3 | 7520 | 40.4 | 1930.5 | 119.99999999999272 | 1569.9999999999927 | 1450 | 10 | 86.75413711583924 | 1425 | 0 | 144.99999999999272 | 0 |  | 16.78240740740741 | 1450 | 2018 | 10 | 2018_10_Asomata_english.xlsx
18 | 5 | 250 | 255 | 0 | 0 | 3 | 255 | 54 | 0 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.65 | 8360.00000000002 | 41.112 | 2763.54 | 840.00000000002 | 3353.00000000002 | 2513 | 9.854901960784314 | 87.3090410521793 | 3171 | 0 | 182.00000000002 | 0 |  | 29.08564814814815 | 2513 | 2018 | 10 | 2018_10_Asomata_english.xlsx
19 | 346 | 84 | 430 | 0 | 0 | 4 | 430 | 108 | 7.19999999999709 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.7 | 8480.000000000015 | 41.532 | 3254.94 | 119.99999999999454 | 4462.9999999999945 | 4343 | 10.1 | 85.09054652537853 | 4483.5 | 0 | 9.499999999994543 | 30 |  | 50.2662037037037 | 4343 | 2018 | 10 | 2018_10_Asomata_english.xlsx
20 | 0 | 207 | 207 | 0 | 0 | 3 | 207 | 54 | 0 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.55 | 8120 | 40.61 | 2176.2 | -360.00000000001455 | 1668.5999999999856 | 2028.6 | 9.8 | 88.00450850140291 | 1457.15 | 0 | 211.44999999998572 | 0 |  | 23.479166666666668 | 2028.6 | 2018 | 10 | 2018_10_Asomata_english.xlsx
21 | 309 | 0 | 309 | 0 | 0 | 3 | 309 | 54 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.1 | 7039.999999999993 | 41.51 | 3229.2 | -1080.0000000000073 | 2040.8999999999928 | 3120.9 | 10.1 | 86.3032383998495 | 1912.6 | 0 | 128.2999999999929 | 0 |  | 36.12152777777778 | 3120.9 | 2018 | 10 | 2018_10_Asomata_english.xlsx
22 | 0 | 155 | 155 | 0 | 0 | 3 | 155 | 54 | 0 | 4.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84 | 6800.000000000007 | 40.85 | 2457 | -239.99999999998545 | 1317.7500000000146 | 1557.75 | 10.05 | 86.93911395403933 | 1291.05 | 0 | 26.700000000014597 | 0 |  | 18.02951388888889 | 1557.75 | 2018 | 10 | 2018_10_Asomata_english.xlsx
23 | 566 | 49 | 615 | 0 | 0 | 3 | 615 | 70 | 13.200000000004366 | 1.3499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.4 | 7760.00000000002 | 41.703 | 3455.01 | 960.0000000000127 | 7110.000000000013 | 6150 | 10 | 86.54952830188678 | 7022.6 | 0 | 87.40000000001328 | 0 |  | 71.18055555555556 | 6150 | 2018 | 10 | 2018_10_Asomata_english.xlsx
24 | 0 | 215 | 215 | 0 | 0 | 4 | 215 | 35 | 0 | 4.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.15 | 7160.00000000002 | 41.29 | 2971.8 | -600 | 1571.5 | 2171.5 | 10.1 | 86.20086207909047 | 1475.1 | 0 | 96.39999999999986 | 0 |  | 25.13310185185185 | 2171.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
25 | 275 | 40 | 315 | 0 | 0 | 4 | 315 | 93 | 6.599999999998545 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 25 | 84.4 | 7760.00000000002 | 41.8105 | 3580.785000000002 | 600 | 3781.5 | 3181.5 | 10.1 | 85.69260227909582 | 3766.8 | 0 | 44.70000000000027 | 30 |  | 36.822916666666664 | 3181.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
26 | 134 | 260 | 394 | 0 | 0 | 3 | 394 | 80 | 3.5 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.25 | 7400.000000000007 | 41.73 | 3486.6 | -360.00000000001273 | 3619.399999999987 | 3979.4 | 10.1 | 85.99683637002754 | 3630 | 0 | 19.399999999986903 | 30 |  | 46.05787037037037 | 3979.4 | 2018 | 10 | 2018_10_Asomata_english.xlsx
27 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 40 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.1 | 7039.999999999993 | 41.11 | 2761.2 | -360.00000000001455 | 1811.4999999999854 | 2171.5 | 10.1 | 86.3032383998495 | 1691.2 | 0 | 120.2999999999854 | 0 |  | 25.13310185185185 | 2171.5 | 2018 | 10 | 2018_10_Asomata_english.xlsx
28 | 0 | 112 | 112 | 0 | 0 | 3 | 112 | 35 | 0 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.35 | 7639.999999999993 | 41 | 2632.5 | 600 | 1731.2 | 1131.2 | 10.1 | 85.79377418261309 | 1695 | 0 | 36.2 | 0 |  | 13.092592592592593 | 1131.2 | 2018 | 10 | 2018_10_Asomata_english.xlsx
29 | 250 | 0 | 250 | 0 | 0 | 4 | 250 | 55 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.25 | 7400.000000000007 | 41.542 | 3266.64 | -239.99999999998545 | 2285.0000000000146 | 2525 | 10.1 | 85.99683637002754 | 2197.3 | 0 | 147.70000000001482 | 60 |  | 29.224537037037038 | 2525 | 2018 | 10 | 2018_10_Asomata_english.xlsx
30 | 0 | 263 | 263 | 0 | 0 | 3 | 263 | 55 | 0 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.8 | 8720 | 41.946 | 3739.3199999999933 | 1319.9999999999927 | 3976.2999999999925 | 2656.3 | 10.1 | 84.89173683723513 | 4050 | 0 | 6.299999999992451 | 80 |  | 30.74421296296296 | 2656.3 | 2018 | 10 | 2018_10_Asomata_english.xlsx
31 | 270 | 0 | 270 | 0 | 0 | 4 | 270 | 54 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.5 | 8000.000000000007 | 41.15 | 2808 | -719.9999999999927 | 1980.0000000000073 | 2700 | 10 | 86.34588235294117 | 1750.75 | 0 | 229.25000000000728 | 0 |  | 31.25 | 2700 | 2018 | 10 | 2018_10_Asomata_english.xlsx
1 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.3 | 7520 | 40.9 | 2515.5 | -480.0000000000073 | 580.4999999999927 | 1060.5 | 10.1 | 85.89518526320718 | 503.7 | 0 | 76.79999999999274 | 0 |  | 12.274305555555555 | 1060.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
2 | 0 | 115 | 115 | 0 | 0 | 3 | 115 | 40 | 0 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.85 | 8839.999999999993 | 41.037 | 2675.79 | 1319.9999999999927 | 2446.9999999999927 | 1127 | 9.8 | 87.38837425285168 | 2317.85 | 0 | 129.14999999999281 | 0 |  | 13.043981481481481 | 1127 | 2018 | 11 | 2018_11_Asomata_english.xlsx
3 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 35 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85 | 9200.000000000007 | 41.252 | 2927.34 | 360.00000000001455 | 1521.5000000000146 | 1161.5 | 10.1 | 84.49689154962007 | 1390.8 | 0 | 130.7000000000146 | 0 |  | 13.443287037037036 | 1161.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
4 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 55 | 0 | 5.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.65 | 8360.00000000002 | 40.962 | 2588.0400000000086 | -839.9999999999873 | 3018.064766839391 | 2070.5 | 10.1 | 85.19030097617029 | 2962.5 | 1787.564766839378 | 55.56476683939081 | 0 |  | 23.96412037037037 | 2070.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
5 | 235 | 0 | 235 | 0 | 0 | 3 | 235 | 55 | 5.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.55 | 8120 | 40.67 | 2246.4 | -240.00000000002 | 2203.99999999998 | 2444 | 10.4 | 82.92732531862967 | 2197.05 | 0 | 66.94999999998026 | 60 |  | 28.287037037037038 | 2444 | 2018 | 11 | 2018_11_Asomata_english.xlsx
6 | 0 | 77 | 77 | 0 | 0 | 3 | 77 | 55 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.6 | 8239.999999999993 | 40.48 | 2024.0999999999947 | 119.99999999999272 | 874.5999999999927 | 754.6 | 9.8 | 87.90121682475808 | 724.8 | 0 | 149.7999999999928 | 0 |  | 8.733796296296296 | 754.6 | 2018 | 11 | 2018_11_Asomata_english.xlsx
7 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 55 | 4.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.7 | 8480.000000000015 | 40.401 | 1931.67 | 240.00000000002183 | 2319.000000000022 | 2079 | 9.9 | 86.80954746528516 | 2166.85 | 0 | 152.15000000002192 | 0 |  | 24.0625 | 2079 | 2018 | 11 | 2018_11_Asomata_english.xlsx
8 | 130 | 155 | 285 | 0 | 0 | 3 | 285 | 55 | 2.3000000000029104 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.5 | 8000.000000000007 | 41.299 | 2982.33 | -480.0000000000073 | 2398.4999999999927 | 2878.5 | 10.1 | 85.49097262667443 | 2339.3 | 0 | 59.19999999999254 | 0 |  | 33.31597222222222 | 2878.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
9 | 0 | 73 | 73 | 0 | 0 | 4 | 73 | 40 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 84.7 | 8480.000000000015 | 40.05 | 1520.9999999999945 | 480.0000000000073 | 1195.4000000000074 | 715.4 | 9.8 | 87.6953591741146 | 875.8 | 0 | 319.6000000000074 | 0 |  | 8.280092592592593 | 715.4 | 2018 | 11 | 2018_11_Asomata_english.xlsx
10 | 0 | 227 | 227 | 0 | 0 | 3 | 227 | 54 | 0 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.65 | 8360.00000000002 | 40.498 | 2045.16 | -119.99999999999454 | 2172.7000000000053 | 2292.7 | 10.1 | 85.19030097617029 | 1983.2 | 0 | 189.50000000000523 | 0 |  | 26.53587962962963 | 2292.7 | 2018 | 11 | 2018_11_Asomata_english.xlsx
11 | 193 | 0 | 193 | 0 | 0 | 4 | 193 | 50 | 4.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.5 | 8000.000000000007 | 40.582 | 2143.44 | -360.00000000001273 | 1589.2999999999872 | 1949.3 | 10.1 | 85.49097262667443 | 1522.5 | 0 | 66.79999999998722 | 0 |  | 22.56134259259259 | 1949.3 | 2018 | 11 | 2018_11_Asomata_english.xlsx
12 | 0 | 93 | 93 | 0 | 0 | 3 | 93 | 35 | 0 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.6 | 8239.999999999993 | 40.371 | 1896.57 | 239.99999999998545 | 1151.3999999999855 | 911.4 | 9.8 | 87.90121682475808 | 1011.7 | 0 | 139.6999999999856 | 0 |  | 10.548611111111112 | 911.4 | 2018 | 11 | 2018_11_Asomata_english.xlsx
13 | 117 | 0 | 117 | 0 | 0 | 4 | 117 | 55 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.45 | 7880.000000000014 | 40.827 | 2430.09 | -359.9999999999791 | 821.700000000021 | 1181.7 | 10.1 | 85.5916687075068 | 871.2 | 0 | 10.500000000020918 | 60 |  | 13.677083333333334 | 1181.7 | 2018 | 11 | 2018_11_Asomata_english.xlsx
14 | 275 | 257 | 532 | 0 | 0 | 4 | 532 | 90 | 6.900000000001455 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84.55 | 8120 | 40.62 | 2187.9 | 239.99999999998636 | 5559.999999999986 | 5320 | 10 | 86.24441833137486 | 5519.68 | 0 | 40.319999999986976 | 0 |  | 61.574074074074076 | 5320 | 2018 | 11 | 2018_11_Asomata_english.xlsx
15 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.6 | 8239.999999999993 | 40.743 | 2331.81 | 119.99999999999272 | 911.9999999999927 | 792 | 9.9 | 87.01332574572012 | 787.5 | 0 | 124.49999999999272 | 0 |  | 9.166666666666666 | 792 | 2018 | 11 | 2018_11_Asomata_english.xlsx
16 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 40 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.5 | 8000.000000000007 | 40.903 | 2519.01 | -239.99999999998545 | 1022.5000000000146 | 1262.5 | 10.1 | 85.49097262667443 | 847.5 | 0 | 175.00000000001455 | 0 |  | 14.612268518518519 | 1262.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
17 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 54 | 5.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.6 | 8239.999999999993 | 41.102 | 2751.84 | 239.99999999998545 | 2259.2499999999854 | 2019.25 | 9.85 | 87.45501775458165 | 2138.9 | 0 | 120.34999999998536 | 0 |  | 23.370949074074073 | 2019.25 | 2018 | 11 | 2018_11_Asomata_english.xlsx
18 | 160 | 413 | 573 | 0 | 0 | 5 | 573 | 71 | 4.299999999995634 | 9.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.1 | 9439.999999999993 | 40.832 | 2435.94 | 1200 | 6987.3 | 5787.3 | 10.1 | 84.30084307734718 | 6965.75 | 0 | 21.550000000000182 | 0 |  | 66.98263888888889 | 5787.3 | 2018 | 11 | 2018_11_Asomata_english.xlsx
19 | 510 | 175 | 685 | 0 | 0 | 4 | 685 | 108 | 11.900000000001455 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.7 | 8480.000000000015 | 40.901 | 2516.67 | -959.9999999999782 | 5958.500000000022 | 6918.5 | 10.1 | 85.09054652537853 | 5630.1 | 0 | 328.40000000002146 | 0 |  | 80.07523148148148 | 6918.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
20 | 0 | 285 | 285 | 0 | 0 | 4 | 285 | 40 | 0 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.9 | 8960.00000000002 | 40.891 | 2504.97 | 480.00000000000546 | 3358.5000000000055 | 2878.5 | 10.1 | 84.6938540007847 | 3285 | 0 | 133.50000000000546 | 60 |  | 33.31597222222222 | 2878.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
21 | 230 | 0 | 230 | 0 | 0 | 3 | 230 | 54 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.8 | 8720 | 40.682 | 2260.44 | -240.00000000002 | 2082.99999999998 | 2323 | 10.1 | 84.89173683723513 | 1949.1 | 0 | 133.89999999998008 | 0 |  | 26.886574074074073 | 2323 | 2018 | 11 | 2018_11_Asomata_english.xlsx
22 | 0 | 455 | 455 | 0 | 0 | 4 | 455 | 55 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85.1 | 9439.999999999993 | 40.692 | 2272.14 | 719.9999999999927 | 5224.499999999993 | 4504.5 | 9.9 | 86.0038904122431 | 5043.4 | 0 | 181.0999999999931 | 0 |  | 52.135416666666664 | 4504.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
23 | 200 | 135 | 335 | 0 | 0 | 8 | 335 | 55 | 4.799999999995634 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.5 | 8000.000000000007 | 40.47 | 2012.4 | -1439.9999999999854 | 1943.5000000000146 | 3383.5 | 10.1 | 85.49097262667443 | 1890.7 | 0 | 52.800000000014506 | 0 |  | 39.160879629629626 | 3383.5 | 2018 | 11 | 2018_11_Asomata_english.xlsx
24 | 0 | 570 | 570 | 0 | 0 | 4 | 570 | 55 | 0 | 11.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.65 | 8360.00000000002 | 40.551 | 2107.17 | 360.00000000001273 | 6060.000000000013 | 5700 | 10 | 86.04220398593199 | 6029.8 | 0 | 30.20000000001255 | 0 |  | 65.97222222222223 | 5700 | 2018 | 11 | 2018_11_Asomata_english.xlsx
25 | 203 | 0 | 203 | 0 | 0 | 4 | 203 | 55 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.8 | 8720 | 40.63 | 2199.6 | 359.99999999998 | 2349.39999999998 | 1989.4 | 9.8 | 87.49046347510966 | 2159.3 | 0 | 190.09999999998035 | 0 |  | 23.025462962962962 | 1989.4 | 2018 | 11 | 2018_11_Asomata_english.xlsx
26 | 47 | 500 | 547 | 0 | 0 | 4 | 547 | 70 | 1.3499999999985448 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.5 | 8000.000000000007 | 40.45 | 1989.0000000000055 | -719.9999999999927 | 4804.700000000007 | 5524.7 | 10.1 | 85.49097262667443 | 4745 | 0 | 59.700000000007094 | 0 |  | 63.94328703703704 | 5524.7 | 2018 | 11 | 2018_11_Asomata_english.xlsx
27 | 482 | 154 | 636 | 0 | 0 | 3 | 636 | 108 | 11.150000000001455 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.15 | 7160.00000000002 | 40.651 | 2224.17 | -839.9999999999873 | 5456.400000000013 | 6296.4 | 9.9 | 87.9422936362438 | 5475 | 0 | 41.40000000001328 | 60 |  | 72.875 | 6296.4 | 2018 | 11 | 2018_11_Asomata_english.xlsx
28 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 54 | 0 | 9.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.2 | 7280.000000000014 | 40.501 | 2048.67 | 119.99999999999363 | 4361.999999999994 | 4242 | 10.1 | 86.09872835624795 | 4254.25 | 0 | 107.74999999999363 | 0 |  | 49.09722222222222 | 4242 | 2018 | 11 | 2018_11_Asomata_english.xlsx
29 | 400 | 88 | 488 | 0 | 0 | 4 | 488 | 70 | 9.400000000001455 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.5 | 8000.000000000007 | 40.561 | 2118.87 | 719.9999999999936 | 5648.799999999994 | 4928.8 | 10.1 | 85.49097262667443 | 5628.3 | 0 | 80.49999999999363 | 60 |  | 57.0462962962963 | 4928.8 | 2018 | 11 | 2018_11_Asomata_english.xlsx
30 | 285 | 405 | 690 | 0 | 0 | 5 | 690 | 110 | 6.30000000000291 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.45 | 7880.000000000014 | 40.468 | 2010.06 | -119.99999999999363 | 6849.000000000006 | 6969 | 10.1 | 85.5916687075068 | 6907.5 | 0 | 1.5000000000063665 | 60 |  | 80.65972222222223 | 6969 | 2018 | 11 | 2018_11_Asomata_english.xlsx
1 | 335 | 175 | 510 | 0 | 0 | 5 | 510 | 110 | 7.399999999994179 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.85 | 8839.999999999993 | 40.493 | 2039.31 | 959.9999999999791 | 6110.999999999979 | 5151 | 10.1 | 84.79267996811352 | 6037.5 | 0 | 73.49999999997908 | 0 |  | 59.61805555555556 | 5151 | 2018 | 12 | 2018_12_Asomata_english.xlsx
2 | 134 | 0 | 134 | 0 | 0 | 5 | 134 | 55 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.7 | 8480.000000000015 | 40.14 | 1626.3 | -359.9999999999782 | 953.2000000000219 | 1313.2 | 9.8 | 87.6953591741146 | 717.25 | 0 | 235.95000000002187 | 0 |  | 15.199074074074074 | 1313.2 | 2018 | 12 | 2018_12_Asomata_english.xlsx
3 | 289 | 0 | 289 | 0 | 0 | 4 | 289 | 55 | 6.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.4 | 7760.00000000002 | 40.501 | 2048.67 | -719.9999999999945 | 2198.9000000000055 | 2918.9 | 10.1 | 85.69260227909582 | 2146.2 | 0 | 52.70000000000573 | 0 |  | 33.78356481481482 | 2918.9 | 2018 | 12 | 2018_12_Asomata_english.xlsx
4 | 515 | 352 | 867 | 0 | 0 | 4 | 867 | 108 | 10.599999999998545 | 7.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.35 | 7639.999999999993 | 40.75 | 2340 | -120.00000000002728 | 8636.699999999973 | 8756.7 | 10.1 | 85.79377418261306 | 8665.65 | 0 | 31.049999999973807 | 60 |  | 101.35069444444444 | 8756.7 | 2018 | 12 | 2018_12_Asomata_english.xlsx
5 | 175 | 0 | 175 | 0 | 0 | 5 | 175 | 40 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.5 | 8000.000000000007 | 40.48 | 2024.0999999999947 | 360.00000000001455 | 2127.5000000000146 | 1767.5 | 10.1 | 85.49097262667443 | 1907.6 | 0 | 219.90000000001464 | 0 |  | 20.457175925925927 | 1767.5 | 2018 | 12 | 2018_12_Asomata_english.xlsx
6 | 157 | 135 | 292 | 0 | 0 | 4 | 292 | 70 | 4.149999999994179 | 3.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.2 | 7280.000000000014 | 41.249 | 2923.8300000000063 | -719.9999999999936 | 2229.200000000006 | 2949.2 | 10.1 | 86.09872835624795 | 2226.5 | 0 | 62.700000000006185 | 60 |  | 34.13425925925926 | 2949.2 | 2018 | 12 | 2018_12_Asomata_english.xlsx
7 | 186 | 0 | 186 | 0 | 0 | 5 | 186 | 40 | 4.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.4 | 7760.00000000002 | 41.531 | 3253.7699999999936 | 480.00000000000637 | 2358.6000000000063 | 1878.6 | 10.1 | 85.69260227909582 | 2295.2 | 0 | 93.40000000000646 | 30 |  | 21.743055555555557 | 1878.6 | 2018 | 12 | 2018_12_Asomata_english.xlsx
8 | 0 | 236 | 236 | 0 | 0 | 4 | 236 | 40 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.45 | 7880.000000000014 | 41.942 | 3734.64 | 119.99999999999363 | 2503.5999999999935 | 2383.6 | 10.1 | 85.5916687075068 | 2477.6 | 0 | 25.999999999993634 | 0 |  | 27.587962962962962 | 2383.6 | 2018 | 12 | 2018_12_Asomata_english.xlsx
9 | 247 | 0 | 247 | 0 | 0 | 5 | 247 | 40 | 6.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 41.53 | 3252.6 | -360.00000000001364 | 2109.9999999999864 | 2470 | 10 | 86.75413711583924 | 2064.6 | 0 | 45.39999999998645 | 0 |  | 28.587962962962962 | 2470 | 2018 | 12 | 2018_12_Asomata_english.xlsx
10 | 0 | 401 | 401 | 0 | 0 | 4 | 401 | 55 | 0 | 10.35000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.2 | 7280.000000000014 | 41.32 | 3006.9 | -239.99999999998636 | 3729.9000000000137 | 3969.9 | 9.9 | 87.83809660586911 | 3774 | 0 | 15.900000000013733 | 60 |  | 45.947916666666664 | 3969.9 | 2018 | 12 | 2018_12_Asomata_english.xlsx
11 | 595 | 340 | 935 | 0 | 0 | 5 | 935 | 110 | 12.19999999999709 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.55 | 8120 | 41.68 | 3428.1 | 839.9999999999864 | 10283.5 | 9443.5 | 10.1 | 85.39051319938106 | 10300.3 | 0 | 43.199999999986176 | 60 |  | 109.29976851851852 | 9443.5 | 2018 | 12 | 2018_12_Asomata_english.xlsx
12 | 95 | 334 | 429 | 0 | 0 | 5 | 429 | 110 | 1.9000000000014552 | 7.5 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | ΒΛΑΒΗ ΣΥΓΧΡΟΝΙΣΤΗ | 12 | 84.6 | 8239.999999999993 | 40.6 | 2164.5 | 119.99999999999272 | 4452.899999999992 | 4332.9 | 10.1 | 85.29028959233953 | 4248.6 | 0 | 204.299999999992 | 0 |  | 50.14930555555556 | 4332.9 | 2018 | 12 | 2018_12_Asomata_english.xlsx
13 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 55 | 0 | 14.39999999999418 | 0 | 0 | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΣΥΓΧΡΟΝΙΣΤΗ | 13 | 83.4 | 5360.00000000002 | 41.201 | 2867.67 | -2879.9999999999727 | 4188.500000000028 | 7068.5 | 10.55 | 84.01904892735305 | 4210.3 | 0 | 38.20000000002801 | 60 |  | 81.81134259259261 | 7068.5 | 2018 | 12 | 2018_12_Asomata_english.xlsx
14 | 95 | 385 | 480 | 0 | 0 | 5 | 480 | 70 | 2.400000000001455 | 9.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 83.95 | 6680.000000000014 | 41.352 | 3044.34 | 1319.9999999999936 | 6167.999999999994 | 4848 | 10.1 | 86.61183162416361 | 6149.4 | 0 | 18.599999999993997 | 0 |  | 56.111111111111114 | 4848 | 2018 | 12 | 2018_12_Asomata_english.xlsx
15 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 40 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.8 | 6320 | 41.35 | 3042 | -360.00000000001364 | 1306.4999999999864 | 1666.5 | 10.1 | 86.9226396323843 | 1260 | 0 | 46.49999999998636 | 0 |  | 19.288194444444443 | 1666.5 | 2018 | 12 | 2018_12_Asomata_english.xlsx
16 | 0 | 127 | 127 | 0 | 0 | 5 | 127 | 40 | 0 | 3.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83.9 | 6560.00000000002 | 41.2 | 2866.5 | 240.00000000002 | 1522.70000000002 | 1282.7 | 10.1 | 86.71518703182966 | 1411.2 | 0 | 111.50000000002024 | 0 |  | 14.846064814814815 | 1282.7 | 2018 | 12 | 2018_12_Asomata_english.xlsx
17 | 255 | 0 | 255 | 0 | 0 | 5 | 255 | 45 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.1 | 7039.999999999993 | 41.252 | 2927.34 | 479.9999999999727 | 3055.4999999999727 | 2575.5 | 10.1 | 86.3032383998495 | 3065.3 | 0 | 50.19999999997299 | 60 |  | 29.80902777777778 | 2575.5 | 2018 | 12 | 2018_12_Asomata_english.xlsx
18 | 0 | 138 | 138 | 0 | 0 | 5 | 138 | 35 | 0 | 3.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.4 | 7760.00000000002 | 40.96 | 2585.7 | 720.0000000000273 | 2113.8000000000275 | 1393.8 | 10.1 | 85.69260227909582 | 1740 | 0 | 373.80000000002747 | 0 |  | 16.131944444444443 | 1393.8 | 2018 | 12 | 2018_12_Asomata_english.xlsx
19 | 250 | 0 | 250 | 0 | 0 | 4 | 250 | 40 | 7.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.1 | 7039.999999999993 | 40.729 | 2315.43 | -720.0000000000273 | 1779.9999999999727 | 2500 | 10 | 87.16627078384799 | 1795.45 | 0 | 44.54999999997267 | 60 |  | 28.935185185185187 | 2500 | 2018 | 12 | 2018_12_Asomata_english.xlsx
20 | 140 | 292 | 432 | 0 | 0 | 5 | 432 | 108 | 3.099999999998545 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.4 | 7760.00000000002 | 41.57 | 3299.4 | 720.0000000000273 | 5083.200000000027 | 4363.2 | 10.1 | 85.69260227909582 | 5157.8 | 0 | 25.40000000002692 | 100 |  | 50.5 | 4363.2 | 2018 | 12 | 2018_12_Asomata_english.xlsx
21 | 225 | 0 | 225 | 0 | 0 | 4 | 225 | 35 | 6.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.0249 | 2661.6329999999975 | -240.00000000002 | 2009.99999999998 | 2250 | 10 | 86.75413711583924 | 1990.6 | 0 | 79.39999999997985 | 60 |  | 26.041666666666668 | 2250 | 2018 | 12 | 2018_12_Asomata_english.xlsx
22 | 0 | 123 | 123 | 0 | 0 | 5 | 123 | 35 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.45 | 7880.000000000014 | 40.357 | 1880.19 | 360.00000000001364 | 1577.7000000000137 | 1217.7 | 9.9 | 87.32079332786046 | 1298.6 | 0 | 279.1000000000138 | 0 |  | 14.09375 | 1217.7 | 2018 | 12 | 2018_12_Asomata_english.xlsx
23 | 270 | 130 | 400 | 0 | 0 | 5 | 400 | 85 | 5.650000000001455 | 2.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480.000000000015 | 41.4 | 3100.5 | 600.0000000000009 | 4560 | 3960 | 9.9 | 86.80954746528516 | 4477 | 0 | 83.00000000000091 | 0 |  | 45.833333333333336 | 3960 | 2018 | 12 | 2018_12_Asomata_english.xlsx
24 | 0 | 123 | 123 | 0 | 0 | 4 | 123 | 45 | 0 | 3.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.65 | 8360.00000000002 | 40.9289 | 2549.3129999999987 | -119.99999999999454 | 2455.7446808510695 | 1230 | 10 | 86.04220398593199 | 2423.6 | 1345.7446808510638 | 92.14468085106955 | 60 |  | 14.23611111111111 | 1230 | 2018 | 12 | 2018_12_Asomata_english.xlsx
25 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.2 | 7280.000000000014 | 40.659 | 2233.53 | -1080.0000000000064 | 4547.148936170206 | 808 | 10.1 | 86.09872835624795 | 4526 | 4819.148936170212 | 81.14893617020607 | 60 |  | 9.351851851851851 | 808 | 2018 | 12 | 2018_12_Asomata_english.xlsx
26 | 0 | 137 | 137 | 0 | 0 | 5 | 137 | 35 | 0 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.35 | 7639.999999999993 | 40.366 | 1890.72 | 359.9999999999791 | 1702.5999999999792 | 1342.6 | 9.8 | 88.42011420861144 | 1638.35 | 0 | 64.24999999997931 | 0 |  | 15.539351851851855 | 1342.6 | 2018 | 12 | 2018_12_Asomata_english.xlsx
27 | 230 | 0 | 230 | 0 | 0 | 5 | 230 | 35 | 6.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.35 | 7639.999999999993 | 41.02 | 2655.9 | 0 | 2323 | 2323 | 10.1 | 85.79377418261309 | 2117 | 0 | 206 | 0 |  | 26.886574074074073 | 2323 | 2018 | 12 | 2018_12_Asomata_english.xlsx
28 | 110 | 300 | 410 | 0 | 0 | 5 | 410 | 70 | 3.3000000000029104 | 7.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.8 | 8720 | 41.801 | 3569.67 | 1080.0000000000073 | 5303.000000000007 | 4223 | 10.3 | 83.24335359767717 | 5343.25 | 0 | 19.750000000007276 | 60 |  | 48.87731481481482 | 4223 | 2018 | 12 | 2018_12_Asomata_english.xlsx
29 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 35 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.4 | 7760.00000000002 | 40.98 | 2609.1 | -959.99999999998 | 1539.00000000002 | 2499 | 9.8 | 88.31584520600691 | 1449.6 | 0 | 89.4000000000201 | 0 |  | 28.92361111111111 | 2499 | 2018 | 12 | 2018_12_Asomata_english.xlsx
30 | 136 | 171 | 307 | 0 | 0 | 5 | 307 | 55 | 3.2999999999956344 | 3.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.05 | 6920 | 41.55 | 3276 | -840.00000000002 | 2260.69999999998 | 3100.7 | 10.1 | 86.4058581839159 | 2073.2 | 0 | 187.49999999998 | 0 |  | 35.88773148148148 | 3100.7 | 2018 | 12 | 2018_12_Asomata_english.xlsx
31 | 191 | 0 | 191 | 0 | 0 | 5 | 191 | 35 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.6 | 8239.999999999993 | 41 | 2632.5 | 1319.9999999999927 | 3249.0999999999926 | 1929.1 | 10.1 | 85.29028959233953 | 3182.8 | 0 | 66.2999999999929 | 0 |  | 22.327546296296298 | 1929.1 | 2018 | 12 | 2018_12_Asomata_english.xlsx
1 | 83 | 0 | 83 | 0 | 0 | 4 | 83 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.1 | 7039.999999999993 | 40.75 | 2340 | -1200 | 2919.55 | 838.3 | 10.1 | 86.3032383998495 | 2920 | 3281.25 | 59.55000000000018 | 60 |  | 9.702546296296296 | 838.3 | 2019 | 1 | 2019_01_Asomata_english.xlsx
2 | 0 | 400 | 400 | 0 | 0 | 5 | 400 | 54 | 0 | 8.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.8 | 8720 | 41.682 | 3430.44 | 1680.0000000000073 | 5720.000000000007 | 4040 | 10.1 | 84.89173683723513 | 5664.8 | 0 | 115.2000000000071 | 60 |  | 46.75925925925926 | 4040 | 2019 | 1 | 2019_01_Asomata_english.xlsx
3 | 575 | 0 | 575 | 0 | 0 | 3 | 575 | 45 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.5 | 8000.000000000007 | 41.24 | 2913.3 | -719.9999999999927 | 5087.500000000007 | 5807.5 | 10.1 | 85.49097262667443 | 5043.4 | 0 | 104.10000000000764 | 60 |  | 67.21643518518519 | 5807.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
4 | 573 | 651 | 1224 | 0 | 0 | 7 | 1224 | 110 | 11.099999999998545 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.6 | 8239.999999999993 | 41.615 | 3352.05 | 239.99999999998545 | 13153.2 | 12913.2 | 10.55 | 81.65231515475158 | 13129.75 | 0 | 83.44999999998618 | 60 |  | 149.45833333333334 | 12913.2 | 2019 | 1 | 2019_01_Asomata_english.xlsx
5 | 251 | 178 | 429 | 0 | 0 | 4 | 429 | 70 | 6.19999999999709 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.4 | 7760.00000000002 | 41.646 | 3388.32 | -479.9999999999727 | 8573.952631578974 | 4332.9 | 10.1 | 85.69260227909582 | 8548.3 | 4721.052631578947 | 85.65263157897425 | 60 |  | 50.14930555555556 | 4332.9 | 2019 | 1 | 2019_01_Asomata_english.xlsx
6 | 0 | 195 | 195 | 0 | 0 | 5 | 195 | 45 | 0 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 85.05 | 9320 | 40.81 | 2410.2 | 1559.99999999998 | 5891.202127659555 | 1969.5 | 10.1 | 84.3987534641966 | 5964.1 | 2361.7021276595747 | 27.102127659554753 | 100 |  | 22.79513888888889 | 1969.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
7 | 196 | 0 | 196 | 0 | 0 | 3 | 196 | 35 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 85.2 | 9680.000000000015 | 40.495 | 2041.6499999999946 | 360.00000000001455 | 6600.238297872354 | 1979.6 | 10.1 | 84.10570223689035 | 6453.2 | 4260.63829787234 | 207.03829787235463 | 60 |  | 22.912037037037038 | 1979.6 | 2019 | 1 | 2019_01_Asomata_english.xlsx
8 | 635 | 660 | 1295 | 0 | 0 | 4 | 1295 | 110 | 12 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85.1 | 9439.999999999993 | 41.851 | 3628.17 | -240.00000000002183 | 19416.728723404234 | 13273.75 | 10.25 | 83.06717220304455 | 19432.71 | 6382.978723404255 | 44.01872340423506 | 60 |  | 153.63136574074073 | 13273.75 | 2019 | 1 | 2019_01_Asomata_english.xlsx
9 | 590 | 435 | 1025 | 0 | 0 | 5 | 1025 | 110 | 13.30000000000291 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 84.25 | 7400.000000000007 | 41.201 | 2867.67 | -2039.9999999999854 | 14185.515873015887 | 10352.5 | 10.1 | 85.99683637002754 | 14217 | 5873.015873015873 | 28.515873015887337 | 60 |  | 119.82060185185185 | 10352.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
10 | 100 | 375 | 475 | 0 | 0 | 5 | 475 | 108 | 2.2999999999956344 | 8.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.3 | 9920 | 40.902 | 2517.84 | 2519.9999999999927 | 10782.73936170212 | 4821.25 | 10.15 | 83.49810578049807 | 10774.8 | 3441.489361702128 | 67.93936170212146 | 60 |  | 55.801504629629626 | 4821.25 | 2019 | 1 | 2019_01_Asomata_english.xlsx
11 | 805 | 497 | 1302 | 0 | 0 | 5 | 1302 | 108 | 15.80000000000291 | 9.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 11 | 84.25 | 7400.000000000007 | 41.218 | 2887.56 | -2519.9999999999927 | 12417.4340425532 | 13150.2 | 10.1 | 85.99683637002752 | 12427.2 | 1787.2340425531916 | 50.23404255319838 | 60 |  | 152.20138888888889 | 13150.2 | 2019 | 1 | 2019_01_Asomata_english.xlsx
12 | 408 | 345 | 753 | 0 | 0 | 4 | 753 | 108 | 8 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84 | 6800.000000000007 | 41.38 | 3077.1 | -600 | 7005.3 | 7605.3 | 10.1 | 86.50872230080151 | 7047.04 | 0 | 18.26000000000022 | 60 |  | 88.02430555555556 | 7605.3 | 2019 | 1 | 2019_01_Asomata_english.xlsx
13 | 339 | 56 | 395 | 0 | 0 | 5 | 395 | 110 | 6.900000000001455 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 1 |  | 13 | 85.15 | 9560.00000000002 | 41.68 | 3428.1 | 2760.0000000000127 | 6591.500000000013 | 3831.5 | 9.7 | 87.67545483867114 | 6508.1 | 0 | 143.40000000001328 | 60 |  | 44.34606481481481 | 3831.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
14 | 702 | 662 | 1364 | 0 | 0 | 5 | 1364 | 110 | 13.5 | 13.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 85 | 9200.000000000007 | 41.762 | 3524.04 | -360.00000000001273 | 18939.896774193534 | 13912.8 | 10.2 | 83.6684906520748 | 18958.75 | 5387.096774193548 | 41.14677419353393 | 60 |  | 161.02777777777777 | 13912.8 | 2019 | 1 | 2019_01_Asomata_english.xlsx
15 | 421 | 265 | 686 | 0 | 0 | 5 | 686 | 70 | 11.25 | 7.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 85.4 | 10160 | 41.6315 | 3371.3550000000064 | 960.0000000000127 | 12731.531937172786 | 6928.6 | 10.1 | 83.71811835561435 | 12744.9 | 4842.931937172774 | 46.63193717278773 | 60 |  | 80.19212962962962 | 6928.6 | 2019 | 1 | 2019_01_Asomata_english.xlsx
16 | 500 | 600 | 1100 | 0 | 0 | 5 | 1100 | 110 | 10.849999999998545 | 12.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 16 | 85.1 | 9439.999999999993 | 42.095 | 3913.65 | -720.0000000000273 | 17671.914893616995 | 11110 | 10.1 | 84.30084307734718 | 17546.1 | 7281.91489361702 | 185.81489361699278 | 60 |  | 128.58796296296296 | 11110 | 2019 | 1 | 2019_01_Asomata_english.xlsx
17 | 572 | 253 | 825 | 0 | 0 | 5 | 825 | 110 | 14.30000000000291 | 6.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 17 | 85.1 | 9439.999999999993 | 41.302 | 2985.84 | 0 | 14929.274193548386 | 8332.5 | 10.1 | 84.30084307734718 | 14960.1 | 6596.774193548387 | 69.17419354838785 | 100 |  | 96.44097222222223 | 8332.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
18 | 309 | 422 | 731 | 0 | 0 | 5 | 731 | 108 | 7.19999999999709 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.5 | 8000.000000000007 | 41.35 | 3042 | -1439.9999999999854 | 10734.969148936185 | 7419.65 | 10.15 | 85.06983483048391 | 10760.2 | 4755.319148936171 | 34.76914893618414 | 60 |  | 85.87557870370371 | 7419.65 | 2019 | 1 | 2019_01_Asomata_english.xlsx
19 | 419 | 338 | 757 | 0 | 0 | 4 | 757 | 108 | 9.19999999999709 | 7.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 84.3 | 7520 | 41.05 | 2691 | -480.0000000000073 | 7165.699999999992 | 7645.7 | 10.1 | 85.8951852632072 | 7073.7 | 0 | 151.99999999999181 | 60 |  | 88.49189814814814 | 7645.7 | 2019 | 1 | 2019_01_Asomata_english.xlsx
20 | 0 | 177 | 177 | 0 | 0 | 5 | 177 | 54 | 0 | 4.350000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.15 | 9560.00000000002 | 40.8 | 2398.5 | 2040.00000000002 | 3810.00000000002 | 1770 | 10 | 85.045191193511 | 3672.85 | 0 | 137.15000000001965 | 0 |  | 20.48611111111111 | 1770 | 2019 | 1 | 2019_01_Asomata_english.xlsx
21 | 387 | 390 | 777 | 0 | 0 | 6 | 777 | 108 | 8.60000000000582 | 8.64999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 84.1 | 7039.999999999993 | 41.46 | 3170.7 | -2520.0000000000273 | 9475.848148148121 | 7847.7 | 10.1 | 86.3032383998495 | 9520 | 4148.148148148148 | 15.848148148121254 | 60 |  | 90.82986111111111 | 7847.7 | 2019 | 1 | 2019_01_Asomata_english.xlsx
22 | 210 | 410 | 620 | 0 | 0 | 5 | 620 | 108 | 5.599999999998545 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84 | 6800.000000000007 | 41.31 | 2995.2 | -239.99999999998545 | 6022.000000000015 | 6262 | 10.1 | 86.50872230080151 | 5953.5 | 0 | 68.50000000001455 | 0 |  | 72.47685185185185 | 6262 | 2019 | 1 | 2019_01_Asomata_english.xlsx
23 | 243 | 20 | 263 | 0 | 0 | 5 | 263 | 54 | 6.25 | 0.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.5 | 8000.000000000007 | 40.3 | 1813.4999999999945 | 1200 | 5946.7255319148935 | 2656.3 | 10.1 | 85.49097262667443 | 5883.8 | 2090.425531914894 | 62.92553191489333 | 0 |  | 30.74421296296296 | 2656.3 | 2019 | 1 | 2019_01_Asomata_english.xlsx
24 | 175 | 110 | 285 | 0 | 0 | 6 | 285 | 55 | 4.049999999995634 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.8 | 8720 | 41.2 | 2866.5 | 719.9999999999927 | 3541.4999999999927 | 2821.5 | 9.9 | 86.60672141980554 | 3145.8 | 0 | 395.69999999999254 | 0 |  | 32.65625 | 2821.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
25 | 443 | 337 | 780 | 0 | 0 | 5 | 780 | 110 | 10.400000000001455 | 7.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 25 | 83.9 | 6560.00000000002 | 40.95 | 2574 | -2159.99999999998 | 5718.00000000002 | 7878 | 10.1 | 86.71518703182966 | 5715.5 | 0 | 62.50000000002001 | 60 |  | 91.18055555555556 | 7878 | 2019 | 1 | 2019_01_Asomata_english.xlsx
26 | 74 | 233 | 307 | 0 | 0 | 5 | 307 | 70 | 1.8000000000029104 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.3 | 7520 | 41.2 | 2866.5 | 959.99999999998 | 4029.99999999998 | 3070 | 10 | 86.75413711583924 | 3959 | 0 | 70.99999999997999 | 0 |  | 35.532407407407405 | 3070 | 2019 | 1 | 2019_01_Asomata_english.xlsx
27 | 113 | 0 | 113 | 0 | 0 | 5 | 113 | 54 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.4 | 7760.00000000002 | 40.6 | 2164.5 | 240.00000000002 | 1381.30000000002 | 1141.3 | 10.1 | 85.69260227909582 | 1266.5 | 0 | 114.80000000001996 | 0 |  | 13.20949074074074 | 1141.3 | 2019 | 1 | 2019_01_Asomata_english.xlsx
28 | 0 | 215 | 215 | 0 | 0 | 6 | 215 | 54 | 0 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 83.9 | 6560.00000000002 | 40.751 | 2341.17 | -1200 | 971.5 | 2171.5 | 10.1 | 86.71518703182966 | 722.7 | 0 | 248.8 | 0 |  | 25.13310185185185 | 2171.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
29 | 120 | 0 | 120 | 0 | 0 | 5 | 120 | 35 | 3.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.2 | 7280.000000000014 | 40.18 | 1673.1 | 719.9999999999936 | 1931.9999999999936 | 1212 | 10.1 | 86.09872835624795 | 1781.2 | 0 | 150.7999999999936 | 0 |  | 14.027777777777779 | 1212 | 2019 | 1 | 2019_01_Asomata_english.xlsx
30 | 0 | 88 | 88 | 0 | 0 | 6 | 88 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.4 | 7760.00000000002 | 40.347 | 1868.49 | 480.00000000000637 | 1360.0000000000064 | 880 | 10 | 86.54952830188678 | 1268.4 | 0 | 91.6000000000065 | 0 |  | 10.185185185185185 | 880 | 2019 | 1 | 2019_01_Asomata_english.xlsx
31 | 285 | 0 | 285 | 0 | 0 | 5 | 285 | 40 | 6.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.05 | 6920 | 40.63 | 2199.6 | -840.00000000002 | 2038.49999999998 | 2878.5 | 10.1 | 86.4058581839159 | 1955.45 | 0 | 83.04999999997995 | 0 |  | 33.31597222222222 | 2878.5 | 2019 | 1 | 2019_01_Asomata_english.xlsx
1 | 95 | 0 | 95 | 0 | 0 | 5 | 95 | 55 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.15 | 7160.00000000002 | 40.98 | 2609.1 | 240.00000000002 | 1199.50000000002 | 959.5 | 10.1 | 86.20086207909047 | 927.1 | 0 | 332.40000000002 | 60 |  | 11.105324074074074 | 959.5 | 2019 | 2 | 2019_02_Asomata_english.xlsx
2 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.3 | 7520 | 41.25 | 2925 | 359.99999999998 | 1159.99999999998 | 800 | 10 | 86.75413711583924 | 1013.8 | 0 | 146.19999999997992 | 0 |  | 9.25925925925926 | 800 | 2019 | 2 | 2019_02_Asomata_english.xlsx
3 | 190 | 0 | 190 | 0 | 0 | 6 | 190 | 35 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.2 | 7280.000000000014 | 41.3 | 2983.5 | -239.99999999998636 | 1679.0000000000136 | 1919 | 10.1 | 86.09872835624795 | 1609.65 | 0 | 69.35000000001378 | 0 |  | 22.21064814814815 | 1919 | 2019 | 2 | 2019_02_Asomata_english.xlsx
4 | 0 | 120 | 120 | 0 | 0 | 5 | 120 | 35 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.05 | 6920 | 41.45 | 3159 | -360.00000000001364 | 851.9999999999864 | 1212 | 10.1 | 86.4058581839159 | 777.65 | 0 | 74.34999999998638 | 0 |  | 14.027777777777779 | 1212 | 2019 | 2 | 2019_02_Asomata_english.xlsx
5 | 154 | 0 | 154 | 0 | 0 | 5 | 154 | 54 | 3.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.2 | 7280.000000000014 | 41.5 | 3217.5 | 360.00000000001364 | 1876.9000000000135 | 1516.9 | 9.85 | 88.28397526884307 | 1646.45 | 0 | 230.45000000001346 | 0 |  | 17.556712962962962 | 1516.9 | 2019 | 2 | 2019_02_Asomata_english.xlsx
6 | 0 | 245 | 245 | 0 | 0 | 5 | 245 | 54 | 0 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.05 | 6920 | 40.76 | 2351.7 | -360.00000000001364 | 2089.9999999999864 | 2450 | 10 | 87.26991676575506 | 2056.2 | 0 | 33.799999999986085 | 0 |  | 28.35648148148148 | 2450 | 2019 | 2 | 2019_02_Asomata_english.xlsx
7 | 111 | 0 | 111 | 0 | 0 | 5 | 111 | 55 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84 | 6800.000000000007 | 40.91 | 2527.199999999995 | -119.99999999999272 | 1001.1000000000072 | 1121.1 | 10.1 | 86.50872230080151 | 846.8 | 0 | 154.30000000000723 | 0 |  | 12.975694444444445 | 1121.1 | 2019 | 2 | 2019_02_Asomata_english.xlsx
8 | 0 | 174 | 174 | 0 | 0 | 6 | 174 | 55 | 0 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84 | 6800.000000000007 | 41.468 | 3180.06 | 0 | 1757.4 | 1757.4 | 10.1 | 86.50872230080151 | 1664.4 | 0 | 93 | 0 |  | 20.340277777777775 | 1757.4 | 2019 | 2 | 2019_02_Asomata_english.xlsx
9 | 150 | 0 | 150 | 0 | 0 | 5 | 150 | 55 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.3 | 7520 | 41.45 | 3159 | 719.9999999999927 | 2189.9999999999927 | 1470 | 9.8 | 88.52462971004005 | 2107.5 | 0 | 82.49999999999272 | 0 |  | 17.01388888888889 | 1470 | 2019 | 2 | 2019_02_Asomata_english.xlsx
10 | 0 | 78 | 78 | 0 | 0 | 6 | 78 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.35 | 7639.999999999993 | 40.96 | 2585.7 | 119.99999999999272 | 888.2999999999927 | 768.3 | 9.85 | 87.97128114156266 | 708.1 | 0 | 180.19999999999266 | 0 |  | 8.89236111111111 | 768.3 | 2019 | 2 | 2019_02_Asomata_english.xlsx
11 | 130 | 0 | 130 | 0 | 0 | 5 | 130 | 35 | 3.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.35 | 7639.999999999993 | 40.95 | 2574 | 0 | 1313 | 1313 | 10.1 | 85.79377418261309 | 1110 | 0 | 203 | 0 |  | 15.19675925925926 | 1313 | 2019 | 2 | 2019_02_Asomata_english.xlsx
12 | 0 | 90 | 90 | 0 | 0 | 5 | 90 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.5 | 8000.000000000007 | 40.9 | 2515.5 | 360.00000000001455 | 1246.5000000000146 | 886.5 | 9.85 | 87.66079426694536 | 975 | 0 | 271.50000000001455 | 0 |  | 10.260416666666666 | 886.5 | 2019 | 2 | 2019_02_Asomata_english.xlsx
13 | 234 | 0 | 234 | 0 | 0 | 5 | 234 | 54 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.3 | 7520 | 41.681 | 3429.2699999999936 | -480.0000000000073 | 1883.3999999999928 | 2363.4 | 10.1 | 85.89518526320718 | 1817.7 | 0 | 65.69999999999277 | 0 |  | 27.354166666666668 | 2363.4 | 2019 | 2 | 2019_02_Asomata_english.xlsx
14 | 0 | 175 | 175 | 0 | 0 | 5 | 175 | 35 | 0 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.05 | 6920 | 41.2 | 2866.5 | -600 | 1150 | 1750 | 10 | 87.26991676575506 | 1087.7 | 0 | 62.3 | 0 |  | 20.25462962962963 | 1750 | 2019 | 2 | 2019_02_Asomata_english.xlsx
15 | 106 | 70 | 176 | 0 | 0 | 6 | 176 | 74 | 2.900000000001455 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.1 | 7039.999999999993 | 41.53 | 3252.6 | 119.99999999999272 | 1853.5999999999926 | 1733.6 | 9.85 | 88.49367592268831 | 1737.4 | 0 | 116.19999999999277 | 0 |  | 20.064814814814813 | 1733.6 | 2019 | 2 | 2019_02_Asomata_english.xlsx
16 | 0 | 160 | 160 | 0 | 0 | 5 | 160 | 55 | 0 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.15 | 7160.00000000002 | 41.47 | 3182.4 | 120.00000000002728 | 1736.0000000000273 | 1616 | 10.1 | 86.20086207909047 | 1615.7 | 0 | 120.30000000002724 | 0 |  | 18.703703703703702 | 1616 | 2019 | 2 | 2019_02_Asomata_english.xlsx
17 | 160 | 0 | 160 | 0 | 0 | 5 | 160 | 55 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.2 | 7280.000000000014 | 41.75 | 3510 | 119.99999999999363 | 1695.9999999999936 | 1576 | 9.85 | 88.28397526884307 | 1554.9 | 0 | 141.09999999999377 | 0 |  | 18.24074074074074 | 1576 | 2019 | 2 | 2019_02_Asomata_english.xlsx
18 | 215 | 220 | 435 | 0 | 0 | 6 | 435 | 110 | 4.799999999995634 | 4.950000000004366 | 0 | 4.25 | 0 | 0 | 0 | 4.25 | 0 | 0 | 1 | 1 |  | 18 | 84.6 | 8239.999999999993 | 41.73 | 3486.6 | 959.9999999999791 | 5527.499999999979 | 4567.5 | 10.5 | 82.04113570310754 | 5520 | 0 | 7.499999999979082 | 0 |  | 52.864583333333336 | 4567.5 | 2019 | 2 | 2019_02_Asomata_english.xlsx
19 | 331 | 410 | 741 | 0 | 0 | 5 | 741 | 110 | 6.700000000004366 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 84.35 | 7639.999999999993 | 41.301 | 2984.67 | -600 | 6735.9 | 7335.9 | 9.9 | 87.52698174185778 | 6679.5 | 0 | 56.399999999999636 | 0 |  | 84.90625 | 7335.9 | 2019 | 2 | 2019_02_Asomata_english.xlsx
20 | 69 | 270 | 339 | 0 | 0 | 5 | 339 | 110 | 1.3999999999941792 | 6.149999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.5 | 8000.000000000007 | 41.55 | 3276 | 360.00000000001455 | 3783.9000000000146 | 3423.9 | 10.1 | 85.49097262667443 | 3635.2 | 0 | 148.70000000001482 | 0 |  | 39.62847222222222 | 3423.9 | 2019 | 2 | 2019_02_Asomata_english.xlsx
21 | 240 | 0 | 240 | 0 | 0 | 5 | 240 | 35 | 6.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.6 | 8239.999999999993 | 41.7 | 3451.5 | 239.99999999998545 | 2663.9999999999854 | 2424 | 10.1 | 85.29028959233953 | 2436.15 | 0 | 227.84999999998536 | 0 |  | 28.055555555555557 | 2424 | 2019 | 2 | 2019_02_Asomata_english.xlsx
22 | 10 | 70 | 80 | 0 | 0 | 6 | 80 | 50 | 0.09999999999854481 | 1.8500000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.65 | 8360.00000000002 | 40.65 | 2223 | 120.00000000002728 | 910.5000000000273 | 790.5 | 9.88125 | 87.07623426786286 | 732.35 | 0 | 178.15000000002726 | 0 |  | 9.149305555555555 | 790.5 | 2019 | 2 | 2019_02_Asomata_english.xlsx
23 | 246 | 0 | 246 | 0 | 0 | 4 | 246 | 40 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.1 | 7039.999999999993 | 41.1 | 2749.5 | -1320.0000000000273 | 1164.5999999999726 | 2484.6 | 10.1 | 86.3032383998495 | 1087.5 | 0 | 77.09999999997262 | 0 |  | 28.756944444444443 | 2484.6 | 2019 | 2 | 2019_02_Asomata_english.xlsx
24 | 0 | 110 | 110 | 0 | 0 | 6 | 110 | 54 | 0 | 2.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84 | 6800.000000000007 | 41.15 | 2808 | -239.99999999998545 | 871.0000000000146 | 1111 | 10.1 | 86.50872230080151 | 795.7 | 0 | 75.30000000001462 | 0 |  | 12.858796296296296 | 1111 | 2019 | 2 | 2019_02_Asomata_english.xlsx
25 | 129 | 0 | 129 | 0 | 0 | 6 | 129 | 54 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.1 | 7039.999999999993 | 41.1 | 2749.5 | 239.99999999998545 | 1542.8999999999853 | 1302.9 | 10.1 | 86.3032383998495 | 1452.7 | 0 | 150.19999999998527 | 60 |  | 15.079861111111109 | 1302.9 | 2019 | 2 | 2019_02_Asomata_english.xlsx
26 | 0 | 125 | 125 | 0 | 0 | 6 | 125 | 55 | 0 | 2.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.1 | 7039.999999999993 | 41.23 | 2901.6 | 0 | 1250 | 1250 | 10 | 87.16627078384799 | 989.05 | 0 | 260.95 | 0 |  | 14.467592592592593 | 1250 | 2019 | 2 | 2019_02_Asomata_english.xlsx
27 | 170 | 0 | 170 | 0 | 0 | 5 | 170 | 35 | 4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.05 | 6920 | 41.45 | 3159 | -119.99999999999272 | 1546.0000000000075 | 1666 | 9.8 | 89.05093547526026 | 1366.55 | 0 | 179.45000000000755 | 0 |  | 19.28240740740741 | 1666 | 2019 | 2 | 2019_02_Asomata_english.xlsx
28 | 0 | 90 | 90 | 0 | 0 | 5 | 90 | 54 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.1 | 7039.999999999993 | 40.55 | 2106 | 119.99999999999272 | 1001.9999999999928 | 882 | 9.8 | 88.94517426923264 | 898.45 | 0 | 163.5499999999929 | 60 |  | 10.208333333333334 | 882 | 2019 | 2 | 2019_02_Asomata_english.xlsx
1 | 130 | 0 | 130 | 0 | 0 | 5 | 130 | 35 | 3.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.25 | 7400.000000000007 | 40.85 | 2457 | 360.00000000001455 | 1634.0000000000146 | 1274 | 9.8 | 88.62939258543653 | 1547.75 | 0 | 146.25000000001455 | 60 |  | 14.74537037037037 | 1274 | 2019 | 3 | 2019_03_Asomata_english.xlsx
2 | 0 | 130 | 130 | 0 | 0 | 5 | 130 | 35 | 0 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.25 | 7400.000000000007 | 41.4 | 3100.5 | 0 | 1313 | 1313 | 10.1 | 85.99683637002754 | 1170 | 0 | 143 | 0 |  | 15.19675925925926 | 1313 | 2019 | 3 | 2019_03_Asomata_english.xlsx
3 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 55 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.3 | 7520 | 41.04 | 2679.3 | 119.99999999999272 | 919.9999999999927 | 800 | 10 | 86.75413711583924 | 765 | 0 | 154.99999999999272 | 0 |  | 9.25925925925926 | 800 | 2019 | 3 | 2019_03_Asomata_english.xlsx
4 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 35 | 0 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.5 | 8000.000000000007 | 40.92 | 2538.9 | 480.0000000000073 | 1264.0000000000073 | 784 | 9.8 | 88.1080432172869 | 1005 | 0 | 259.0000000000073 | 0 |  | 9.074074074074074 | 784 | 2019 | 3 | 2019_03_Asomata_english.xlsx
5 | 120 | 0 | 120 | 0 | 0 | 5 | 120 | 40 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.4 | 7760.00000000002 | 41.22 | 2889.9 | -239.99999999998727 | 972.0000000000127 | 1212 | 10.1 | 85.69260227909582 | 854.1 | 0 | 117.90000000001271 | 0 |  | 14.027777777777779 | 1212 | 2019 | 3 | 2019_03_Asomata_english.xlsx
6 | 0 | 65 | 65 | 0 | 0 | 6 | 65 | 40 | 0 | 1.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.4 | 7760.00000000002 | 40.88 | 2492.1 | 0 | 656.5 | 656.5 | 10.1 | 85.69260227909582 | 735 | 0 | 21.5 | 100 |  | 7.59837962962963 | 656.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
7 | 90 | 0 | 90 | 0 | 0 | 5 | 90 | 35 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.5 | 8000.000000000007 | 41.18 | 2843.1 | 239.99999999998727 | 1139.9999999999873 | 900 | 10 | 86.34588235294117 | 906 | 0 | 233.99999999998727 | 0 |  | 10.416666666666666 | 900 | 2019 | 3 | 2019_03_Asomata_english.xlsx
8 | 0 | 95 | 95 | 0 | 0 | 5 | 95 | 35 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.4 | 7760.00000000002 | 41.52 | 3240.9 | -239.99999999998727 | 1714.1808510638425 | 959.5 | 10.1 | 85.69260227909582 | 1635.2 | 994.6808510638298 | 138.98085106384247 | 60 |  | 11.105324074074074 | 959.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
9 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.55 | 8120 | 41.02 | 2655.9 | 359.99999999998 | 1117.49999999998 | 757.5 | 10.1 | 85.39051319938106 | 855 | 0 | 262.49999999998 | 0 |  | 8.76736111111111 | 757.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
10 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.8500000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.5 | 8000.000000000007 | 40.8 | 2398.5 | -119.99999999999272 | 1769.5833333333405 | 650 | 10 | 86.34588235294117 | 1676.1 | 1239.5833333333333 | 93.48333333334062 | 0 |  | 7.523148148148148 | 650 | 2019 | 3 | 2019_03_Asomata_english.xlsx
11 | 100 | 0 | 100 | 0 | 0 | 5 | 100 | 35 | 2.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.55 | 8120 | 41.15 | 2808 | 119.99999999999272 | 1104.9999999999927 | 985 | 9.85 | 87.55778510799479 | 868.25 | 0 | 236.74999999999272 | 0 |  | 11.400462962962964 | 985 | 2019 | 3 | 2019_03_Asomata_english.xlsx
12 | 0 | 120 | 120 | 0 | 0 | 5 | 120 | 35 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84 | 6800.000000000007 | 41.58 | 3311.1 | -1319.9999999999927 | 1524.9787234042626 | 1212 | 10.1 | 86.50872230080151 | 1379.7 | 1632.9787234042553 | 205.27872340426256 | 60 |  | 14.027777777777779 | 1212 | 2019 | 3 | 2019_03_Asomata_english.xlsx
13 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.05 | 6920 | 41.92 | 3708.9 | 119.99999999999272 | 1569.9999999999927 | 1450 | 10 | 87.26991676575506 | 1430.4 | 0 | 139.59999999999263 | 0 |  | 16.78240740740741 | 1450 | 2019 | 3 | 2019_03_Asomata_english.xlsx
14 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 35 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.1 | 7039.999999999993 | 41.19 | 2854.8 | 119.99999999999272 | 927.9999999999927 | 808 | 10.1 | 86.3032383998495 | 781.1 | 0 | 146.89999999999281 | 0 |  | 9.351851851851851 | 808 | 2019 | 3 | 2019_03_Asomata_english.xlsx
15 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 54 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 84.2 | 7280.000000000014 | 40.63 | 2199.6 | 240.00000000002092 | 1028.000000000021 | 788 | 9.85 | 88.28397526884307 | 830.5 | 0 | 197.50000000002092 | 0 |  | 9.12037037037037 | 788 | 2019 | 3 | 2019_03_Asomata_english.xlsx
16 | 60 | 0 | 60 | 0 | 0 | 5 | 60 | 35 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 84.15 | 7160.00000000002 | 40.488 | 2033.46 | -119.99999999999363 | 1810.4680851063893 | 606 | 10.1 | 86.20086207909047 | 1715.5 | 1324.468085106383 | 154.96808510638925 | 60 |  | 7.013888888888889 | 606 | 2019 | 3 | 2019_03_Asomata_english.xlsx
17 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 40 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.4 | 7760.00000000002 | 40.626 | 2194.92 | 600 | 1408 | 808 | 10.1 | 85.69260227909582 | 1153.4 | 0 | 254.6 | 0 |  | 9.351851851851851 | 808 | 2019 | 3 | 2019_03_Asomata_english.xlsx
18 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 35 | 0 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.6 | 8239.999999999993 | 40.599 | 2163.33 | 479.9999999999727 | 1279.9999999999727 | 800 | 10 | 86.14319248826293 | 1278 | 0 | 31.999999999972715 | 30 |  | 9.25925925925926 | 800 | 2019 | 3 | 2019_03_Asomata_english.xlsx
19 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 35 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.5 | 8000.000000000007 | 41.295 | 2977.65 | -239.99999999998545 | 1181.0000000000146 | 1421 | 9.8 | 88.1080432172869 | 876 | 0 | 305.00000000001455 | 0 |  | 16.44675925925926 | 1421 | 2019 | 3 | 2019_03_Asomata_english.xlsx
20 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.7 | 8480.000000000015 | 40.941 | 2563.47 | 480.0000000000073 | 1136.5000000000073 | 656.5 | 10.1 | 85.09054652537853 | 962 | 0 | 174.50000000000728 | 0 |  | 7.59837962962963 | 656.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
21 | 95 | 0 | 95 | 0 | 0 | 5 | 95 | 45 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.55 | 8120 | 40.8968 | 2511.755999999998 | -360.00000000001455 | 3714.617021276581 | 931 | 9.8 | 88.00450850140291 | 3592.5 | 3143.6170212765956 | 122.117021276581 | 0 |  | 10.775462962962964 | 931 | 2019 | 3 | 2019_03_Asomata_english.xlsx
22 | 0 | 198 | 198 | 0 | 0 | 5 | 198 | 54 | 0 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.1 | 7039.999999999993 | 41.499 | 3216.3300000000063 | -1080.0000000000073 | 919.7999999999927 | 1999.8 | 10.1 | 86.3032383998495 | 941.7 | 0 | 8.099999999992747 | 30 |  | 23.145833333333332 | 1999.8 | 2019 | 3 | 2019_03_Asomata_english.xlsx
23 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.2 | 7280.000000000014 | 40.773 | 2366.91 | 240.00000000002092 | 3804.7872340425743 | 735 | 9.8 | 88.73440371409225 | 3682.5 | 2829.7872340425533 | 122.28723404257425 | 0 |  | 8.506944444444445 | 735 | 2019 | 3 | 2019_03_Asomata_english.xlsx
24 | 0 | 58 | 58 | 0 | 0 | 5 | 58 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.85 | 6439.999999999993 | 40.241 | 1744.47 | -840.0000000000209 | 2431.0085106382767 | 574.2 | 9.9 | 88.57270434331367 | 2299.5 | 2696.808510638298 | 131.50851063827668 | 0 |  | 6.645833333333333 | 574.2 | 2019 | 3 | 2019_03_Asomata_english.xlsx
25 | 135 | 0 | 135 | 0 | 0 | 4 | 135 | 35 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.35 | 5239.999999999993 | 41.52 | 3240.9 | -1200 | 3136.904255319149 | 1363.5 | 10.1 | 87.86859338896406 | 3168.2 | 2973.404255319149 | 28.70425531914907 | 60 |  | 15.78125 | 1363.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
26 | 0 | 199 | 199 | 0 | 0 | 4 | 199 | 55 | 0 | 4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.45 | 7880.000000000014 | 40.65 | 2223 | 2640.000000000021 | 4590.200000000021 | 1950.2 | 9.8 | 88.21182183120597 | 4432.5 | 0 | 157.70000000002074 | 0 |  | 22.57175925925926 | 1950.2 | 2019 | 3 | 2019_03_Asomata_english.xlsx
27 | 135 | 0 | 135 | 0 | 0 | 4 | 135 | 55 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.5 | 8000.000000000007 | 41.23 | 2901.6 | 119.99999999999363 | 1483.4999999999936 | 1363.5 | 10.1 | 85.49097262667443 | 1408.9 | 0 | 134.59999999999377 | 60 |  | 15.78125 | 1363.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
28 | 425 | 560 | 985 | 0 | 0 | 4 | 985 | 70 | 11.599999999998545 | 14.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 83.3 | 5120 | 41.1 | 2749.5 | -2880.0000000000073 | 7166.999999999993 | 10047 | 10.2 | 87.11247210748708 | 7148.4 | 0 | 78.59999999999218 | 60 |  | 116.28472222222223 | 10047 | 2019 | 3 | 2019_03_Asomata_english.xlsx
29 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 83.8 | 6320 | 40.3 | 1813.4999999999945 | 1200 | 4373.076923076923 | 650 | 10 | 87.79186602870813 | 4049.85 | 2523.076923076923 | 323.2269230769234 | 0 |  | 7.523148148148148 | 650 | 2019 | 3 | 2019_03_Asomata_english.xlsx
30 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 45 | 0 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 83.9 | 6560.00000000002 | 40.578 | 2138.76 | 240.00000000002 | 1199.50000000002 | 959.5 | 10.1 | 86.71518703182966 | 1116.9 | 0 | 142.60000000002015 | 60 |  | 11.105324074074074 | 959.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 45 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.1 | 7039.999999999993 | 40.67 | 2246.4 | 479.9999999999727 | 3858.012820512793 | 757.5 | 10.1 | 86.3032383998495 | 3744.9 | 2620.5128205128203 | 173.1128205127934 | 60 |  | 8.76736111111111 | 757.5 | 2019 | 3 | 2019_03_Asomata_english.xlsx
1 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 45 | 0 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 84.55 | 8120 | 40.71 | 2293.2 | 1080.0000000000073 | 6316.28723404256 | 656.5 | 10.1 | 85.39051319938106 | 6248.8 | 4579.787234042553 | 127.48723404256089 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
2 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 55 | 0 | 3.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.65 | 8360.00000000002 | 41.49 | 3205.8 | 240.00000000002 | 1865.25000000002 | 1625.25 | 9.85 | 87.35249135627615 | 1755 | 0 | 110.25000000002001 | 0 |  | 18.81076388888889 | 1625.25 | 2019 | 4 | 2019_04_Asomata_english.xlsx
3 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 55 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.6 | 8239.999999999993 | 41.902 | 3687.84 | -120.00000000002728 | 1899.2499999999727 | 2019.25 | 9.85 | 87.45501775458165 | 1664.4 | 0 | 234.84999999997285 | 0 |  | 23.370949074074073 | 2019.25 | 2019 | 4 | 2019_04_Asomata_english.xlsx
4 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 54 | 0 | 3.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.7 | 8480.000000000015 | 40.999 | 2631.3300000000063 | 240.00000000002183 | 1824.0000000000218 | 1584 | 9.9 | 86.80954746528516 | 1762.5 | 0 | 61.50000000002183 | 0 |  | 18.333333333333332 | 1584 | 2019 | 4 | 2019_04_Asomata_english.xlsx
5 | 235 | 0 | 235 | 0 | 0 | 4 | 235 | 55 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.15 | 7160.00000000002 | 40.873 | 2483.91 | -1319.9999999999945 | 1494.989361702133 | 2373.5 | 10.1 | 86.20086207909047 | 1416.2 | 441.48936170212767 | 78.78936170213296 | 0 |  | 27.471064814814813 | 2373.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
6 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 40 | 0 | 3.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.1 | 7039.999999999993 | 40.94 | 2562.3 | -120.00000000002728 | 1321.9999999999727 | 1442 | 10.3 | 84.6274473629592 | 1292.1 | 0 | 89.8999999999728 | 60 |  | 16.689814814814813 | 1442 | 2019 | 4 | 2019_04_Asomata_english.xlsx
7 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 35 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.1 | 7039.999999999993 | 41.148 | 2805.66 | 0 | 1544.25 | 1544.25 | 10.65 | 81.84626364680562 | 1537.25 | 0 | 67 | 60 |  | 17.87326388888889 | 1544.25 | 2019 | 4 | 2019_04_Asomata_english.xlsx
8 | 101 | 59 | 160 | 0 | 0 | 4 | 160 | 54 | 1.9000000000014552 | 1.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 83.9 | 6560.00000000002 | 40.608 | 2173.86 | -479.9999999999727 | 1136.0000000000273 | 1616 | 10.1 | 86.71518703182966 | 880.4 | 0 | 255.6000000000273 | 0 |  | 18.703703703703702 | 1616 | 2019 | 4 | 2019_04_Asomata_english.xlsx
9 | 89 | 0 | 89 | 0 | 0 | 3 | 89 | 45 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.15 | 7160.00000000002 | 40.487 | 2032.29 | 600 | 1498.9 | 898.9 | 10.1 | 86.20086207909047 | 1401.6 | 0 | 157.3 | 60 |  | 10.403935185185185 | 898.9 | 2019 | 4 | 2019_04_Asomata_english.xlsx
10 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 54 | 0 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.25 | 7400.000000000007 | 40.38 | 1907.1000000000054 | 239.99999999998727 | 1153.4999999999873 | 913.5 | 10.15 | 85.57320663421459 | 1029.3 | 0 | 124.19999999998731 | 0 |  | 10.572916666666666 | 913.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
11 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.4 | 7760.00000000002 | 40.4919 | 2038.0230000000006 | 360.00000000001273 | 1319.5000000000127 | 959.5 | 10.1 | 85.69260227909582 | 1153.4 | 0 | 166.10000000001287 | 0 |  | 11.105324074074074 | 959.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
12 | 0 | 81 | 81 | 0 | 0 | 4 | 81 | 35 | 0 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.3 | 7520 | 40.6058 | 2171.2860000000046 | -240.00000000002 | 602.39999999998 | 842.4 | 10.4 | 83.41743953446083 | 666 | 0 | 16.39999999997997 | 80 |  | 9.75 | 842.4 | 2019 | 4 | 2019_04_Asomata_english.xlsx
13 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 54 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.4 | 7760.00000000002 | 41.11 | 2761.2 | 240.00000000002 | 1654.00000000002 | 1414 | 10.1 | 85.69260227909582 | 1562.2 | 0 | 91.80000000001996 | 0 |  | 16.36574074074074 | 1414 | 2019 | 4 | 2019_04_Asomata_english.xlsx
14 | 0 | 105 | 105 | 0 | 0 | 4 | 105 | 54 | 0 | 2.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.7 | 8480.000000000015 | 41.091 | 2738.97 | 719.9999999999945 | 1754.2499999999945 | 1034.25 | 9.85 | 87.25020506663179 | 1402.5 | 0 | 351.74999999999454 | 0 |  | 11.97048611111111 | 1034.25 | 2019 | 4 | 2019_04_Asomata_english.xlsx
15 | 170 | 0 | 170 | 0 | 0 | 4 | 170 | 35 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.35 | 7639.999999999993 | 41.195 | 2860.65 | -840.0000000000218 | 910.9999999999784 | 1751 | 10.3 | 84.12787565479535 | 952 | 0 | 18.9999999999784 | 60 |  | 20.266203703703706 | 1751 | 2019 | 4 | 2019_04_Asomata_english.xlsx
16 | 80 | 165 | 245 | 0 | 0 | 4 | 245 | 70 | 2.099999999998545 | 4.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 84.5 | 8000.000000000007 | 41.825 | 3597.75 | 360.00000000001455 | 2810.0000000000146 | 2450 | 10 | 86.34588235294117 | 2682 | 0 | 128.00000000001455 | 0 |  | 28.35648148148148 | 2450 | 2019 | 4 | 2019_04_Asomata_english.xlsx
17 | 110 | 5 | 115 | 0 | 0 | 3 | 115 | 35 | 2.599999999998545 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480.000000000015 | 40.75 | 2340 | 480.0000000000073 | 1607.0000000000073 | 1127 | 9.8 | 87.6953591741146 | 1490.4 | 0 | 116.60000000000719 | 0 |  | 13.043981481481481 | 1127 | 2019 | 4 | 2019_04_Asomata_english.xlsx
18 | 0 | 160 | 160 | 0 | 0 | 5 | 160 | 35 | 0 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.3 | 7520 | 41.288 | 2969.4599999999914 | -960.0000000000146 | 719.9999999999854 | 1680 | 10.5 | 82.6229877293707 | 686 | 0 | 93.99999999998545 | 60 |  | 19.444444444444443 | 1680 | 2019 | 4 | 2019_04_Asomata_english.xlsx
19 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.45 | 7880.000000000014 | 41 | 2632.5 | 360.00000000001364 | 1152.0000000000136 | 792 | 9.9 | 87.32079332786046 | 981.5 | 0 | 170.50000000001364 | 0 |  | 9.166666666666666 | 792 | 2019 | 4 | 2019_04_Asomata_english.xlsx
20 | 0 | 60 | 60 | 0 | 0 | 5 | 60 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.6 | 8239.999999999993 | 40.34 | 1860.3000000000054 | 359.9999999999791 | 950.9999999999791 | 591 | 9.85 | 87.45501775458165 | 896.8 | 0 | 54.19999999997913 | 0 |  | 6.840277777777778 | 591 | 2019 | 4 | 2019_04_Asomata_english.xlsx
21 | 105 | 0 | 105 | 0 | 0 | 5 | 105 | 35 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.6 | 8239.999999999993 | 39.981 | 1440.27 | 0 | 1081.5 | 1081.5 | 10.3 | 83.63416746433293 | 1015.2 | 0 | 66.3 | 0 |  | 12.51736111111111 | 1081.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
22 | 0 | 115 | 115 | 0 | 0 | 5 | 115 | 55 | 0 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.7 | 8480.000000000015 | 40.406 | 1937.52 | 240.00000000002183 | 1378.5000000000218 | 1138.5 | 9.9 | 86.80954746528516 | 1212.75 | 0 | 165.75000000002183 | 0 |  | 13.177083333333334 | 1138.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
23 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 55 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.5 | 8000.000000000007 | 40.793 | 2390.31 | -480.0000000000073 | 727.4999999999927 | 1207.5 | 10.5 | 82.2341736694678 | 658 | 0 | 69.49999999999272 | 0 |  | 13.975694444444445 | 1207.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
24 | 0 | 60 | 60 | 0 | 0 | 5 | 60 | 35 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.3 | 7520 | 40.19 | 1684.8 | -480.0000000000073 | 1097.3617021276523 | 588 | 9.8 | 88.52462971004005 | 1117.5 | 989.3617021276596 | 39.86170212765228 | 60 |  | 6.805555555555555 | 588 | 2019 | 4 | 2019_04_Asomata_english.xlsx
25 | 77 | 0 | 77 | 0 | 0 | 5 | 77 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.5 | 8000.000000000007 | 40.9 | 2515.5 | 480.0000000000073 | 2874.721276595752 | 777.7 | 10.1 | 85.49097262667443 | 2708.3 | 1617.0212765957447 | 166.42127659575226 | 0 |  | 9.001157407407407 | 777.7 | 2019 | 4 | 2019_04_Asomata_english.xlsx
26 | 0 | 35 | 35 | 0 | 0 | 5 | 35 | 45 | 0 | 0.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85.2 | 9680.000000000015 | 40.581 | 2142.27 | 1680.0000000000073 | 3540.0561224489866 | 344.75 | 9.85 | 86.24036473021243 | 3480.55 | 1515.3061224489795 | 59.50612244898639 | 0 |  | 3.990162037037037 | 344.75 | 2019 | 4 | 2019_04_Asomata_english.xlsx
27 | 96 | 0 | 96 | 0 | 0 | 4 | 96 | 45 | 2.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.85 | 8839.999999999993 | 40.748 | 2337.66 | -840.0000000000218 | 2597.6851063829567 | 969.6 | 10.1 | 84.79267996811352 | 2430.9 | 2468.0851063829787 | 166.78510638295666 | 0 |  | 11.222222222222221 | 969.6 | 2019 | 4 | 2019_04_Asomata_english.xlsx
28 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.75 | 6200.000000000007 | 40.68 | 2258.1 | -2639.9999999999854 | 979.6578947368566 | 656.5 | 10.1 | 87.02673860200392 | 934.4 | 2963.157894736842 | 45.257894736856656 | 0 |  | 7.59837962962963 | 656.5 | 2019 | 4 | 2019_04_Asomata_english.xlsx
29 | 72 | 0 | 72 | 0 | 0 | 5 | 72 | 35 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 82.7 | 3740.0000000000064 | 40.65 | 2223 | -2460 | 1246.9979797979786 | 727.2 | 10.1 | 89.27190016298927 | 1162.7 | 2979.7979797979797 | 84.29797979797854 | 0 |  | 8.416666666666666 | 727.2 | 2019 | 4 | 2019_04_Asomata_english.xlsx
30 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.25 | 7400.000000000007 | 40.605 | 2170.349999999995 | 3660 | 5104.270100502514 | 640.25 | 9.85 | 88.17949719160184 | 5028.75 | 804.0201005025125 | 75.52010050251374 | 0 |  | 7.410300925925926 | 640.25 | 2019 | 4 | 2019_04_Asomata_english.xlsx
1 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 35 | 0 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 83.6 | 5839.999999999993 | 40.724 | 2309.58 | -1560.0000000000146 | 1627.1208791208646 | 808 | 10.1 | 87.34053693830923 | 1617 | 2379.120879120879 | 70.12087912086463 | 60 |  | 9.351851851851851 | 808 | 2019 | 5 | 2019_05_Asomata_english.xlsx
2 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 54 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.7 | 6080.000000000014 | 40.702 | 2283.84 | 240.00000000002092 | 880.2500000000209 | 640.25 | 9.85 | 89.34253612338556 | 722.65 | 0 | 157.60000000002094 | 0 |  | 7.410300925925926 | 640.25 | 2019 | 5 | 2019_05_Asomata_english.xlsx
3 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 45 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.9 | 6560.00000000002 | 40.816 | 2417.22 | 480.00000000000637 | 1272.0000000000064 | 792 | 9.9 | 88.46700899206864 | 1102.5 | 0 | 169.50000000000637 | 0 |  | 9.166666666666666 | 792 | 2019 | 5 | 2019_05_Asomata_english.xlsx
4 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.35 | 7639.999999999993 | 40.776 | 2370.42 | 1079.9999999999727 | 1736.4999999999727 | 656.5 | 10.1 | 85.79377418261309 | 1693.6 | 0 | 42.899999999972806 | 0 |  | 7.59837962962963 | 656.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
5 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 45 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 83.9 | 6560.00000000002 | 40.733 | 2320.11 | -1079.9999999999727 | 4343.351063829814 | 742.5 | 9.9 | 88.46700899206864 | 4262.4 | 4680.851063829787 | 80.95106382981339 | 0 |  | 8.59375 | 742.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
6 | 0 | 160 | 160 | 0 | 0 | 5 | 160 | 45 | 0 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 83.95 | 6680.000000000014 | 40.756 | 2347.02 | 119.99999999999363 | 2528.742268041231 | 1584 | 9.9 | 88.36156559636892 | 2518.08 | 824.7422680412371 | 10.662268041231073 | 0 |  | 18.333333333333332 | 1584 | 2019 | 5 | 2019_05_Asomata_english.xlsx
7 | 200 | 0 | 200 | 0 | 0 | 5 | 200 | 45 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 83.9 | 6560.00000000002 | 41.025 | 2661.75 | -119.99999999999363 | 1920.0000000000061 | 2040 | 10.2 | 85.86503813936075 | 1860 | 0 | 60.00000000000614 | 0 |  | 23.611111111111107 | 2040 | 2019 | 5 | 2019_05_Asomata_english.xlsx
8 | 0 | 220 | 220 | 0 | 0 | 4 | 220 | 55 | 0 | 5.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 83.85 | 6439.999999999993 | 41.398 | 3098.16 | -120.00000000002728 | 2101.9999999999727 | 2222 | 10.1 | 86.81878940582232 | 2059 | 0 | 42.999999999972715 | 0 |  | 25.71759259259259 | 2222 | 2019 | 5 | 2019_05_Asomata_english.xlsx
9 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 45 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84 | 6800.000000000007 | 41.113 | 2764.71 | 360.00000000001455 | 2191.5000000000146 | 1831.5 | 9.9 | 88.25637325637325 | 2091.35 | 0 | 100.15000000001464 | 0 |  | 21.197916666666668 | 1831.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
10 | 0 | 132 | 132 | 0 | 0 | 5 | 132 | 35 | 0 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84 | 6800.000000000007 | 40.52 | 2070.9000000000055 | 0 | 1333.2 | 1333.2 | 10.1 | 86.50872230080151 | 1314 | 0 | 49.2 | 30 |  | 15.430555555555555 | 1333.2 | 2019 | 5 | 2019_05_Asomata_english.xlsx
11 | 235 | 0 | 235 | 0 | 0 | 5 | 235 | 40 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84 | 6800.000000000007 | 40.55 | 2106 | 0 | 2420.5 | 2420.5 | 10.3 | 84.82894128525196 | 2422 | 0 | 58.5 | 60 |  | 28.015046296296298 | 2420.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
12 | 120 | 123 | 243 | 0 | 0 | 4 | 243 | 70 | 3.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.2 | 7280.000000000014 | 40.65 | 2223 | 480.00000000000637 | 2885.700000000006 | 2405.7 | 9.9 | 87.83809660586913 | 2619.85 | 0 | 265.8500000000063 | 0 |  | 27.84375 | 2405.7 | 2019 | 5 | 2019_05_Asomata_english.xlsx
13 | 250 | 0 | 250 | 0 | 0 | 5 | 250 | 54 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84 | 6800.000000000007 | 40.699 | 2280.33 | -480.00000000000637 | 2007.4999999999936 | 2487.5 | 9.95 | 87.8128738932759 | 1940.35 | 0 | 67.14999999999372 | 0 |  | 28.79050925925926 | 2487.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
14 | 0 | 308 | 308 | 0 | 0 | 5 | 308 | 45 | 0 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.05 | 6920 | 41.2 | 2866.5 | 119.99999999999272 | 3230.7999999999925 | 3110.8 | 10.1 | 86.4058581839159 | 3263.1 | 0 | 27.699999999992542 | 60 |  | 36.004629629629626 | 3110.8 | 2019 | 5 | 2019_05_Asomata_english.xlsx
15 | 260 | 0 | 260 | 0 | 0 | 5 | 260 | 45 | 6.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.7 | 8480.000000000015 | 41.333 | 3022.11 | 1560.0000000000146 | 4186.000000000015 | 2626 | 10.1 | 85.09054652537853 | 4107.2 | 0 | 138.80000000001473 | 60 |  | 30.39351851851852 | 2626 | 2019 | 5 | 2019_05_Asomata_english.xlsx
16 | 25 | 235 | 260 | 0 | 0 | 5 | 260 | 45 | 0.6000000000058208 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.5 | 8000.000000000007 | 41.41 | 3112.2 | -480.0000000000073 | 2119.9999999999927 | 2600 | 10 | 86.34588235294117 | 1995 | 0 | 124.99999999999272 | 0 |  | 30.09259259259259 | 2600 | 2019 | 5 | 2019_05_Asomata_english.xlsx
17 | 260 | 0 | 260 | 0 | 0 | 4 | 260 | 55 | 6.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.55 | 8120 | 41.544 | 3268.98 | 119.99999999999272 | 2862.9999999999927 | 2743 | 10.55 | 81.7482638212084 | 2604.8 | 0 | 258.19999999999254 | 0 |  | 31.747685185185187 | 2743 | 2019 | 5 | 2019_05_Asomata_english.xlsx
18 | 0 | 302 | 302 | 0 | 0 | 5 | 302 | 40 | 0 | 7.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 85.15 | 9560.00000000002 | 41.95 | 3744 | 1440.00000000002 | 4611.00000000002 | 3171 | 10.5 | 80.9954201842962 | 4432.75 | 0 | 178.25000000002 | 0 |  | 36.701388888888886 | 3171 | 2019 | 5 | 2019_05_Asomata_english.xlsx
19 | 180 | 30 | 210 | 0 | 0 | 4 | 210 | 45 | 4.650000000001455 | 0.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.8 | 6320 | 41.57 | 3299.4 | -3240.00000000002 | 2633.9591836734494 | 2226 | 10.6 | 82.82251512142278 | 2619.85 | 3647.9591836734694 | 74.10918367344948 | 60 |  | 25.76388888888889 | 2226 | 2019 | 5 | 2019_05_Asomata_english.xlsx
20 | 0 | 315 | 315 | 0 | 0 | 4 | 315 | 40 | 0 | 7.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85 | 9200.000000000007 | 41.521 | 3242.07 | 2880.0000000000073 | 8950.77631578948 | 3260.25 | 10.35 | 82.45590383103021 | 8738.1 | 2810.5263157894738 | 272.6763157894802 | 60 |  | 37.734375 | 3260.25 | 2019 | 5 | 2019_05_Asomata_english.xlsx
21 | 320 | 45 | 365 | 0 | 0 | 5 | 365 | 70 | 8.30000000000291 | 1.1500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.8 | 8720 | 41.871 | 3651.57 | -480.0000000000073 | 3334.2499999999927 | 3814.25 | 10.45 | 82.0484729240263 | 3102.5 | 0 | 231.74999999999272 | 0 |  | 44.14641203703704 | 3814.25 | 2019 | 5 | 2019_05_Asomata_english.xlsx
22 | 0 | 385 | 385 | 0 | 0 | 4 | 385 | 45 | 0 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.9 | 8960.00000000002 | 41.78 | 3545.1 | 240.00000000002 | 4128.50000000002 | 3888.5 | 10.1 | 84.6938540007847 | 4070 | 0 | 58.500000000019554 | 0 |  | 45.00578703703704 | 3888.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
23 | 355 | 0 | 355 | 0 | 0 | 4 | 355 | 45 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.55 | 8120 | 41.92 | 3708.9 | -840.00000000002 | 2869.7499999999795 | 3709.75 | 10.45 | 82.53054385777499 | 2540.4 | 0 | 329.34999999997945 | 0 |  | 42.93692129629629 | 3709.75 | 2019 | 5 | 2019_05_Asomata_english.xlsx
24 | 0 | 345 | 345 | 0 | 0 | 5 | 345 | 45 | 0 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.65 | 8360.00000000002 | 41.79 | 3556.8 | 240.00000000002 | 3862.50000000002 | 3622.5 | 10.5 | 81.9449561770781 | 3664.6 | 0 | 257.9000000000201 | 60 |  | 41.927083333333336 | 3622.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
25 | 340 | 0 | 340 | 0 | 0 | 4 | 340 | 45 | 8.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.35 | 7639.999999999993 | 41.721 | 3476.0699999999933 | -720.0000000000273 | 2713.9999999999727 | 3434 | 10.1 | 85.79377418261309 | 2591.5 | 0 | 122.49999999997272 | 0 |  | 39.745370370370374 | 3434 | 2019 | 5 | 2019_05_Asomata_english.xlsx
26 | 0 | 195 | 195 | 0 | 0 | 4 | 195 | 45 | 0 | 5.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 83 | 4400 | 40.93 | 2550.6 | -3239.9999999999927 | 4016.7340425531984 | 1969.5 | 10.1 | 88.61869113740643 | 3990 | 5287.234042553191 | 86.73404255319838 | 60 |  | 22.79513888888889 | 1969.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
27 | 285 | 10 | 295 | 0 | 0 | 4 | 295 | 45 | 6.69999999999709 | 0.09999999999854481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 83.8 | 6320 | 41.2 | 2866.5 | 1920 | 5047 | 3127 | 10.6 | 82.82251512142278 | 4990.65 | 0 | 56.349999999999454 | 0 |  | 36.192129629629626 | 3127 | 2019 | 5 | 2019_05_Asomata_english.xlsx
28 | 0 | 265 | 265 | 0 | 0 | 4 | 265 | 45 | 0 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 83.6 | 5839.999999999993 | 41.052 | 2693.34 | -480.0000000000073 | 2196.4999999999927 | 2676.5 | 10.1 | 87.34053693830923 | 2124.15 | 0 | 72.34999999999263 | 0 |  | 30.97800925925926 | 2676.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
29 | 420 | 0 | 420 | 0 | 0 | 5 | 420 | 55 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 83.75 | 6200.000000000007 | 42.001 | 3803.6699999999937 | 360.00000000001455 | 4602.000000000015 | 4242 | 10.1 | 87.02673860200392 | 4550.4 | 0 | 51.600000000014006 | 0 |  | 49.09722222222222 | 4242 | 2019 | 5 | 2019_05_Asomata_english.xlsx
30 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 54 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.3 | 7520 | 41.582 | 3313.44 | 1319.9999999999927 | 4837.499999999993 | 3517.5 | 10.5 | 82.6229877293707 | 4816.8 | 0 | 80.69999999999254 | 60 |  | 40.71180555555556 | 3517.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
31 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 45 | 7.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.4 | 7760.00000000002 | 41.65 | 3393 | 240.00000000002 | 4177.50000000002 | 3937.5 | 10.5 | 82.42812219227312 | 3922 | 0 | 255.50000000002 | 0 |  | 45.572916666666664 | 3937.5 | 2019 | 5 | 2019_05_Asomata_english.xlsx
1 | 350 | 0 | 350 | 0 | 0 | 5 | 350 | 45 | 9.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.2 | 7280.000000000014 | 41.36 | 3053.7 | -480.00000000000637 | 3054.9999999999936 | 3535 | 10.1 | 86.09872835624795 | 2985 | 0 | 129.99999999999363 | 60 |  | 40.914351851851855 | 3535 | 2019 | 6 | 2019_06_Asomata_english.xlsx
2 | 0 | 275 | 275 | 0 | 0 | 4 | 275 | 45 | 0 | 6.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.1 | 7039.999999999993 | 40.62 | 2187.9 | -240.00000000002092 | 4859.166666666646 | 2901.25 | 10.55 | 82.62205761502179 | 4755 | 2197.9166666666665 | 164.16666666664605 | 60 |  | 33.579282407407405 | 2901.25 | 2019 | 6 | 2019_06_Asomata_english.xlsx
3 | 365 | 0 | 365 | 0 | 0 | 4 | 365 | 45 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.2 | 7280.000000000014 | 40.987 | 2617.29 | 240.00000000002092 | 3926.500000000021 | 3686.5 | 10.1 | 86.09872835624795 | 3898.2 | 0 | 88.3000000000211 | 60 |  | 42.667824074074076 | 3686.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
4 | 12 | 405 | 417 | 0 | 0 | 4 | 417 | 44 | 0.4000000000014552 | 9.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.5 | 8000.000000000007 | 41.498 | 3215.16 | 719.9999999999936 | 4931.699999999993 | 4211.7 | 10.1 | 85.49097262667443 | 4920.2 | 0 | 71.49999999999363 | 60 |  | 48.74652777777778 | 4211.7 | 2019 | 6 | 2019_06_Asomata_english.xlsx
5 | 393 | 0 | 393 | 0 | 0 | 5 | 393 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.6 | 8239.999999999993 | 41.899 | 3684.33 | 239.99999999998545 | 4209.299999999985 | 3969.3 | 10.1 | 85.29028959233953 | 4219.4 | 0 | 49.899999999985084 | 60 |  | 45.940972222222214 | 3969.3 | 2019 | 6 | 2019_06_Asomata_english.xlsx
6 | 0 | 320 | 320 | 0 | 0 | 4 | 320 | 40 | 0 | 8.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.65 | 8360.00000000002 | 41.7 | 3451.5 | 120.00000000002728 | 3352.0000000000273 | 3232 | 10.1 | 85.19030097617029 | 3204.7 | 0 | 147.30000000002747 | 0 |  | 37.407407407407405 | 3232 | 2019 | 6 | 2019_06_Asomata_english.xlsx
7 | 345 | 0 | 345 | 0 | 0 | 3 | 345 | 40 | 8.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.7 | 8480.000000000015 | 41.549 | 3274.83 | 119.99999999999454 | 3707.9999999999945 | 3588 | 10.4 | 82.63601152945415 | 3577 | 0 | 190.99999999999454 | 60 |  | 41.52777777777778 | 3588 | 2019 | 6 | 2019_06_Asomata_english.xlsx
8 | 0 | 375 | 375 | 0 | 0 | 3 | 375 | 45 | 0 | 8.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.85 | 8839.999999999993 | 41.53 | 3252.6 | 359.9999999999782 | 4237.499999999978 | 3877.5 | 10.34 | 82.82457134216116 | 3920.1 | 0 | 317.39999999997826 | 0 |  | 44.87847222222222 | 3877.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
9 | 305 | 55 | 360 | 0 | 0 | 3 | 360 | 45 | 6.899999999994179 | 1.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 83.4 | 5360.00000000002 | 41.4 | 3100.5 | -3479.9999999999727 | 1936.104712041912 | 3636 | 10.1 | 87.76247189936385 | 1925.7 | 1780.1047120418848 | 70.40471204191226 | 60 |  | 42.083333333333336 | 3636 | 2019 | 6 | 2019_06_Asomata_english.xlsx
10 | 0 | 410 | 410 | 0 | 0 | 4 | 410 | 45 | 0 | 9.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.4 | 5360.00000000002 | 41.57 | 3299.4 | 0 | 4346 | 4346 | 10.6 | 83.62273265882781 | 4221 | 0 | 185 | 60 |  | 50.300925925925924 | 4346 | 2019 | 6 | 2019_06_Asomata_english.xlsx
11 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 45 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.55 | 8120 | 41.33 | 3018.6 | 2759.99999999998 | 6648.49999999998 | 3888.5 | 10.1 | 85.39051319938106 | 6540.8 | 0 | 167.6999999999798 | 60 |  | 45.00578703703704 | 3888.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
12 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 45 | 0 | 10.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.75 | 8600.000000000007 | 41.38 | 3077.1 | 480.0000000000073 | 4990.000000000007 | 4510 | 10.25 | 83.74725431464842 | 4715.85 | 0 | 274.1500000000069 | 0 |  | 52.199074074074076 | 4510 | 2019 | 6 | 2019_06_Asomata_english.xlsx
13 | 350 | 50 | 400 | 0 | 0 | 4 | 400 | 90 | 8 | 1.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 85.1 | 9439.999999999993 | 40.91 | 2527.199999999995 | 839.9999999999854 | 4919.999999999985 | 4080 | 10.2 | 83.47436422364771 | 4779.15 | 0 | 140.8499999999858 | 0 |  | 47.222222222222214 | 4080 | 2019 | 6 | 2019_06_Asomata_english.xlsx
14 | 23 | 610 | 633 | 0 | 0 | 3 | 633 | 109 | 0.6000000000058208 | 13.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.95 | 6680.000000000014 | 41.951 | 3745.17 | -2759.999999999979 | 3570.000000000021 | 6330 | 10 | 87.47794994040524 | 3233.9 | 0 | 336.1000000000213 | 0 |  | 73.26388888888889 | 6330 | 2019 | 6 | 2019_06_Asomata_english.xlsx
15 | 472 | 0 | 472 | 0 | 0 | 3 | 472 | 45 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84 | 6800.000000000007 | 41.45 | 3159 | 119.99999999999363 | 4887.199999999993 | 4767.2 | 10.1 | 86.50872230080151 | 4876.4 | 0 | 70.79999999999382 | 60 |  | 55.175925925925924 | 4767.2 | 2019 | 6 | 2019_06_Asomata_english.xlsx
16 | 0 | 500 | 500 | 0 | 0 | 3 | 500 | 54 | 0 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.3 | 7520 | 41.25 | 2925 | 719.9999999999927 | 5769.999999999993 | 5050 | 10.1 | 85.89518526320718 | 5657.5 | 0 | 112.49999999999272 | 0 |  | 58.449074074074076 | 5050 | 2019 | 6 | 2019_06_Asomata_english.xlsx
17 | 550 | 0 | 550 | 0 | 0 | 3 | 550 | 45 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.4 | 7760.00000000002 | 41.201 | 2867.67 | 240.00000000002 | 5822.50000000002 | 5582.5 | 10.15 | 85.27047123338599 | 5557.5 | 0 | 265.00000000002 | 0 |  | 64.61226851851852 | 5582.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
18 | 0 | 565 | 565 | 0 | 0 | 3 | 565 | 54 | 0 | 12.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84 | 6800.000000000007 | 41.34 | 3030.3 | -960.0000000000127 | 4746.499999999987 | 5706.5 | 10.1 | 86.50872230080151 | 4740.45 | 0 | 66.04999999998745 | 60 |  | 66.04745370370371 | 5706.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
19 | 545 | 0 | 545 | 0 | 0 | 3 | 545 | 54 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.2 | 7280.000000000014 | 41.28 | 2960.1 | 480.00000000000637 | 5930.000000000006 | 5450 | 10 | 86.95971563981043 | 5752.4 | 0 | 177.60000000000673 | 0 |  | 63.0787037037037 | 5450 | 2019 | 6 | 2019_06_Asomata_english.xlsx
20 | 70 | 540 | 610 | 0 | 0 | 4 | 610 | 70 | 1.9000000000014552 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.6 | 8239.999999999993 | 41.72 | 3474.9 | 959.9999999999791 | 7059.999999999979 | 6100 | 10 | 86.14319248826293 | 6926.4 | 0 | 193.59999999997763 | 60 |  | 70.60185185185185 | 6100 | 2019 | 6 | 2019_06_Asomata_english.xlsx
21 | 570 | 0 | 570 | 0 | 0 | 3 | 570 | 45 | 12.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.7 | 8480.000000000015 | 41.86 | 3638.7 | 240.00000000002183 | 5997.000000000022 | 5757 | 10.1 | 85.09054652537853 | 5854.6 | 0 | 202.40000000002237 | 60 |  | 66.63194444444444 | 5757 | 2019 | 6 | 2019_06_Asomata_english.xlsx
22 | 0 | 565 | 565 | 0 | 0 | 3 | 565 | 45 | 0 | 12.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.8 | 8720 | 41.74 | 3498.3 | 239.99999999998545 | 5946.499999999985 | 5706.5 | 10.1 | 84.89173683723513 | 5870.6 | 0 | 75.89999999998508 | 0 |  | 66.04745370370371 | 5706.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
23 | 615 | 10 | 625 | 0 | 0 | 3 | 625 | 45 | 13.099999999998545 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.45 | 7880.000000000014 | 41.92 | 3708.9 | -839.9999999999864 | 5472.500000000014 | 6312.5 | 10.1 | 85.5916687075068 | 5292.5 | 0 | 180.00000000001364 | 0 |  | 73.0613425925926 | 6312.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
24 | 20 | 570 | 590 | 0 | 0 | 3 | 590 | 45 | 0.5999999999985448 | 11.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.6 | 8239.999999999993 | 42 | 3802.5 | 359.9999999999791 | 6318.999999999979 | 5959 | 10.1 | 85.29028959233953 | 6314.4 | 0 | 64.59999999997854 | 60 |  | 68.9699074074074 | 5959 | 2019 | 6 | 2019_06_Asomata_english.xlsx
25 | 565 | 0 | 565 | 0 | 0 | 3 | 565 | 45 | 12.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.1 | 7039.999999999993 | 42 | 3802.5 | -1200 | 4506.5 | 5706.5 | 10.1 | 86.3032383998495 | 4365.4 | 0 | 141.1 | 0 |  | 66.04745370370371 | 5706.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
26 | 0 | 605 | 605 | 0 | 0 | 3 | 605 | 54 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.6 | 8239.999999999993 | 42 | 3802.5 | 1200 | 7522.25 | 6322.25 | 10.45 | 82.43367702226118 | 7592.4 | 0 | 19.849999999999454 | 90 |  | 73.17418981481481 | 6322.25 | 2019 | 6 | 2019_06_Asomata_english.xlsx
27 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 54 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.45 | 7880.000000000014 | 42.02 | 3825.9 | -359.9999999999791 | 6255.500000000021 | 6615.5 | 10.1 | 85.5916687075068 | 6256.75 | 0 | 58.75000000002092 | 60 |  | 76.56828703703704 | 6615.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
28 | 5 | 605 | 610 | 0 | 0 | 3 | 610 | 45 | 0.20000000000436557 | 12.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.75 | 8600.000000000007 | 41.96 | 3755.7 | 719.9999999999936 | 6880.999999999994 | 6161 | 10.1 | 84.9910254183313 | 6708.7 | 0 | 172.2999999999929 | 0 |  | 71.30787037037037 | 6161 | 2019 | 6 | 2019_06_Asomata_english.xlsx
29 | 550 | 0 | 550 | 0 | 0 | 3 | 550 | 45 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.7 | 8480.000000000015 | 41.73 | 3486.6 | -119.99999999999272 | 6070.416666666674 | 5555 | 10.1 | 85.09054652537853 | 6031 | 635.4166666666666 | 99.41666666667425 | 60 |  | 64.29398148148148 | 5555 | 2019 | 6 | 2019_06_Asomata_english.xlsx
30 | 0 | 485 | 485 | 0 | 0 | 3 | 485 | 45 | 0 | 10.830000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 83.95 | 6680.000000000014 | 41.04 | 2679.3 | -1800 | 8163.016129032258 | 4898.5 | 10.1 | 86.61183162416361 | 8212.5 | 5064.5161290322585 | 10.516129032257595 | 60 |  | 56.695601851851855 | 4898.5 | 2019 | 6 | 2019_06_Asomata_english.xlsx
1 | 592 | 0 | 592 | 0 | 0 | 3 | 592 | 54 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.6 | 8239.999999999993 | 41.041 | 2680.4699999999934 | 1559.999999999979 | 7479.999999999979 | 5920 | 10 | 86.14319248826293 | 7365 | 0 | 114.99999999997908 | 0 |  | 68.51851851851852 | 5920 | 2019 | 7 | 2019_07_Asomata_english.xlsx
2 | 35 | 580 | 615 | 0 | 0 | 3 | 615 | 70 | 1 | 12.87000000000262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.6 | 8239.999999999993 | 41.251 | 2926.1699999999937 | 0 | 6150 | 6150 | 10 | 86.14319248826293 | 6075.4 | 0 | 74.59999999999945 | 0 |  | 71.18055555555556 | 6150 | 2019 | 7 | 2019_07_Asomata_english.xlsx
3 | 613 | 0 | 613 | 0 | 0 | 3 | 613 | 45 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.75 | 8600.000000000007 | 41.2 | 2866.5 | 360.00000000001455 | 6490.000000000015 | 6130 | 10 | 85.84093567251462 | 6274.05 | 0 | 215.95000000001528 | 0 |  | 70.94907407407408 | 6130 | 2019 | 7 | 2019_07_Asomata_english.xlsx
4 | 5 | 585 | 590 | 0 | 0 | 3 | 590 | 50 | 0.20000000000436557 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.85 | 8839.999999999993 | 41.05 | 2691 | 239.99999999998545 | 6788.743589743575 | 5959 | 10.1 | 84.79267996811352 | 6576.05 | 589.7435897435897 | 212.693589743576 | 0 |  | 68.9699074074074 | 5959 | 2019 | 7 | 2019_07_Asomata_english.xlsx
5 | 590 | 155 | 745 | 0 | 0 | 4 | 745 | 90 | 13.39999999999418 | 3.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.5 | 8000.000000000007 | 42.08 | 3896.1 | -839.9999999999854 | 6759.000000000015 | 7599 | 10.2 | 84.65282583621685 | 6615 | 0 | 144.00000000001455 | 0 |  | 87.95138888888889 | 7599 | 2019 | 7 | 2019_07_Asomata_english.xlsx
6 | 0 | 705 | 705 | 0 | 0 | 3 | 705 | 50 | 0 | 13.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.5 | 8000.000000000007 | 42.1 | 3919.5 | 0 | 7120.5 | 7120.5 | 10.1 | 85.49097262667443 | 6997.2 | 0 | 183.3 | 60 |  | 82.41319444444444 | 7120.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
7 | 310 | 385 | 695 | 0 | 0 | 3 | 695 | 55 | 5.80000000000291 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 85 | 9200.000000000007 | 42.1 | 3919.5 | 1200 | 8219.5 | 7019.5 | 10.1 | 84.49689154962007 | 8205.2 | 0 | 74.29999999999927 | 60 |  | 81.24421296296296 | 7019.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
8 | 180 | 640 | 820 | 0 | 0 | 3 | 820 | 90 | 4.650000000001455 | 14.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.6 | 8239.999999999993 | 41.83 | 3603.6 | -960.0000000000146 | 7321.999999999985 | 8282 | 10.1 | 85.29028959233953 | 7318.15 | 0 | 63.84999999998581 | 60 |  | 95.85648148148148 | 8282 | 2019 | 7 | 2019_07_Asomata_english.xlsx
9 | 700 | 0 | 700 | 0 | 0 | 4 | 700 | 55 | 13.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85 | 9200.000000000007 | 42.1 | 3919.5 | 960.0000000000146 | 8030.000000000015 | 7070 | 10.1 | 84.49689154962007 | 7744.4 | 0 | 285.6000000000149 | 0 |  | 81.82870370370371 | 7070 | 2019 | 7 | 2019_07_Asomata_english.xlsx
10 | 0 | 730 | 730 | 0 | 0 | 2 | 730 | 55 | 0 | 14.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.5 | 5600.000000000007 | 42.049 | 3859.83 | -3600 | 4028.5 | 7628.5 | 10.45 | 84.61866605176688 | 4102.6 | 0 | 25.899999999999636 | 100 |  | 88.29282407407406 | 7628.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
11 | 440 | 0 | 440 | 0 | 0 | 3 | 440 | 55 | 8.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.65 | 8360.00000000002 | 41.5 | 3217.5 | 2760.0000000000127 | 7160.000000000013 | 4400 | 10 | 86.04220398593199 | 7080 | 0 | 140.00000000001273 | 60 |  | 50.925925925925924 | 4400 | 2019 | 7 | 2019_07_Asomata_english.xlsx
12 | 225 | 370 | 595 | 0 | 0 | 3 | 595 | 54 | 4.5 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.7 | 8480.000000000015 | 41.9 | 3685.5 | 119.99999999999454 | 6069.9999999999945 | 5950 | 10 | 85.94145199063232 | 5874.8 | 0 | 195.19999999999527 | 0 |  | 68.86574074074075 | 5950 | 2019 | 7 | 2019_07_Asomata_english.xlsx
13 | 455 | 0 | 455 | 0 | 0 | 4 | 455 | 45 | 10.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 13 | 84.9 | 8960.00000000002 | 41.9 | 3685.5 | 480.00000000000546 | 5030.0000000000055 | 4550 | 10 | 85.54079254079252 | 4757.6 | 0 | 272.400000000006 | 0 |  | 52.66203703703704 | 4550 | 2019 | 7 | 2019_07_Asomata_english.xlsx
14 | 135 | 205 | 340 | 0 | 0 | 3 | 340 | 45 | 3.1999999999970896 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84 | 6800.000000000007 | 41.9 | 3685.5 | -2160.0000000000127 | 4889.789473684198 | 3434 | 10.1 | 86.50872230080151 | 4599 | 3615.789473684211 | 350.78947368419813 | 60 |  | 39.745370370370374 | 3434 | 2019 | 7 | 2019_07_Asomata_english.xlsx
15 | 490 | 0 | 490 | 0 | 0 | 4 | 490 | 45 | 10.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.2 | 7280.000000000014 | 41.9 | 3685.5 | 480.00000000000637 | 5551.500000000006 | 5071.5 | 10.35 | 84.01904892735307 | 5562.6 | 0 | 48.90000000000691 | 60 |  | 58.697916666666664 | 5071.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
16 | 0 | 305 | 305 | 0 | 0 | 4 | 305 | 45 | 0 | 7.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.3 | 7520 | 41.42 | 3123.9 | 239.99999999998636 | 3396.7499999999864 | 3156.75 | 10.35 | 83.82042233414421 | 3226.6 | 0 | 230.14999999998645 | 60 |  | 36.536458333333336 | 3156.75 | 2019 | 7 | 2019_07_Asomata_english.xlsx
17 | 290 | 0 | 290 | 0 | 0 | 3 | 290 | 45 | 6.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.5 | 8000.000000000007 | 41.531 | 3253.7699999999936 | 480.0000000000073 | 5597.775510204088 | 2929 | 10.1 | 85.49097262667443 | 5616.6 | 2188.7755102040815 | 41.175510204087914 | 60 |  | 33.90046296296296 | 2929 | 2019 | 7 | 2019_07_Asomata_english.xlsx
18 | 0 | 315 | 315 | 0 | 0 | 3 | 315 | 45 | 0 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.5 | 8000.000000000007 | 41.621 | 3359.07 | 0 | 3181.5 | 3181.5 | 10.1 | 85.49097262667443 | 3217.5 | 0 | 24 | 60 |  | 36.822916666666664 | 3181.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
19 | 115 | 180 | 295 | 0 | 0 | 4 | 295 | 54 | 2.900000000001455 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 84.65 | 8360.00000000002 | 41.42 | 3123.9 | 360.00000000001273 | 3339.5000000000127 | 2979.5 | 10.1 | 85.19030097617029 | 3066 | 0 | 273.50000000001273 | 0 |  | 34.4849537037037 | 2979.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
20 | 0 | 325 | 325 | 0 | 0 | 3 | 325 | 45 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.35 | 7639.999999999993 | 41.12 | 2772.9 | -720.0000000000273 | 2692.4999999999727 | 3412.5 | 10.5 | 82.52543992803734 | 2671.8 | 0 | 80.69999999997299 | 60 |  | 39.49652777777778 | 3412.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
21 | 335 | 90 | 425 | 0 | 0 | 4 | 425 | 99 | 7.599999999998545 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.7 | 8480.000000000015 | 41.461 | 3171.8699999999935 | 840.0000000000218 | 4962.500000000021 | 4122.5 | 9.7 | 88.599435041889 | 4827.15 | 0 | 135.35000000002128 | 0 |  | 47.71412037037036 | 4122.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
22 | 0 | 485 | 485 | 0 | 0 | 4 | 485 | 54 | 0 | 9.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.8 | 8720 | 41.96 | 3755.7 | 239.99999999998545 | 5089.999999999985 | 4850 | 10 | 85.74065420560747 | 4693.9 | 0 | 396.0999999999858 | 0 |  | 56.13425925925926 | 4850 | 2019 | 7 | 2019_07_Asomata_english.xlsx
23 | 495 | 0 | 495 | 0 | 0 | 3 | 495 | 50 | 10.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 85 | 9200.000000000007 | 41.97 | 3767.4 | 480.0000000000073 | 5430.000000000007 | 4950 | 10 | 85.34186046511628 | 5201.95 | 0 | 228.05000000000746 | 0 |  | 57.291666666666664 | 4950 | 2019 | 7 | 2019_07_Asomata_english.xlsx
24 | 0 | 563 | 563 | 0 | 0 | 4 | 563 | 50 | 0 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85.15 | 9560.00000000002 | 42.04 | 3849.3 | 360.00000000001273 | 5990.000000000013 | 5630 | 10 | 85.045191193511 | 5646.8 | 0 | 343.20000000001346 | 0 |  | 65.16203703703704 | 5630 | 2019 | 7 | 2019_07_Asomata_english.xlsx
25 | 570 | 0 | 570 | 0 | 0 | 3 | 570 | 45 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.7 | 8480.000000000015 | 41.75 | 3510 | -1080.0000000000055 | 4619.9999999999945 | 5700 | 10 | 85.94145199063232 | 4455.1 | 0 | 164.89999999999418 | 0 |  | 65.97222222222223 | 5700 | 2019 | 7 | 2019_07_Asomata_english.xlsx
26 | 0 | 622 | 622 | 0 | 0 | 3 | 622 | 50 | 0 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.5 | 8000.000000000007 | 41.71 | 3463.2 | -480.0000000000073 | 5739.999999999993 | 6220 | 10 | 86.34588235294117 | 5609.65 | 0 | 130.3499999999931 | 0 |  | 71.99074074074075 | 6220 | 2019 | 7 | 2019_07_Asomata_english.xlsx
27 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 52 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.8 | 8720 | 41.7 | 3451.5 | 719.9999999999927 | 7169.999999999993 | 6450 | 10 | 85.74065420560747 | 7044.8 | 0 | 125.19999999999254 | 0 |  | 74.65277777777777 | 6450 | 2019 | 7 | 2019_07_Asomata_english.xlsx
28 | 0 | 685 | 685 | 0 | 0 | 4 | 685 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.4 | 7760.00000000002 | 41.79 | 3556.8 | -959.99999999998 | 5787.25000000002 | 6747.25 | 9.85 | 87.86754142323531 | 5692.4 | 0 | 94.85000000002037 | 0 |  | 78.09317129629629 | 6747.25 | 2019 | 7 | 2019_07_Asomata_english.xlsx
29 | 700 | 0 | 700 | 0 | 0 | 3 | 700 | 50 | 13.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.8 | 8720 | 41.93 | 3720.6 | 959.99999999998 | 8029.99999999998 | 7070 | 10.1 | 84.89173683723513 | 7666.05 | 0 | 363.9499999999789 | 0 |  | 81.82870370370371 | 7070 | 2019 | 7 | 2019_07_Asomata_english.xlsx
30 | 245 | 630 | 875 | 0 | 0 | 3 | 875 | 85 | 5.599999999998545 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.75 | 8600.000000000007 | 40.97 | 2597.4 | -119.99999999999272 | 8717.500000000007 | 8837.5 | 10.1 | 84.9910254183313 | 8617.5 | 0 | 100.00000000000728 | 0 |  | 102.28587962962963 | 8837.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
31 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 50 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 85.2 | 9680.000000000015 | 41.821 | 3593.0699999999933 | 1080.0000000000073 | 7796.500000000007 | 6716.5 | 10.1 | 84.10570223689035 | 7466.6 | 0 | 389.9000000000069 | 60 |  | 77.73726851851852 | 6716.5 | 2019 | 7 | 2019_07_Asomata_english.xlsx
1 | 900 | 325 | 1225 | 0 | 0 | 3 | 1225 | 107 | 17.299999999995634 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 83.8 | 6320 | 42.011 | 3815.37 | -3360.0000000000146 | 9012.499999999985 | 12372.5 | 10.1 | 86.9226396323843 | 9030.45 | 0 | 42.04999999998472 | 60 |  | 143.2002314814815 | 12372.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
2 | 215 | 645 | 860 | 0 | 0 | 4 | 860 | 110 | 4.400000000001455 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.4 | 7760.00000000002 | 41.8 | 3568.5 | 1440.00000000002 | 10151.8 | 8711.8 | 10.13 | 85.43882359514983 | 10179 | 0 | 32.8000000000211 | 60 |  | 100.83101851851853 | 8711.8 | 2019 | 8 | 2019_08_Asomata_english.xlsx
3 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 50 | 13.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.9 | 8960.00000000002 | 41.69 | 3439.8 | 1200 | 7750 | 6550 | 10 | 85.54079254079252 | 7497.15 | 0 | 252.85 | 0 |  | 75.81018518518519 | 6550 | 2019 | 8 | 2019_08_Asomata_english.xlsx
4 | 310 | 370 | 680 | 0 | 0 | 3 | 680 | 50 | 6.400000000001455 | 8.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.5 | 8000.000000000007 | 41.73 | 3486.6 | -960.0000000000127 | 5839.999999999987 | 6800 | 10 | 86.34588235294117 | 5722.9 | 0 | 117.09999999998763 | 0 |  | 78.70370370370371 | 6800 | 2019 | 8 | 2019_08_Asomata_english.xlsx
5 | 415 | 250 | 665 | 0 | 0 | 3 | 665 | 105 | 8.39999999999418 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85.25 | 9800.000000000007 | 41.85 | 3627 | 1800 | 8516.5 | 6716.5 | 10.1 | 84.00847021118297 | 8280 | 0 | 236.5 | 0 |  | 77.73726851851852 | 6716.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
6 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 50 | 0 | 14.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85 | 9200.000000000007 | 42.1 | 3919.5 | -600 | 6167 | 6767 | 10.1 | 84.49689154962007 | 5907.85 | 0 | 259.15 | 0 |  | 78.32175925925925 | 6767 | 2019 | 8 | 2019_08_Asomata_english.xlsx
7 | 635 | 0 | 635 | 0 | 0 | 3 | 635 | 50 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.9 | 8960.00000000002 | 41.85 | 3627 | -239.99999999998727 | 6173.500000000013 | 6413.5 | 10.1 | 84.6938540007847 | 6118 | 0 | 55.50000000001273 | 0 |  | 74.23032407407408 | 6413.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
8 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 50 | 0 | 13.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.05 | 9320 | 41.9 | 3685.5 | 359.99999999998 | 6859.99999999998 | 6500 | 10 | 85.24274099883856 | 6578.25 | 0 | 281.74999999998 | 0 |  | 75.23148148148148 | 6500 | 2019 | 8 | 2019_08_Asomata_english.xlsx
9 | 675 | 0 | 675 | 0 | 0 | 3 | 675 | 50 | 14.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.95 | 9080.000000000015 | 41.95 | 3744 | -239.99999999998545 | 6577.500000000015 | 6817.5 | 10.1 | 84.59525812883966 | 6278 | 0 | 299.50000000001455 | 0 |  | 78.90625 | 6817.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
10 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 50 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.9 | 8960.00000000002 | 42.07 | 3884.4 | -119.99999999999454 | 6647.0000000000055 | 6767 | 10.1 | 84.6938540007847 | 6304.8 | 0 | 342.2000000000053 | 0 |  | 78.32175925925925 | 6767 | 2019 | 8 | 2019_08_Asomata_english.xlsx
11 | 415 | 280 | 695 | 0 | 0 | 3 | 695 | 55 | 8.400000000001455 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 85.05 | 9320 | 42.05 | 3861 | 359.99999999998 | 7379.49999999998 | 7019.5 | 10.1 | 84.3987534641966 | 7151.6 | 0 | 227.89999999998054 | 0 |  | 81.24421296296296 | 7019.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
12 | 0 | 610 | 610 | 0 | 0 | 3 | 610 | 50 | 0 | 12.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.2 | 9680.000000000015 | 41.7 | 3451.5 | 360.00000000001455 | 6460.000000000015 | 6100 | 10 | 84.94675925925925 | 6287.8 | 0 | 172.20000000001437 | 0 |  | 70.60185185185185 | 6100 | 2019 | 8 | 2019_08_Asomata_english.xlsx
13 | 725 | 0 | 725 | 0 | 0 | 4 | 725 | 55 | 15.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.1 | 9439.999999999993 | 41.7 | 3451.5 | -240.00000000002183 | 7082.499999999978 | 7322.5 | 10.1 | 84.30084307734718 | 7029 | 0 | 113.49999999997817 | 60 |  | 84.7511574074074 | 7322.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
14 | 115 | 655 | 770 | 0 | 0 | 3 | 770 | 90 | 3.3000000000029104 | 14.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.8 | 8720 | 42.1 | 3919.5 | -719.9999999999927 | 7057.000000000007 | 7777 | 10.1 | 84.89173683723513 | 6906.15 | 0 | 150.85000000000673 | 0 |  | 90.01157407407408 | 7777 | 2019 | 8 | 2019_08_Asomata_english.xlsx
15 | 670 | 15 | 685 | 0 | 0 | 3 | 685 | 100 | 13.80000000000291 | 0.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.1 | 7039.999999999993 | 42.1 | 3919.5 | -1680.0000000000073 | 6077.6923076923 | 6850 | 10 | 87.16627078384799 | 5934.8 | 907.6923076923076 | 142.89230769230016 | 0 |  | 79.2824074074074 | 6850 | 2019 | 8 | 2019_08_Asomata_english.xlsx
16 | 0 | 680 | 680 | 0 | 0 | 4 | 680 | 55 | 0 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000.000000000007 | 41.85 | 3627 | 960.0000000000146 | 7828.000000000015 | 6868 | 10.1 | 85.49097262667443 | 7695 | 0 | 193.00000000001455 | 60 |  | 79.49074074074075 | 6868 | 2019 | 8 | 2019_08_Asomata_english.xlsx
17 | 600 | 0 | 600 | 0 | 0 | 3 | 600 | 55 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 85 | 9200.000000000007 | 41.65 | 3393 | 1200 | 7260 | 6060 | 10.1 | 84.49689154962007 | 7227 | 0 | 93 | 60 |  | 70.13888888888889 | 6060 | 2019 | 8 | 2019_08_Asomata_english.xlsx
18 | 160 | 630 | 790 | 0 | 0 | 3 | 790 | 108 | 3.7999999999956344 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.5 | 8000.000000000007 | 41.9 | 3685.5 | -1200 | 6779 | 7979 | 10.1 | 85.49097262667443 | 6794.91 | 0 | 44.090000000000146 | 60 |  | 92.34953703703704 | 7979 | 2019 | 8 | 2019_08_Asomata_english.xlsx
19 | 555 | 0 | 555 | 0 | 0 | 3 | 555 | 54 | 12.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.8 | 8720 | 41.2 | 2866.5 | 719.9999999999927 | 6158.999999999993 | 5439 | 9.8 | 87.49046347510966 | 6030 | 0 | 128.99999999999272 | 0 |  | 62.951388888888886 | 5439 | 2019 | 8 | 2019_08_Asomata_english.xlsx
20 | 0 | 535 | 535 | 0 | 0 | 4 | 535 | 45 | 0 | 12.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.8 | 8720 | 40.8801 | 2492.2169999999974 | 0 | 5403.5 | 5403.5 | 10.1 | 84.89173683723513 | 5350.2 | 0 | 113.29999999999927 | 60 |  | 62.54050925925926 | 5403.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
21 | 605 | 60 | 665 | 0 | 0 | 3 | 665 | 108 | 13.099999999998545 | 1.1500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.3 | 7520 | 41.72016 | 3475.0871999999954 | -1200 | 5616.25 | 6816.25 | 10.25 | 84.63818255203829 | 5638.8 | 0 | 37.44999999999982 | 60 |  | 78.8917824074074 | 6816.25 | 2019 | 8 | 2019_08_Asomata_english.xlsx
22 | 0 | 545 | 545 | 0 | 0 | 3 | 545 | 40 | 0 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.4 | 7760.00000000002 | 41.85 | 3627 | 240.00000000002 | 5744.50000000002 | 5504.5 | 10.1 | 85.69260227909582 | 5752.4 | 0 | 52.10000000002037 | 60 |  | 63.70949074074074 | 5504.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
23 | 235 | 290 | 525 | 0 | 0 | 3 | 525 | 54 | 5.05000000000291 | 6.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.25 | 7400.000000000007 | 41.53 | 3252.6 | -360.00000000001273 | 4889.999999999987 | 5250 | 10 | 86.85680473372781 | 4770 | 0 | 119.99999999998727 | 0 |  | 60.763888888888886 | 5250 | 2019 | 8 | 2019_08_Asomata_english.xlsx
24 | 0 | 555 | 555 | 0 | 0 | 3 | 555 | 54 | 0 | 12.14999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.55 | 8120 | 41.66 | 3404.7 | 719.9999999999927 | 6380.999999999993 | 5661 | 10.2 | 84.55335130526947 | 6332.5 | 0 | 108.49999999999272 | 60 |  | 65.52083333333333 | 5661 | 2019 | 8 | 2019_08_Asomata_english.xlsx
25 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 54 | 12.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 85 | 9200.000000000007 | 41.6005 | 3335.0849999999914 | 1080.0000000000073 | 6584.500000000007 | 5504.5 | 10.1 | 84.49689154962007 | 6482.8 | 0 | 101.700000000008 | 0 |  | 63.70949074074074 | 5504.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
26 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 55 | 0 | 12.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.65 | 8360.00000000002 | 42.0802 | 3896.3339999999944 | -839.9999999999873 | 5637.000000000013 | 6477 | 10.2 | 84.35510194699215 | 5613.7 | 0 | 83.30000000001291 | 60 |  | 74.96527777777777 | 6477 | 2019 | 8 | 2019_08_Asomata_english.xlsx
27 | 520 | 0 | 520 | 0 | 0 | 3 | 520 | 55 | 11.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.75 | 8600.000000000007 | 41.76 | 3521.7 | 239.99999999998727 | 5335.999999999987 | 5096 | 9.8 | 87.59279150256593 | 5153.8 | 0 | 182.199999999988 | 0 |  | 58.98148148148148 | 5096 | 2019 | 8 | 2019_08_Asomata_english.xlsx
28 | 0 | 485 | 485 | 0 | 0 | 3 | 485 | 45 | 0 | 12.05000000000291 | 0 | 0 | 0 | 2.33 | 0 | 0 | 0 | 2.33 | 0 | 3 | ΒΛΑΒΗ Κ.Γ. ΜΕΤΑΦΟΡΑΣ Μ.Τ. ΔΕΔΔΗΕ | 28 | 85.075 | 9380.000000000015 | 41.46 | 3170.7 | 780.0000000000073 | 5533.000000000007 | 4753 | 9.8 | 86.93190566998707 | 5416.8 | 0 | 116.2000000000071 | 0 |  | 55.011574074074076 | 4753 | 2019 | 8 | 2019_08_Asomata_english.xlsx
29 | 505 | 0 | 505 | 0 | 0 | 3 | 505 | 40 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.2 | 9680.000000000015 | 41.2401 | 2913.417000000002 | 300 | 5299.5 | 4999.5 | 9.9 | 85.8048073325851 | 4898.3 | 0 | 401.2 | 0 |  | 57.864583333333336 | 4999.5 | 2019 | 8 | 2019_08_Asomata_english.xlsx
30 | 85 | 495 | 580 | 0 | 0 | 3 | 580 | 110 | 2.099999999998545 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.9 | 8960.00000000002 | 41.63 | 3369.6 | -719.9999999999945 | 5080.0000000000055 | 5800 | 10 | 85.54079254079252 | 4943.2 | 0 | 136.80000000000473 | 0 |  | 67.12962962962963 | 5800 | 2019 | 8 | 2019_08_Asomata_english.xlsx
31 | 490 | 0 | 490 | 0 | 0 | 3 | 490 | 45 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 85.05 | 9320 | 41.6 | 3334.5 | 359.99999999998 | 5259.99999999998 | 4900 | 10 | 85.24274099883856 | 5115 | 0 | 144.99999999998 | 0 |  | 56.71296296296296 | 4900 | 2019 | 8 | 2019_08_Asomata_english.xlsx
1 | 510 | 0 | 510 | 0 | 0 | 4 | 510 | 40 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.9 | 8960.00000000002 | 41.77 | 3533.4 | -359.99999999998 | 4663.50000000002 | 5023.5 | 9.85 | 86.84344420385028 | 4529.6 | 0 | 133.90000000001965 | 0 |  | 58.142361111111114 | 5023.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
2 | 0 | 475 | 475 | 0 | 0 | 3 | 475 | 55 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85 | 9200.000000000007 | 41.8905 | 3674.3850000000025 | 239.99999999998727 | 5037.499999999987 | 4797.5 | 10.1 | 84.49689154962007 | 4934.8 | 0 | 102.69999999998709 | 0 |  | 55.526620370370374 | 4797.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
3 | 495 | 0 | 495 | 0 | 0 | 3 | 495 | 55 | 11.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.9 | 8960.00000000002 | 41.7 | 3451.5 | -239.99999999998727 | 4710.000000000013 | 4950 | 10 | 85.54079254079252 | 4540.6 | 0 | 169.40000000001328 | 0 |  | 57.291666666666664 | 4950 | 2019 | 9 | 2019_09_Asomata_english.xlsx
4 | 0 | 405 | 405 | 0 | 0 | 3 | 405 | 40 | 0 | 9.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.9 | 8960.00000000002 | 41.45 | 3159 | 0 | 4131 | 4131 | 10.2 | 83.8635220988162 | 4075.2 | 0 | 115.8 | 60 |  | 47.8125 | 4131 | 2019 | 9 | 2019_09_Asomata_english.xlsx
5 | 445 | 0 | 445 | 0 | 0 | 3 | 445 | 40 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 85 | 9200.000000000007 | 41.54 | 3264.3 | 239.99999999998727 | 4600.999999999987 | 4361 | 9.8 | 87.08353108685334 | 4431.85 | 0 | 169.1499999999878 | 0 |  | 50.47453703703704 | 4361 | 2019 | 9 | 2019_09_Asomata_english.xlsx
6 | 0 | 535 | 535 | 0 | 0 | 3 | 535 | 55 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.6 | 8239.999999999993 | 41.75 | 3510 | -960.0000000000146 | 4443.499999999985 | 5403.5 | 10.1 | 85.29028959233953 | 4440 | 0 | 63.49999999998545 | 60 |  | 62.54050925925926 | 5403.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
7 | 423 | 0 | 423 | 0 | 0 | 3 | 423 | 40 | 10.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.65 | 8360.00000000002 | 41.59 | 3322.8 | 120.00000000002728 | 4392.3000000000275 | 4272.3 | 10.1 | 85.19030097617029 | 4197.5 | 0 | 194.80000000002747 | 0 |  | 49.447916666666664 | 4272.3 | 2019 | 9 | 2019_09_Asomata_english.xlsx
8 | 0 | 415 | 415 | 0 | 0 | 3 | 415 | 55 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.4 | 7760.00000000002 | 41.38 | 3077.1 | -600 | 3591.5 | 4191.5 | 10.1 | 85.69260227909582 | 3620.8 | 0 | 30.700000000000273 | 60 |  | 48.51273148148148 | 4191.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
9 | 480 | 75 | 555 | 0 | 0 | 3 | 555 | 95 | 10.099999999998545 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.4 | 7760.00000000002 | 41.82 | 3591.9 | 0 | 5688.75 | 5688.75 | 10.25 | 84.43856419696272 | 5715 | 0 | 33.75 | 60 |  | 65.84201388888889 | 5688.75 | 2019 | 9 | 2019_09_Asomata_english.xlsx
10 | 22 | 370 | 392 | 0 | 0 | 3 | 392 | 110 | 0.5 | 8.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.5 | 8000.000000000007 | 41.6 | 3334.5 | 239.99999999998727 | 4199.199999999987 | 3959.2 | 10.1 | 85.49097262667443 | 4102.5 | 0 | 96.69999999998709 | 0 |  | 45.824074074074076 | 3959.2 | 2019 | 9 | 2019_09_Asomata_english.xlsx
11 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 45 | 9.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.7 | 8480.000000000015 | 41.55 | 3276 | 480.0000000000073 | 4368.500000000007 | 3888.5 | 10.1 | 85.09054652537853 | 4112.4 | 0 | 256.10000000000764 | 0 |  | 45.00578703703704 | 3888.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
12 | 0 | 360 | 360 | 0 | 0 | 4 | 360 | 45 | 0 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.8 | 8720 | 41.4 | 3100.5 | 239.99999999998545 | 3839.9999999999854 | 3600 | 10 | 85.74065420560747 | 3767.45 | 0 | 72.54999999998563 | 0 |  | 41.666666666666664 | 3600 | 2019 | 9 | 2019_09_Asomata_english.xlsx
13 | 340 | 0 | 340 | 0 | 0 | 2 | 340 | 45 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.55 | 8120 | 41.3 | 2983.5 | -600 | 3446.2448979591836 | 3434 | 10.1 | 85.39051319938106 | 3329.55 | 612.2448979591836 | 116.69489795918389 | 0 |  | 39.745370370370374 | 3434 | 2019 | 9 | 2019_09_Asomata_english.xlsx
14 | 0 | 310 | 310 | 0 | 0 | 3 | 310 | 45 | 0 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 14 | 84.6 | 8239.999999999993 | 41.2 | 2866.5 | 119.99999999999272 | 3250.9999999999927 | 3131 | 10.1 | 85.29028959233953 | 3145 | 0 | 105.99999999999272 | 0 |  | 36.238425925925924 | 3131 | 2019 | 9 | 2019_09_Asomata_english.xlsx
15 | 325 | 0 | 325 | 0 | 0 | 2 | 325 | 55 | 7.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.5 | 8000.000000000007 | 41.32 | 3006.9 | -239.99999999998545 | 3616.858974358989 | 3282.5 | 10.1 | 85.49097262667443 | 3538.75 | 574.3589743589744 | 78.10897435898914 | 0 |  | 37.991898148148145 | 3282.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
16 | 85 | 510 | 595 | 0 | 0 | 3 | 595 | 90 | 1.6499999999941792 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.4 | 7760.00000000002 | 41.75 | 3510 | -239.99999999998727 | 5769.500000000013 | 6009.5 | 10.1 | 85.69260227909582 | 5707.8 | 0 | 61.70000000001346 | 0 |  | 69.55439814814815 | 6009.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
17 | 530 | 355 | 885 | 0 | 0 | 3 | 885 | 110 | 10.60000000000582 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 17 | 84.05 | 6920 | 41.76 | 3521.7 | -840.00000000002 | 8186.99999999998 | 9027 | 10.2 | 85.55874192721085 | 8228.75 | 0 | 18.24999999997999 | 60 |  | 104.47916666666667 | 9027 | 2019 | 9 | 2019_09_Asomata_english.xlsx
18 | 90 | 280 | 370 | 0 | 0 | 3 | 370 | 110 | 2 | 6.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.3 | 7520 | 41.9 | 3685.5 | 600 | 4466.5 | 3866.5 | 10.45 | 83.01831302951125 | 4499.8 | 0 | 26.700000000000728 | 60 |  | 44.751157407407405 | 3866.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
19 | 330 | 0 | 330 | 0 | 0 | 3 | 330 | 45 | 8.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.2 | 7280.000000000014 | 41.9 | 3685.5 | -239.99999999998636 | 3208.500000000013 | 3448.5 | 10.45 | 83.21503888977074 | 3045.9 | 0 | 162.6000000000131 | 0 |  | 39.913194444444436 | 3448.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
20 | 0 | 295 | 295 | 0 | 0 | 3 | 295 | 40 | 0 | 7.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.3 | 7520 | 41.9 | 3685.5 | 239.99999999998636 | 3189.9999999999864 | 2950 | 10 | 86.75413711583924 | 3072.85 | 0 | 117.14999999998645 | 0 |  | 34.14351851851852 | 2950 | 2019 | 9 | 2019_09_Asomata_english.xlsx
21 | 255 | 0 | 255 | 0 | 0 | 3 | 255 | 45 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.95 | 3744 | 0 | 2575.5 | 2575.5 | 10.1 | 85.89518526320718 | 2514.15 | 0 | 61.350000000000364 | 0 |  | 29.80902777777778 | 2575.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
22 | 0 | 300 | 300 | 0 | 0 | 2 | 300 | 55 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.4 | 7760.00000000002 | 41.9 | 3685.5 | 240.00000000002 | 3240.00000000002 | 3000 | 10 | 86.54952830188678 | 3115.4 | 0 | 124.60000000001946 | 0 |  | 34.72222222222222 | 3000 | 2019 | 9 | 2019_09_Asomata_english.xlsx
23 | 255 | 0 | 255 | 0 | 0 | 3 | 255 | 45 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.7 | 8480.000000000015 | 41.5 | 3217.5 | 719.9999999999945 | 3295.4999999999945 | 2575.5 | 10.1 | 85.09054652537853 | 3196.05 | 0 | 99.44999999999436 | 0 |  | 29.80902777777778 | 2575.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
24 | 0 | 220 | 220 | 0 | 0 | 3 | 220 | 55 | 0 | 5.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85 | 9200.000000000007 | 40.97 | 2597.4 | 719.9999999999927 | 2941.9999999999927 | 2222 | 10.1 | 84.49689154962007 | 2873.85 | 0 | 98.14999999999281 | 30 |  | 25.71759259259259 | 2222 | 2019 | 9 | 2019_09_Asomata_english.xlsx
25 | 255 | 40 | 295 | 0 | 0 | 3 | 295 | 90 | 6.599999999998545 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 85.05 | 9320 | 41.11 | 2761.2 | 119.99999999999272 | 3010.9999999999927 | 2891 | 9.8 | 86.98238877432506 | 2841.6 | 0 | 169.39999999999236 | 0 |  | 33.460648148148145 | 2891 | 2019 | 9 | 2019_09_Asomata_english.xlsx
26 | 170 | 168 | 338 | 0 | 0 | 3 | 338 | 55 | 3.75 | 3.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.8 | 8720 | 41.8 | 3568.5 | -600 | 2830.7 | 3430.7 | 10.15 | 84.47355094148521 | 2625 | 0 | 205.7 | 0 |  | 39.707175925925924 | 3430.7 | 2019 | 9 | 2019_09_Asomata_english.xlsx
27 | 250 | 47 | 297 | 0 | 0 | 3 | 297 | 110 | 5.69999999999709 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.85 | 8839.999999999993 | 41.93 | 3720.6 | 119.99999999999272 | 3655.4142857142783 | 2999.7 | 10.1 | 84.79267996811352 | 3661.75 | 535.7142857142857 | 23.66428571427832 | 30 |  | 34.71875 | 2999.7 | 2019 | 9 | 2019_09_Asomata_english.xlsx
28 | 20 | 235 | 255 | 0 | 0 | 3 | 255 | 94 | 0.4500000000043656 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.8 | 8720 | 41.8 | 3568.5 | -119.99999999999272 | 2468.2500000000073 | 2588.25 | 10.15 | 84.4735509414852 | 2310.3 | 0 | 157.95000000000755 | 0 |  | 29.95659722222222 | 2588.25 | 2019 | 9 | 2019_09_Asomata_english.xlsx
29 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 40 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.9 | 8960.00000000002 | 41.5 | 3217.5 | 240.00000000002 | 2350.00000000002 | 2110 | 10.55 | 81.08131994387917 | 2204 | 0 | 146.00000000002 | 0 |  | 24.421296296296298 | 2110 | 2019 | 9 | 2019_09_Asomata_english.xlsx
30 | 0 | 195 | 195 | 0 | 0 | 3 | 195 | 40 | 0 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.9 | 8960.00000000002 | 41.081 | 2727.27 | 0 | 2047.5 | 2047.5 | 10.5 | 81.46742146742146 | 1820.7 | 0 | 286.8 | 60 |  | 23.697916666666668 | 2047.5 | 2019 | 9 | 2019_09_Asomata_english.xlsx
1 | 200 | 85 | 285 | 0 | 0 | 3 | 285 | 110 | 4.799999999995634 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.9 | 8960.00000000002 | 41.84 | 3615.3 | 0 | 3312.173469387755 | 2878.5 | 10.1 | 84.6938540007847 | 3176.8 | 433.67346938775506 | 135.373469387755 | 0 |  | 33.31597222222222 | 2878.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
2 | 0 | 175 | 175 | 0 | 0 | 2 | 175 | 45 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.05 | 9320 | 41.52 | 3240.9 | 359.99999999998 | 2127.49999999998 | 1767.5 | 10.1 | 84.3987534641966 | 2121.55 | 0 | 35.949999999980264 | 30 |  | 20.457175925925927 | 1767.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
3 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 45 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.1 | 9439.999999999993 | 41.19 | 2854.8 | 119.99999999999272 | 3011.85233160621 | 1767.5 | 10.1 | 84.30084307734718 | 2810.5 | 1124.3523316062176 | 201.3523316062101 | 0 |  | 20.457175925925927 | 1767.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
4 | 0 | 370 | 370 | 0 | 0 | 3 | 370 | 55 | 0 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.5 | 8000.000000000007 | 41.48 | 3194.1 | -1439.9999999999854 | 2445.0000000000146 | 3885 | 10.5 | 82.2341736694678 | 2256.45 | 0 | 248.55000000001473 | 60 |  | 44.96527777777778 | 3885 | 2019 | 10 | 2019_10_Asomata_english.xlsx
5 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 45 | 4.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.6 | 8239.999999999993 | 41 | 2632.5 | 239.99999999998545 | 1839.9999999999854 | 1600 | 10 | 86.14319248826293 | 1638.35 | 0 | 201.64999999998554 | 0 |  | 18.51851851851852 | 1600 | 2019 | 10 | 2019_10_Asomata_english.xlsx
6 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 55 | 0 | 4.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.75 | 8600.000000000007 | 41.03 | 2667.6 | 360.00000000001455 | 2380.0000000000146 | 2020 | 10.1 | 84.9910254183313 | 2272.55 | 0 | 167.45000000001482 | 60 |  | 23.37962962962963 | 2020 | 2019 | 10 | 2019_10_Asomata_english.xlsx
7 | 295 | 0 | 295 | 0 | 0 | 2 | 295 | 54 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.4 | 7760.00000000002 | 41.77 | 3533.4 | -839.9999999999873 | 2139.5000000000127 | 2979.5 | 10.1 | 85.69260227909582 | 1992.9 | 0 | 176.60000000001287 | 30 |  | 34.4849537037037 | 2979.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
8 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 40 | 0 | 4.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.5 | 8000.000000000007 | 41.17 | 2831.4 | 239.99999999998727 | 1855.9999999999873 | 1616 | 10.1 | 85.49097262667443 | 1597.5 | 0 | 258.49999999998727 | 0 |  | 18.703703703703702 | 1616 | 2019 | 10 | 2019_10_Asomata_english.xlsx
9 | 205 | 0 | 205 | 0 | 0 | 3 | 205 | 45 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 41.38 | 3077.1 | -480.0000000000073 | 1549.4999999999927 | 2029.5 | 9.9 | 87.63044153115075 | 1457.15 | 0 | 152.34999999999286 | 60 |  | 23.489583333333332 | 2029.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
10 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 40 | 0 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.08 | 6992 | 41.77 | 3533.4 | -527.9999999999973 | 1795 | 2323 | 10.1 | 86.34425704927908 | 1562.2 | 0 | 232.80000000000268 | 0 |  | 26.886574074074073 | 2323 | 2019 | 10 | 2019_10_Asomata_english.xlsx
11 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 54 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.05 | 6920 | 41.59 | 3322.8 | -72.00000000000273 | 1457.75 | 1529.75 | 10.55 | 82.72030025190053 | 1569.5 | 0 | 8.249999999997272 | 120 |  | 17.705439814814813 | 1529.75 | 2019 | 10 | 2019_10_Asomata_english.xlsx
12 | 0 | 135 | 135 | 0 | 0 | 3 | 135 | 55 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.55 | 8120 | 41.29 | 2971.8 | 1200 | 2563.5 | 1363.5 | 10.1 | 85.39051319938106 | 2452.8 | 0 | 170.7 | 60 |  | 15.78125 | 1363.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
13 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 40 | 3.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.8 | 8720 | 40.96 | 2585.7 | 600 | 1972 | 1372 | 9.8 | 87.49046347510966 | 1824 | 0 | 148 | 0 |  | 15.87962962962963 | 1372 | 2019 | 10 | 2019_10_Asomata_english.xlsx
14 | 0 | 120 | 120 | 0 | 0 | 3 | 120 | 55 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.9 | 8960.00000000002 | 40.57 | 2129.4 | 240.00000000002 | 1440.00000000002 | 1200 | 10 | 85.54079254079252 | 1298.6 | 0 | 141.4000000000201 | 0 |  | 13.88888888888889 | 1200 | 2019 | 10 | 2019_10_Asomata_english.xlsx
15 | 220 | 0 | 220 | 0 | 0 | 3 | 220 | 55 | 4.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.95 | 9080.000000000015 | 41 | 2632.5 | 119.99999999999454 | 2275.9999999999945 | 2156 | 9.8 | 87.18490888788575 | 2112.8 | 0 | 163.19999999999482 | 0 |  | 24.953703703703702 | 2156 | 2019 | 10 | 2019_10_Asomata_english.xlsx
16 | 0 | 165 | 165 | 0 | 0 | 2 | 165 | 55 | 0 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85 | 9200.000000000007 | 41.2 | 2866.5 | 119.99999999999272 | 1786.4999999999927 | 1666.5 | 10.1 | 84.49689154962007 | 1565.6 | 0 | 220.89999999999281 | 0 |  | 19.288194444444443 | 1666.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
17 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 45 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85 | 9200.000000000007 | 41.05 | 2691 | 0 | 1464.5 | 1464.5 | 10.1 | 84.49689154962007 | 1406 | 0 | 58.5 | 0 |  | 16.95023148148148 | 1464.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
18 | 90 | 165 | 255 | 0 | 0 | 3 | 255 | 108 | 1.6999999999970896 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.7 | 8480.000000000015 | 41.5 | 3217.5 | -719.9999999999927 | 1830.0000000000073 | 2550 | 10 | 85.94145199063232 | 1577.95 | 0 | 252.05000000000723 | 0 |  | 29.51388888888889 | 2550 | 2019 | 10 | 2019_10_Asomata_english.xlsx
19 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 45 | 2.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.75 | 8600.000000000007 | 41.08 | 2726.1 | 119.99999999999272 | 1331.9999999999927 | 1212 | 10.1 | 84.9910254183313 | 1170.25 | 0 | 161.74999999999272 | 0 |  | 14.027777777777779 | 1212 | 2019 | 10 | 2019_10_Asomata_english.xlsx
20 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 45 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.95 | 9080.000000000015 | 40.57 | 2129.4 | 480.0000000000073 | 2044.6282051282124 | 959.5 | 10.1 | 84.59525812883966 | 1947.9 | 605.1282051282051 | 156.72820512821227 | 60 |  | 11.105324074074074 | 959.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
21 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 45 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85 | 9200.000000000007 | 40.11 | 1591.2 | 119.99999999999272 | 1129.9999999999927 | 1010 | 10.1 | 84.49689154962007 | 941.7 | 0 | 248.2999999999928 | 60 |  | 11.689814814814815 | 1010 | 2019 | 10 | 2019_10_Asomata_english.xlsx
22 | 0 | 100 | 100 | 0 | 0 | 2 | 100 | 40 | 0 | 2.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85 | 9200.000000000007 | 39.77 | 1193.4000000000053 | 0 | 3298.5106382978724 | 990 | 9.9 | 86.20389945971341 | 3060 | 2308.5106382978724 | 238.51063829787245 | 0 |  | 11.458333333333334 | 990 | 2019 | 10 | 2019_10_Asomata_english.xlsx
23 | 90 | 0 | 90 | 0 | 0 | 2 | 90 | 35 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.05 | 9320 | 39.54 | 924.3 | 119.99999999999272 | 1697.17021276595 | 891 | 9.9 | 86.10377878670562 | 1628 | 686.1702127659574 | 69.17021276595005 | 0 |  | 10.3125 | 891 | 2019 | 10 | 2019_10_Asomata_english.xlsx
24 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 55 | 0 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.15 | 9560.00000000002 | 39.8 | 1228.4999999999945 | 240.00000000002 | 1626.00000000002 | 1386 | 9.9 | 85.90423352879898 | 1568.8 | 0 | 57.20000000001983 | 0 |  | 16.041666666666668 | 1386 | 2019 | 10 | 2019_10_Asomata_english.xlsx
25 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 35 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.22 | 9750 | 39.75 | 1170 | 189.99999999998 | 1328.49999999998 | 1138.5 | 9.9 | 85.76510126718364 | 1154.4 | 0 | 174.0999999999799 | 0 |  | 13.177083333333334 | 1138.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
26 | 70 | 135 | 205 | 0 | 0 | 3 | 205 | 390 | 2 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 85 | 9200.000000000007 | 40.7 | 2281.5 | -549.9999999999927 | 2208.2234042553264 | 2029.5 | 9.9 | 86.20389945971341 | 2049.8 | 728.7234042553191 | 158.4234042553262 | 0 |  | 23.489583333333332 | 2029.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
27 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 54 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.9 | 8960.00000000002 | 41.5 | 3217.5 | -239.99999999998727 | 1591.5000000000127 | 1831.5 | 9.9 | 86.40484095029548 | 1480 | 0 | 111.50000000001273 | 0 |  | 21.197916666666668 | 1831.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
28 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 55 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.05 | 9320 | 41.65 | 3393 | 359.99999999998 | 1448.99999999998 | 1089 | 9.9 | 86.10377878670562 | 1346.8 | 0 | 102.19999999998004 | 0 |  | 12.604166666666666 | 1089 | 2019 | 10 | 2019_10_Asomata_english.xlsx
29 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 50 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85 | 9200.000000000007 | 41.78 | 3545.1 | -119.99999999999272 | 1711.5000000000073 | 1831.5 | 9.9 | 86.20389945971341 | 1552.5 | 0 | 159.00000000000728 | 0 |  | 21.197916666666668 | 1831.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
30 | 0 | 155 | 155 | 0 | 0 | 3 | 155 | 50 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.95 | 9080.000000000015 | 41.87 | 3650.4 | -119.99999999999272 | 1414.5000000000073 | 1534.5 | 9.9 | 86.30425324255359 | 1228.4 | 0 | 186.10000000000719 | 0 |  | 17.760416666666668 | 1534.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
31 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 35 | 3.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 85.1 | 9439.999999999993 | 41.84 | 3615.3 | 359.9999999999782 | 1498.4999999999782 | 1138.5 | 9.9 | 86.0038904122431 | 1372.5 | 0 | 125.99999999997817 | 0 |  | 13.177083333333334 | 1138.5 | 2019 | 10 | 2019_10_Asomata_english.xlsx
1 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 35 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85.15 | 9560.00000000002 | 41.76 | 3521.7 | 120.00000000002728 | 1180.5000000000273 | 1060.5 | 10.1 | 84.20315959753565 | 1041.9 | 0 | 138.60000000002742 | 0 |  | 12.274305555555555 | 1060.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
2 | 0 | 145 | 145 | 0 | 0 | 2 | 145 | 54 | 0 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.18 | 9632.000000000024 | 41.75 | 3510 | 72.00000000000364 | 1624.5212765957483 | 1435.5 | 9.9 | 85.8445501798906 | 1449.6 | 117.02127659574468 | 174.9212765957484 | 0 |  | 16.614583333333332 | 1435.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
3 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85.03 | 9272.00000000001 | 41.58 | 3311.1 | -360.00000000001455 | 836.6914893616876 | 643.5 | 9.9 | 86.14379913473569 | 747.45 | 553.1914893617021 | 89.24148936168763 | 0 |  | 7.447916666666667 | 643.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
4 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.56 | 8144.000000000013 | 41.5 | 3217.5 | -1128 | 4568.361702127663 | 707 | 10.1 | 85.37044963894886 | 4321.6 | 4989.36170212766 | 246.76170212766283 | 0 |  | 8.18287037037037 | 707 | 2019 | 11 | 2019_11_Asomata_english.xlsx
5 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.85 | 8839.999999999993 | 41.3 | 2983.5 | 695.99999999998 | 1345.99999999998 | 650 | 10 | 85.64060676779464 | 1073.1 | 0 | 272.8999999999801 | 0 |  | 7.523148148148148 | 650 | 2019 | 11 | 2019_11_Asomata_english.xlsx
6 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.9 | 8960.00000000002 | 41.06 | 2702.7 | 120.00000000002728 | 776.5000000000273 | 656.5 | 10.1 | 84.6938540007847 | 795.2 | 0 | 41.30000000002735 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
7 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 40 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.7 | 8480.000000000015 | 41 | 2632.5 | -480.00000000000546 | 1319.3829787233988 | 693 | 9.9 | 86.80954746528516 | 1110 | 1106.3829787234042 | 209.38297872339876 | 0 |  | 8.020833333333334 | 693 | 2019 | 11 | 2019_11_Asomata_english.xlsx
8 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 40 | 0 | 2.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.9 | 8960.00000000002 | 40.99 | 2620.8 | 480.00000000000546 | 1420.5000000000055 | 940.5 | 9.9 | 86.40484095029548 | 1327.5 | 0 | 93.00000000000546 | 0 |  | 10.885416666666666 | 940.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
9 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85.1 | 9439.999999999993 | 40.8 | 2398.5 | 479.9999999999727 | 1172.9999999999727 | 693 | 9.9 | 86.0038904122431 | 930 | 0 | 242.99999999997272 | 0 |  | 8.020833333333334 | 693 | 2019 | 11 | 2019_11_Asomata_english.xlsx
10 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 55 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.58 | 8192 | 41.37 | 3065.4 | -1247.999999999989 | 2133.9148936170322 | 1600 | 10 | 86.1836542977924 | 2070 | 1781.9148936170213 | 123.91489361703225 | 60 |  | 18.51851851851852 | 1600 | 2019 | 11 | 2019_11_Asomata_english.xlsx
11 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 35 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.9 | 8960.00000000002 | 41.52 | 3240.9 | 768.0000000000164 | 1980.0000000000164 | 1212 | 10.1 | 84.6938540007847 | 1957.5 | 0 | 82.50000000001637 | 60 |  | 14.027777777777779 | 1212 | 2019 | 11 | 2019_11_Asomata_english.xlsx
12 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.95 | 9080.000000000015 | 41.25 | 2925 | 119.99999999999454 | 812.9999999999945 | 693 | 9.9 | 86.30425324255359 | 780 | 0 | 92.99999999999454 | 60 |  | 8.020833333333334 | 693 | 2019 | 11 | 2019_11_Asomata_english.xlsx
13 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 54 | 1.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.67 | 8408.000000000011 | 41.05 | 2691 | -672.0000000000036 | 1241.512820512817 | 693 | 9.9 | 86.87058066012834 | 900 | 1220.5128205128206 | 341.5128205128169 | 0 |  | 8.020833333333334 | 693 | 2019 | 11 | 2019_11_Asomata_english.xlsx
14 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.75 | 8600.000000000007 | 41 | 2632.5 | 191.99999999999636 | 991.9999999999964 | 800 | 10 | 85.84093567251462 | 817.5 | 0 | 174.49999999999636 | 0 |  | 9.25925925925926 | 800 | 2019 | 11 | 2019_11_Asomata_english.xlsx
15 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.85 | 8839.999999999993 | 40.9 | 2515.5 | 239.99999999998545 | 946.9999999999854 | 707 | 10.1 | 84.79267996811352 | 730 | 0 | 276.99999999998545 | 60 |  | 8.18287037037037 | 707 | 2019 | 11 | 2019_11_Asomata_english.xlsx
16 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.95 | 9080.000000000015 | 40.74 | 2328.3 | 240.00000000002183 | 896.5000000000218 | 656.5 | 10.1 | 84.59525812883966 | 810.3 | 0 | 146.20000000002187 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
17 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.8 | 6320 | 40.56 | 2117.7 | -2760.0000000000146 | 806.0744680850917 | 656.5 | 10.1 | 86.9226396323843 | 798 | 2909.574468085106 | 68.07446808509167 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
18 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.9 | 6560.00000000002 | 40.39 | 1918.8 | 240.00000000002 | 896.50000000002 | 656.5 | 10.1 | 86.71518703182966 | 661.5 | 0 | 235.00000000002 | 0 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
19 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84 | 6800.000000000007 | 40.25 | 1755 | 239.99999999998727 | 896.4999999999873 | 656.5 | 10.1 | 86.50872230080151 | 845.25 | 0 | 81.24999999998727 | 30 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
20 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.2 | 7280.000000000014 | 40.2 | 1696.5000000000055 | 480.00000000000637 | 1130.0000000000064 | 650 | 10 | 86.95971563981043 | 765 | 0 | 365.00000000000637 | 0 |  | 7.523148148148148 | 650 | 2019 | 11 | 2019_11_Asomata_english.xlsx
21 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.9 | 8960.00000000002 | 40.22 | 1719.9 | 1680.0000000000064 | 5933.358638743462 | 656.5 | 10.1 | 84.6938540007847 | 5735 | 3596.8586387434552 | 258.3586387434616 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
22 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85 | 9200.000000000007 | 40.2 | 1696.5000000000055 | 239.99999999998727 | 896.4999999999873 | 656.5 | 10.1 | 84.49689154962007 | 759.2 | 0 | 197.29999999998734 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
23 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 85.15 | 9560.00000000002 | 40.16 | 1649.6999999999946 | 360.00000000001273 | 1067.0000000000127 | 707 | 10.1 | 84.20315959753565 | 853.15 | 0 | 243.85000000001276 | 30 |  | 8.18287037037037 | 707 | 2019 | 11 | 2019_11_Asomata_english.xlsx
24 | 0 | 55 | 55 | 0 | 0 | 3 | 55 | 40 | 0 | 1.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.05 | 9320 | 40.07 | 1544.4 | -240.00000000002 | 2294.223404255299 | 555.5 | 10.1 | 84.3987534641966 | 2175.4 | 1978.723404255319 | 178.823404255299 | 60 |  | 6.429398148148148 | 555.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
25 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 55 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.1 | 9439.999999999993 | 41 | 2632.5 | 119.99999999999272 | 1654.4999999999927 | 1534.5 | 9.9 | 86.0038904122431 | 854.1 | 0 | 800.3999999999927 | 0 |  | 17.760416666666668 | 1534.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
26 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 85.05 | 9320 | 41.05 | 2691 | -119.99999999999272 | 1631.2368421052704 | 656.5 | 10.1 | 84.3987534641966 | 1284.8 | 1094.7368421052631 | 406.43684210527044 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
27 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 85.1 | 9439.999999999993 | 41.06 | 2702.7 | 119.99999999999272 | 776.4999999999927 | 656.5 | 10.1 | 84.30084307734718 | 693.5 | 0 | 142.99999999999272 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
28 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.5 | 8000.000000000007 | 41.15 | 2808 | -1439.9999999999854 | 1819.289473684225 | 643.5 | 9.9 | 87.21806298276887 | 1547.6 | 2615.7894736842104 | 271.68947368422505 | 0 |  | 7.447916666666667 | 643.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
29 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 35 | 2.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.7 | 8480.000000000015 | 41.55 | 3276 | 480.0000000000073 | 2315.3157894736914 | 909 | 10.1 | 85.09054652537853 | 2124.3 | 926.3157894736842 | 191.0157894736917 | 0 |  | 10.520833333333334 | 909 | 2019 | 11 | 2019_11_Asomata_english.xlsx
30 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 40 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.45 | 7880.000000000014 | 41.68 | 3428.1 | -600.0000000000009 | 2225.755319148935 | 2171.5 | 10.1 | 85.5916687075068 | 2102.4 | 654.2553191489362 | 183.355319148935 | 60 |  | 25.13310185185185 | 2171.5 | 2019 | 11 | 2019_11_Asomata_english.xlsx
1 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.2 | 7280.000000000014 | 41.48 | 3194.1 | -600 | 1247.9893617021276 | 656.5 | 10.1 | 86.09872835624795 | 970.9 | 1191.4893617021276 | 337.0893617021276 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
2 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.45 | 7880.000000000014 | 41.5 | 3217.5 | 600 | 1307 | 707 | 10.1 | 85.5916687075068 | 1270.2 | 0 | 96.8 | 60 |  | 8.18287037037037 | 707 | 2019 | 12 | 2019_12_Asomata_english.xlsx
3 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 40 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 83.9 | 6560.00000000002 | 41.71 | 3463.2 | -1319.9999999999936 | 1100.5268817204364 | 1313 | 10.1 | 86.71518703182966 | 1099 | 1107.52688172043 | 61.52688172043645 | 60 |  | 15.19675925925926 | 1313 | 2019 | 12 | 2019_12_Asomata_english.xlsx
4 | 50 | 20 | 70 | 0 | 0 | 4 | 70 | 70 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.3 | 7520 | 41.71 | 3463.2 | 959.99999999998 | 1666.99999999998 | 707 | 10.1 | 85.89518526320718 | 1379.7 | 0 | 347.29999999997995 | 60 |  | 8.18287037037037 | 707 | 2019 | 12 | 2019_12_Asomata_english.xlsx
5 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.3 | 7520 | 41.84 | 3615.3 | 0 | 2603.6989247311826 | 808 | 10.1 | 85.89518526320718 | 2569.6 | 1795.6989247311826 | 94.0989247311827 | 60 |  | 9.351851851851851 | 808 | 2019 | 12 | 2019_12_Asomata_english.xlsx
6 | 60 | 5 | 65 | 0 | 0 | 4 | 65 | 35 | 1.5 | 0.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 83.8 | 6320 | 41.84 | 3615.3 | -1200 | 757.018134715026 | 656.5 | 10.1 | 86.9226396323843 | 695.6 | 1300.518134715026 | 121.41813471502599 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
7 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84 | 6800.000000000007 | 41.84 | 3615.3 | 480.0000000000073 | 1130.0000000000073 | 650 | 10 | 87.37380952380953 | 955.5 | 0 | 174.50000000000728 | 0 |  | 7.523148148148148 | 650 | 2019 | 12 | 2019_12_Asomata_english.xlsx
8 | 0 | 105 | 105 | 0 | 0 | 4 | 105 | 40 | 0 | 2.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 8 | 84.6 | 8239.999999999993 | 41.7 | 3451.5 | 1439.9999999999854 | 2500.4999999999854 | 1060.5 | 10.1 | 85.29028959233953 | 2328.7 | 0 | 231.79999999998563 | 60 |  | 12.274305555555555 | 1060.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
9 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.93 | 9032.000000000024 | 41.58 | 3311.1 | 792.0000000000309 | 1435.500000000031 | 643.5 | 9.9 | 86.34446020889067 | 1116.9 | 0 | 318.60000000003106 | 0 |  | 7.447916666666667 | 643.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
10 | 0 | 290 | 290 | 0 | 0 | 4 | 290 | 55 | 0 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.8 | 6320 | 41.43 | 3135.6 | -2712.0000000000236 | 860.6170212765721 | 2929 | 10.1 | 86.9226396323843 | 715.4 | 643.6170212765958 | 205.21702127657215 | 60 |  | 33.90046296296296 | 2929 | 2019 | 12 | 2019_12_Asomata_english.xlsx
11 | 130 | 0 | 130 | 0 | 0 | 4 | 130 | 35 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.5 | 8000.000000000007 | 41.74 | 3498.3 | 1680.0000000000073 | 2993.0000000000073 | 1313 | 10.1 | 85.49097262667443 | 2087.8 | 0 | 965.2000000000075 | 60 |  | 15.19675925925926 | 1313 | 2019 | 12 | 2019_12_Asomata_english.xlsx
12 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 40 | 0 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.55 | 8120 | 41.64 | 3381.3 | 119.99999999999272 | 1357.4999999999927 | 1237.5 | 9.9 | 87.11557407209581 | 1270.2 | 0 | 87.29999999999268 | 0 |  | 14.322916666666666 | 1237.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
13 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 40 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.7 | 8480.000000000015 | 41.32 | 3006.9 | 360.00000000001455 | 1016.5000000000146 | 656.5 | 10.1 | 85.09054652537853 | 730 | 0 | 286.50000000001455 | 0 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
14 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.75 | 8600.000000000007 | 41.1 | 2749.5 | 119.99999999999272 | 776.4999999999927 | 656.5 | 10.1 | 84.9910254183313 | 657 | 0 | 179.49999999999272 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
15 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.65 | 8360.00000000002 | 40.74 | 2328.3 | -239.99999999998727 | 943.0957446808638 | 656.5 | 10.1 | 85.19030097617029 | 657 | 526.5957446808511 | 346.09574468086385 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
16 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 40 | 0 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.75 | 8600.000000000007 | 40.3 | 1813.4999999999945 | 239.99999999998727 | 883.4999999999873 | 643.5 | 9.9 | 86.70801583082284 | 737.3 | 0 | 146.1999999999873 | 0 |  | 7.447916666666667 | 643.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
17 | 100 | 0 | 100 | 0 | 0 | 6 | 100 | 35 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.85 | 8839.999999999993 | 40.35 | 1872 | 239.99999999998545 | 1229.9999999999854 | 990 | 9.9 | 86.50566340181277 | 1036.6 | 0 | 193.39999999998554 | 0 |  | 11.458333333333334 | 990 | 2019 | 12 | 2019_12_Asomata_english.xlsx
18 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 54 | 0 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85 | 9200.000000000007 | 40.15 | 1638 | 360.00000000001455 | 1003.5000000000146 | 643.5 | 9.9 | 86.20389945971341 | 737.3 | 0 | 266.2000000000146 | 0 |  | 7.447916666666667 | 643.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
19 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 35 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.95 | 9080.000000000015 | 40.21 | 1708.2 | -119.99999999999272 | 870.0000000000073 | 990 | 9.9 | 86.30425324255359 | 751.9 | 0 | 118.1000000000073 | 0 |  | 11.458333333333334 | 990 | 2019 | 12 | 2019_12_Asomata_english.xlsx
20 | 0 | 220 | 220 | 0 | 0 | 5 | 220 | 35 | 0 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.25 | 9820 | 41.37 | 3065.4 | 739.9999999999854 | 3598.8510638297726 | 2178 | 9.9 | 85.7056110235301 | 3336.1 | 680.8510638297872 | 262.75106382977265 | 0 |  | 25.208333333333332 | 2178 | 2019 | 12 | 2019_12_Asomata_english.xlsx
21 | 65 | 5 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0.09999999999854481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85 | 9200.000000000007 | 41.46 | 3170.7 | -619.9999999999927 | 3039.1276595744753 | 707 | 10.1 | 84.49689154962007 | 2905.4 | 2952.127659574468 | 133.72765957447518 | 0 |  | 8.18287037037037 | 707 | 2019 | 12 | 2019_12_Asomata_english.xlsx
22 | 0 | 465 | 465 | 0 | 0 | 4 | 465 | 40 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85.05 | 9320 | 41.74 | 3498.3 | 119.99999999999272 | 6462.861702127652 | 4603.5 | 9.9 | 86.10377878670562 | 6314.5 | 1739.3617021276596 | 148.36170212765228 | 0 |  | 53.28125 | 4603.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
23 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 55 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.45 | 5480.000000000014 | 41.44 | 3147.3 | -3839.9999999999864 | 1764.430107526895 | 884 | 10.4 | 85.12805047786954 | 1645 | 4720.430107526881 | 179.43010752689497 | 60 |  | 10.231481481481481 | 884 | 2019 | 12 | 2019_12_Asomata_english.xlsx
24 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84 | 6800.000000000007 | 41.45 | 3159 | 1319.9999999999936 | 2026.9999999999936 | 707 | 10.1 | 86.50872230080151 | 2007.5 | 0 | 79.49999999999363 | 60 |  | 8.18287037037037 | 707 | 2019 | 12 | 2019_12_Asomata_english.xlsx
25 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84 | 6800.000000000007 | 41.4 | 3100.5 | 0 | 2364.8333333333335 | 656.5 | 10.1 | 86.50872230080151 | 2190.4 | 1708.3333333333335 | 174.4333333333334 | 0 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
26 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.05 | 6920 | 41.35 | 3042 | 119.99999999999272 | 776.4999999999927 | 656.5 | 10.1 | 86.4058581839159 | 715.4 | 0 | 91.09999999999275 | 30 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
27 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.4 | 7760.00000000002 | 41.3 | 2983.5 | 840.00000000002 | 1490.00000000002 | 650 | 10 | 86.54952830188678 | 1065 | 0 | 485.00000000002 | 60 |  | 7.523148148148148 | 650 | 2019 | 12 | 2019_12_Asomata_english.xlsx
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.1 | 9439.999999999993 | 41.25 | 2925 | 1679.9999999999727 | 2386.9999999999727 | 707 | 10.1 | 84.30084307734718 | 2265 | 0 | 121.99999999997272 | 0 |  | 8.18287037037037 | 707 | 2019 | 12 | 2019_12_Asomata_english.xlsx
29 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 83.95 | 6680.000000000014 | 41.22 | 2889.9 | -2759.999999999979 | 1353.9468085106591 | 656.5 | 10.1 | 86.61183162416361 | 1244.1 | 3457.446808510638 | 169.846808510659 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
30 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 55 | 0 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.5 | 8000.000000000007 | 41.19 | 2854.8 | 1319.9999999999936 | 1976.4999999999936 | 656.5 | 10.1 | 85.49097262667443 | 1830 | 0 | 206.49999999999363 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
31 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.2 | 7280.000000000014 | 41.17 | 2831.4 | -719.9999999999936 | 920.5425531914957 | 656.5 | 10.1 | 86.09872835624795 | 919.8 | 984.0425531914893 | 60.742553191495745 | 60 |  | 7.59837962962963 | 656.5 | 2019 | 12 | 2019_12_Asomata_english.xlsx
1 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.4 | 7760.00000000002 | 41.13 | 2784.6 | 480.00000000000637 | 2287.541666666673 | 656.5 | 10.1 | 85.69260227909582 | 2100 | 1151.0416666666665 | 247.54166666667288 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
2 | 35 | 70 | 105 | 0 | 0 | 4 | 105 | 54 | 0.9500000000043656 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.7 | 6080.000000000014 | 41.4 | 3100.5 | -1680.0000000000064 | 1785.7631578947303 | 1060.5 | 10.1 | 87.13108720944037 | 1844.85 | 2405.2631578947367 | 20.913157894730375 | 80 |  | 12.274305555555555 | 1060.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
3 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.05 | 6920 | 41.4 | 3100.5 | 839.9999999999864 | 1476.9999999999864 | 637 | 9.8 | 89.05093547526026 | 1283.5 | 0 | 193.49999999998636 | 0 |  | 7.372685185185185 | 637 | 2020 | 1 | 2020_01_Asomata_english.xlsx
4 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.2 | 7280.000000000014 | 41.38 | 3077.1 | 360.00000000001364 | 1016.5000000000136 | 656.5 | 10.1 | 86.09872835624795 | 868.25 | 0 | 148.25000000001364 | 0 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
5 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84 | 6800.000000000007 | 41.34 | 3030.3 | -480.00000000000637 | 738.9999999999936 | 656.5 | 10.1 | 86.50872230080151 | 671.6 | 562.5 | 127.39999999999361 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
6 | 0 | 200 | 200 | 0 | 0 | 4 | 200 | 40 | 0 | 4.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 83.7 | 6080.000000000014 | 41.65 | 3393 | -719.9999999999936 | 1300.0000000000064 | 2020 | 10.1 | 87.13108720944037 | 1299.4 | 0 | 60.6000000000065 | 60 |  | 23.37962962962963 | 2020 | 2020 | 1 | 2020_01_Asomata_english.xlsx
7 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 83.9 | 6560.00000000002 | 41.5 | 3217.5 | 480.00000000000637 | 1136.5000000000064 | 656.5 | 10.1 | 86.71518703182966 | 934.4 | 0 | 262.1000000000064 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
8 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 40 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.8 | 8720 | 41.59 | 3322.8 | 2159.99999999998 | 3544.530612244878 | 808 | 10.1 | 84.89173683723513 | 3276.7 | 576.530612244898 | 267.830612244878 | 0 |  | 9.351851851851851 | 808 | 2020 | 1 | 2020_01_Asomata_english.xlsx
9 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85.05 | 9320 | 41.7 | 3451.5 | 600 | 1408 | 808 | 10.1 | 84.3987534641966 | 1296 | 0 | 172 | 60 |  | 9.351851851851851 | 808 | 2020 | 1 | 2020_01_Asomata_english.xlsx
10 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85.1 | 9439.999999999993 | 41.88 | 3662.1 | 119.99999999999272 | 1028.9999999999927 | 909 | 10.1 | 84.30084307734718 | 883.3 | 0 | 205.69999999999277 | 60 |  | 10.520833333333334 | 909 | 2020 | 1 | 2020_01_Asomata_english.xlsx
11 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 35 | 3.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85 | 9200.000000000007 | 41.8 | 3568.5 | -239.99999999998545 | 1118.0000000000146 | 1358 | 9.7 | 87.9812994485735 | 921.1 | 0 | 196.90000000001453 | 0 |  | 15.717592592592593 | 1358 | 2020 | 1 | 2020_01_Asomata_english.xlsx
12 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85.1 | 9439.999999999993 | 41.65 | 3393 | 239.99999999998545 | 939.9999999999854 | 700 | 10 | 85.14385150812066 | 862.5 | 0 | 77.49999999998545 | 0 |  | 8.101851851851851 | 700 | 2020 | 1 | 2020_01_Asomata_english.xlsx
13 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 40 | 0 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 13 | 85 | 9200.000000000007 | 41.85 | 3627 | -239.99999999998545 | 1060.0000000000146 | 1300 | 10 | 85.34186046511628 | 928.65 | 0 | 131.35000000001457 | 0 |  | 15.046296296296296 | 1300 | 2020 | 1 | 2020_01_Asomata_english.xlsx
14 | 145 | 65 | 210 | 0 | 0 | 4 | 210 | 55 | 3.099999999998545 | 1.6999999999970896 | 0 | 0 | 4.25 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ Δ/Κ Ρ15 | 14 | 84.55 | 8120 | 41.66 | 3404.7 | -1080.0000000000073 | 2180.8963730569876 | 2121 | 10.1 | 85.39051319938106 | 2065.9 | 1139.896373056995 | 114.99637305698752 | 0 |  | 24.54861111111111 | 2121 | 2020 | 1 | 2020_01_Asomata_english.xlsx
15 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.65 | 8360.00000000002 | 41.61 | 3346.2 | 240.00000000002 | 2168.2948717948916 | 656.5 | 10.1 | 85.19030097617029 | 2085 | 1271.7948717948716 | 143.2948717948916 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
16 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 40 | 0 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.5 | 8000.000000000007 | 41.65 | 3393 | -360.00000000001273 | 818.5714285714158 | 750 | 10 | 86.34588235294117 | 747.45 | 428.57142857142856 | 71.12142857141589 | 0 |  | 8.680555555555555 | 750 | 2020 | 1 | 2020_01_Asomata_english.xlsx
17 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.3 | 7520 | 41.63 | 3369.6 | -480.0000000000073 | 1176.4999999999927 | 656.5 | 10.1 | 85.89518526320718 | 1146.1 | 1000 | 90.39999999999281 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
18 | 0 | 115 | 115 | 0 | 0 | 4 | 115 | 54 | 0 | 2.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.3 | 7520 | 41.57 | 3299.4 | 0 | 2920.8333333333335 | 1150 | 10 | 86.75413711583924 | 2725.55 | 1770.8333333333335 | 195.28333333333376 | 0 |  | 13.310185185185185 | 1150 | 2020 | 1 | 2020_01_Asomata_english.xlsx
19 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 2.8 | 0 | 1 | 0 | ΑΠΟΚΑΤΑΣΤΑΣΗ ΒΛΑΒΗΣ Απ/Ζ 16 & 26 | 19 | 84.7 | 8480.000000000015 | 41.56 | 3287.7 | 960.0000000000146 | 1736.2916666666813 | 656.5 | 10.1 | 85.09054652537853 | 1702.5 | 119.79166666666666 | 33.791666666681294 | 0 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
20 | 0 | 170 | 170 | 0 | 0 | 4 | 170 | 35 | 0 | 4.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.9 | 8960.00000000002 | 41.52 | 3240.9 | 480.00000000000546 | 2940.638297872346 | 1700 | 10 | 85.54079254079252 | 2759.4 | 760.6382978723404 | 181.2382978723458 | 0 |  | 19.675925925925927 | 1700 | 2020 | 1 | 2020_01_Asomata_english.xlsx
21 | 165 | 0 | 165 | 0 | 0 | 5 | 165 | 35 | 4.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.7 | 3451.5 | -1440.00000000002 | 1907.4358974358775 | 1650 | 10 | 86.75413711583924 | 1800 | 1697.4358974358975 | 107.43589743587745 | 0 |  | 19.09722222222222 | 1650 | 2020 | 1 | 2020_01_Asomata_english.xlsx
22 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.25 | 7400.000000000007 | 41.6 | 3334.5 | -119.99999999999272 | 1278.3829787234115 | 792 | 9.9 | 87.73414619568464 | 1191.4 | 606.3829787234042 | 86.9829787234114 | 0 |  | 9.166666666666666 | 792 | 2020 | 1 | 2020_01_Asomata_english.xlsx
23 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.4 | 7760.00000000002 | 41.78 | 3545.1 | 360.00000000001273 | 1110.0000000000127 | 750 | 10 | 86.54952830188678 | 996.6 | 0 | 113.40000000001271 | 0 |  | 8.680555555555555 | 750 | 2020 | 1 | 2020_01_Asomata_english.xlsx
24 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 36 | 0 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.55 | 8120 | 41.68 | 3428.1 | 359.99999999998 | 1209.99999999998 | 850 | 10 | 86.24441833137486 | 1125 | 0 | 84.99999999997999 | 0 |  | 9.837962962962964 | 850 | 2020 | 1 | 2020_01_Asomata_english.xlsx
25 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.72 | 8528 | 41.76 | 3521.7 | 408.00000000000364 | 1150.5 | 742.5 | 9.9 | 86.7689062913782 | 969.4 | 0 | 181.10000000000355 | 0 |  | 8.59375 | 742.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
26 | 0 | 60 | 60 | 0 | 0 | 3 | 60 | 40 | 0 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.8 | 8720 | 41.7 | 3451.5 | 191.99999999999636 | 797.9999999999964 | 606 | 10.1 | 84.89173683723513 | 781.1 | 0 | 76.89999999999634 | 60 |  | 7.013888888888889 | 606 | 2020 | 1 | 2020_01_Asomata_english.xlsx
27 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 55 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.9 | 8960.00000000002 | 41.14 | 2796.3 | 240.00000000002 | 2943.7340425532116 | 1666.5 | 10.1 | 84.6938540007847 | 2762.25 | 1037.2340425531916 | 241.48404255321157 | 60 |  | 19.288194444444443 | 1666.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
28 | 0 | 110 | 110 | 0 | 0 | 4 | 110 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84 | 6800.000000000007 | 41.45 | 3159 | -2160.0000000000127 | 1655.7360406091243 | 1100 | 10 | 87.37380952380953 | 1422.95 | 2715.736040609137 | 232.78604060912426 | 0 |  | 12.731481481481481 | 1100 | 2020 | 1 | 2020_01_Asomata_english.xlsx
29 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.2 | 7280.000000000014 | 41.65 | 3393 | 480.00000000000637 | 2719.9923857868084 | 940.5 | 9.9 | 87.83809660586911 | 2715.6 | 1299.492385786802 | 34.39238578680852 | 30 |  | 10.885416666666666 | 940.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
30 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.285 | 7484 | 41.65 | 3393 | 203.99999999998454 | 1833.9042553191334 | 656.5 | 10.1 | 85.92565535375816 | 1759.3 | 973.4042553191489 | 134.60425531913347 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 1 | 2020_01_Asomata_english.xlsx
31 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.245 | 7388.000000000018 | 41.78 | 3545.1 | -95.99999999997999 | 854.00000000002 | 950 | 10 | 86.86708486211386 | 540.2 | 0 | 313.8000000000201 | 0 |  | 10.99537037037037 | 950 | 2020 | 1 | 2020_01_Asomata_english.xlsx
1 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.58 | 8190 | 41.85 | 3627 | 801.9999999999818 | 1544.4999999999818 | 742.5 | 9.9 | 87.05419626039637 | 1430.8 | 0 | 113.69999999998186 | 0 |  | 8.59375 | 742.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
2 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.73 | 8552.000000000016 | 41.82 | 3591.9 | 362.00000000001637 | 1531.5416666666829 | 643.5 | 9.9 | 86.74859997116022 | 1401.6 | 526.0416666666666 | 129.94166666668298 | 0 |  | 7.447916666666667 | 643.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
3 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.9 | 8960.00000000002 | 41.9 | 3685.5 | 408.00000000000364 | 1200 | 792 | 9.9 | 86.40484095029548 | 1110 | 0 | 90.00000000000364 | 0 |  | 9.166666666666666 | 792 | 2020 | 2 | 2020_02_Asomata_english.xlsx
4 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.9 | 8960.00000000002 | 41.2 | 2866.5 | 0 | 757.5 | 757.5 | 10.1 | 84.6938540007847 | 754.8 | 0 | 62.69999999999993 | 60 |  | 8.76736111111111 | 757.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
5 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 35 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.6 | 8239.999999999993 | 41.36 | 3053.7 | -720.0000000000273 | 3618.958333333306 | 990 | 9.9 | 87.01332574572012 | 3358 | 3348.9583333333335 | 260.9583333333062 | 0 |  | 11.458333333333334 | 990 | 2020 | 2 | 2020_02_Asomata_english.xlsx
6 | 0 | 105 | 105 | 0 | 0 | 4 | 105 | 35 | 0 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.6 | 8239.999999999993 | 41.62 | 3357.9 | 0 | 1050 | 1050 | 10 | 86.14319248826293 | 940.8 | 0 | 109.2 | 0 |  | 12.152777777777779 | 1050 | 2020 | 2 | 2020_02_Asomata_english.xlsx
7 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.6499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.85 | 8839.999999999993 | 41.6 | 3334.5 | 600 | 1250 | 650 | 10 | 85.64060676779464 | 1036.35 | 0 | 213.65 | 0 |  | 7.523148148148148 | 650 | 2020 | 2 | 2020_02_Asomata_english.xlsx
8 | 0 | 185 | 185 | 0 | 0 | 5 | 185 | 36 | 0 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.8 | 8720 | 41.68 | 3428.1 | -119.99999999999272 | 1748.5000000000073 | 1868.5 | 10.1 | 84.89173683723513 | 1679 | 0 | 129.50000000000728 | 60 |  | 21.62615740740741 | 1868.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
9 | 135 | 0 | 135 | 0 | 0 | 5 | 135 | 36 | 3.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.8 | 8720 | 41.7 | 3451.5 | 0 | 1363.5 | 1363.5 | 10.1 | 84.89173683723513 | 1241 | 0 | 182.5 | 60 |  | 15.78125 | 1363.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
10 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 35 | 0 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.55 | 8120 | 41.15 | 2808 | -600 | 814 | 1414 | 10.1 | 85.39051319938106 | 824.9 | 0 | 49.1 | 60 |  | 16.36574074074074 | 1414 | 2020 | 2 | 2020_02_Asomata_english.xlsx
11 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 35 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.5 | 8000.000000000007 | 41.81 | 3580.2 | -119.99999999999272 | 2398.9119170984527 | 1550 | 10 | 86.34588235294117 | 2131.5 | 968.9119170984455 | 267.4119170984527 | 0 |  | 17.939814814814813 | 1550 | 2020 | 2 | 2020_02_Asomata_english.xlsx
12 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 55 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84 | 6800.000000000007 | 41.15 | 2808 | -1200 | 1492.3118279569892 | 945 | 10.5 | 83.21315192743764 | 1512 | 1747.3118279569892 | 40.31182795698919 | 60 |  | 10.9375 | 945 | 2020 | 2 | 2020_02_Asomata_english.xlsx
13 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.2 | 7280.000000000014 | 41.19 | 2854.8 | 480.00000000000637 | 1490.2564102564165 | 1000 | 10 | 86.95971563981043 | 1277.5 | 10.256410256410255 | 212.75641025641653 | 0 |  | 11.574074074074074 | 1000 | 2020 | 2 | 2020_02_Asomata_english.xlsx
14 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 55 | 0 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.2 | 7280.000000000014 | 41.81 | 3580.2 | 0 | 6015.5675675675675 | 4848 | 10.1 | 86.09872835624795 | 5810 | 1167.5675675675675 | 265.5675675675675 | 60 |  | 56.111111111111114 | 4848 | 2020 | 2 | 2020_02_Asomata_english.xlsx
15 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.85 | 8839.999999999993 | 41.15 | 2808 | 1559.999999999979 | 4456.153846153826 | 650 | 10 | 85.64060676779464 | 4170 | 2246.153846153846 | 286.1538461538257 | 0 |  | 7.523148148148148 | 650 | 2020 | 2 | 2020_02_Asomata_english.xlsx
16 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 85.3 | 9920 | 41 | 2632.5 | 1080.0000000000073 | 5009.375000000007 | 757.5 | 10.1 | 83.91146273980748 | 4964 | 3171.875 | 75.37500000000728 | 30 |  | 8.76736111111111 | 757.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 54 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480.000000000015 | 40.9 | 2515.5 | -1439.9999999999854 | 5192.97872340427 | 750 | 10 | 85.94145199063232 | 5066.2 | 5882.978723404255 | 126.77872340426984 | 0 |  | 8.680555555555555 | 750 | 2020 | 2 | 2020_02_Asomata_english.xlsx
18 | 65 | 100 | 165 | 0 | 0 | 4 | 165 | 65 | 1.9000000000014552 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.5 | 8000.000000000007 | 41.28 | 2960.1 | -480.0000000000073 | 1186.4999999999927 | 1666.5 | 10.1 | 85.49097262667443 | 1071 | 0 | 175.49999999999272 | 60 |  | 19.288194444444443 | 1666.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
19 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.8 | 8720 | 41.23 | 2901.6 | 719.9999999999927 | 1679.4999999999927 | 959.5 | 10.1 | 84.89173683723513 | 1727.25 | 0 | 12.249999999992724 | 60 |  | 11.105324074074074 | 959.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
20 | 0 | 135 | 135 | 0 | 0 | 3 | 135 | 55 | 0 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.85 | 8839.999999999993 | 41.39 | 3088.8 | 119.99999999999272 | 1483.4999999999927 | 1363.5 | 10.1 | 84.79267996811352 | 1334.8 | 0 | 208.69999999999277 | 60 |  | 15.78125 | 1363.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
21 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 35 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.5 | 8000.000000000007 | 41.67 | 3416.4 | -839.9999999999854 | 1560.861702127674 | 1161.5 | 10.1 | 85.49097262667443 | 1562.2 | 1239.3617021276596 | 58.66170212767406 | 60 |  | 13.443287037037036 | 1161.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
22 | 50 | 115 | 165 | 0 | 0 | 5 | 165 | 55 | 1.1500000000014552 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.6 | 8239.999999999993 | 41.1 | 2749.5 | 239.99999999998545 | 1906.4999999999854 | 1666.5 | 10.1 | 85.29028959233953 | 1832.3 | 0 | 74.1999999999855 | 0 |  | 19.288194444444443 | 1666.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
23 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 55 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.6 | 8239.999999999993 | 41.7 | 3451.5 | 0 | 2011.851063829787 | 1581 | 10.2 | 84.45411028261071 | 2051.3 | 430.8510638297872 | 20.55106382978738 | 60 |  | 18.29861111111111 | 1581 | 2020 | 2 | 2020_02_Asomata_english.xlsx
24 | 80 | 105 | 185 | 0 | 0 | 3 | 185 | 35 | 2.1499999999941792 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.55 | 8120 | 41.64 | 3381.3 | -119.99999999999272 | 2386.797872340433 | 1868.5 | 10.1 | 85.39051319938106 | 2248.4 | 638.2978723404256 | 198.39787234043297 | 60 |  | 21.62615740740741 | 1868.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
25 | 180 | 105 | 285 | 0 | 0 | 4 | 285 | 70 | 5.05000000000291 | 2.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 85 | 9200.000000000007 | 41.95 | 3744 | 1080.0000000000073 | 7255.935897435905 | 2878.5 | 10.1 | 84.49689154962007 | 7241.6 | 3297.4358974358975 | 34.33589743590528 | 20 |  | 33.31597222222222 | 2878.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
26 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83 | 4400 | 41.17 | 2831.4 | -4800.000000000007 | 2852.013513513506 | 738.5 | 10.55 | 84.8387469656687 | 2905 | 6913.513513513513 | 27.01351351350604 | 80 |  | 8.547453703703704 | 738.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
27 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 55 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.97 | 6728 | 40.96 | 2585.7 | 2328 | 5422.2875647668425 | 757.5 | 10.1 | 86.57055841395433 | 5183 | 2336.7875647668393 | 239.28756476684248 | 0 |  | 8.76736111111111 | 757.5 | 2020 | 2 | 2020_02_Asomata_english.xlsx
28 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.27 | 7448 | 41 | 2632.5 | 719.9999999999936 | 1664.9999999999936 | 945 | 10.5 | 82.68162718127232 | 1711.2 | 0 | 53.79999999999359 | 100 |  | 10.9375 | 945 | 2020 | 2 | 2020_02_Asomata_english.xlsx
29 | 240 | 0 | 240 | 0 | 0 | 4 | 240 | 55 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.3 | 7520 | 41.73 | 3486.6 | 72.00000000000273 | 3027.914893617024 | 2424 | 10.1 | 85.89518526320718 | 2916 | 531.9148936170212 | 171.91489361702406 | 60 |  | 28.055555555555557 | 2424 | 2020 | 2 | 2020_02_Asomata_english.xlsx
1 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 55 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.65 | 8360.00000000002 | 41.8 | 3568.5 | 840.00000000002 | 1850.00000000002 | 1010 | 10.1 | 85.19030097617029 | 1868.8 | 0 | 41.200000000020054 | 60 |  | 11.689814814814815 | 1010 | 2020 | 3 | 2020_03_Asomata_english.xlsx
2 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.85 | 6439.999999999993 | 41.83 | 3603.6 | -1920.0000000000273 | 2476.0135135134865 | 682.5 | 10.5 | 83.51140695226718 | 2408 | 3713.5135135135138 | 168.0135135134865 | 100 |  | 7.899305555555555 | 682.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
3 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84 | 6800.000000000007 | 41.86 | 3638.7 | 360.00000000001455 | 5037.776595744695 | 656.5 | 10.1 | 86.50872230080151 | 5168.4 | 4021.276595744681 | 19.376595744695805 | 150 |  | 7.59837962962963 | 656.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
4 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 55 | 0 | 4.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.25 | 7400.000000000007 | 41.78 | 3545.1 | 600 | 2923 | 2323 | 10.1 | 85.99683637002754 | 2863 | 0 | 120 | 60 |  | 26.886574074074073 | 2323 | 2020 | 3 | 2020_03_Asomata_english.xlsx
5 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 54 | 1.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.9 | 8960.00000000002 | 41.67 | 3416.4 | 1560.0000000000127 | 2260.0000000000127 | 700 | 10 | 85.54079254079252 | 2057.2 | 0 | 202.80000000001246 | 0 |  | 8.101851851851851 | 700 | 2020 | 3 | 2020_03_Asomata_english.xlsx
6 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.9 | 8960.00000000002 | 41.67 | 3416.4 | 0 | 656.5 | 656.5 | 10.1 | 84.6938540007847 | 617.4 | 0 | 99.1 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
7 | 85 | 35 | 120 | 0 | 0 | 4 | 120 | 35 | 2.3000000000029104 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.6 | 8239.999999999993 | 41.69 | 3439.8 | -720.0000000000273 | 3029.2340425531643 | 1212 | 10.1 | 85.29028959233953 | 3000.3 | 2537.2340425531916 | 88.93404255316455 | 60 |  | 14.027777777777779 | 1212 | 2020 | 3 | 2020_03_Asomata_english.xlsx
8 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.1 | 7039.999999999993 | 41.54 | 3264.3 | -1200 | 5924.521276595745 | 757.5 | 10.1 | 86.3032383998495 | 5858 | 6367.021276595745 | 126.5212765957449 | 60 |  | 8.76736111111111 | 757.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
9 | 175 | 45 | 220 | 0 | 0 | 4 | 220 | 70 | 4.5 | 2.099999999998545 | 0 | 8.25 | 0 | 0 | 0 | 8.25 | 0 | 0 | 2 | 1 | ΣΥΝΤΗΡΗΣΗ Δ/Κ Ρ10 | 9 | 84.65 | 8360.00000000002 | 41.6 | 3334.5 | 1320.0000000000273 | 4142.000000000027 | 2222 | 10.1 | 85.19030097617029 | 3850 | 600 | 292.0000000000273 | 0 |  | 25.71759259259259 | 2222 | 2020 | 3 | 2020_03_Asomata_english.xlsx
10 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 2.2 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ60 Υ/Σ ΡΑΧΙΑΣ | 10 | 84.95 | 9080.000000000015 | 41.32 | 3006.9 | 719.9999999999945 | 1413.734042553186 | 656.5 | 10.1 | 84.59525812883966 | 1379.7 | 37.234042553191486 | 34.034042553186055 | 0 |  | 7.59837962962963 | 656.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
11 | 155 | 20 | 175 | 0 | 0 | 4 | 175 | 55 | 3.099999999998545 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.9 | 8960.00000000002 | 42 | 3802.5 | -119.99999999999454 | 1647.5000000000055 | 1767.5 | 10.1 | 84.6938540007847 | 1659 | 0 | 48.50000000000546 | 60 |  | 20.457175925925927 | 1767.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
12 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.76 | 8624.000000000018 | 41.05 | 2691 | -336.0000000000018 | 980.0744680851045 | 656.5 | 10.1 | 84.97114912613806 | 980 | 659.5744680851063 | 60.07446808510451 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
13 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 85 | 9200.000000000007 | 40.85 | 2457 | 575.9999999999891 | 1700.921052631568 | 656.5 | 10.1 | 84.49689154962007 | 1558.2 | 468.42105263157896 | 142.72105263156823 | 0 |  | 7.59837962962963 | 656.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
14 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 36 | 0 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 85 | 9200.000000000007 | 41.3 | 2983.5 | 0 | 1313 | 1313 | 10.1 | 84.49689154962007 | 1219.1 | 0 | 93.90000000000009 | 0 |  | 15.19675925925926 | 1313 | 2020 | 3 | 2020_03_Asomata_english.xlsx
15 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 55 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.4 | 10160 | 41.3 | 2983.5 | 960.0000000000127 | 4608.798429319384 | 2575.5 | 10.1 | 83.71811835561435 | 4518.7 | 1073.2984293193717 | 90.0984293193842 | 0 |  | 29.80902777777778 | 2575.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 36 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83 | 4400 | 41.32 | 3006.9 | -5760.00000000002 | 5526.787234042533 | 707 | 10.1 | 88.61869113740643 | 5436 | 10579.787234042553 | 150.78723404253287 | 60 |  | 8.18287037037037 | 707 | 2020 | 3 | 2020_03_Asomata_english.xlsx
17 | 285 | 0 | 285 | 0 | 0 | 4 | 285 | 55 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.7 | 8480.000000000015 | 41.68 | 3428.1 | 4080.0000000000146 | 6987.000000000015 | 2907 | 10.2 | 84.25632548101207 | 6967.25 | 0 | 79.75000000001455 | 60 |  | 33.645833333333336 | 2907 | 2020 | 3 | 2020_03_Asomata_english.xlsx
18 | 0 | 125 | 125 | 0 | 0 | 3 | 125 | 55 | 0 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 83.85 | 6439.999999999993 | 41.76 | 3521.7 | -2040.0000000000218 | 1296.9680851063613 | 1262.5 | 10.1 | 86.81878940582232 | 1320.6 | 2074.468085106383 | 36.36808510636138 | 60 |  | 14.612268518518519 | 1262.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.9 | 6560.00000000002 | 41.65 | 3393 | 120.00000000002728 | 3524.916666666694 | 707 | 10.1 | 86.71518703182966 | 3379.9 | 2697.9166666666665 | 205.01666666669416 | 60 |  | 8.18287037037037 | 707 | 2020 | 3 | 2020_03_Asomata_english.xlsx
20 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.1 | 7039.999999999993 | 41.72 | 3474.9 | 479.9999999999727 | 1186.9999999999727 | 707 | 10.1 | 86.3032383998495 | 1173 | 0 | 73.99999999997272 | 60 |  | 8.18287037037037 | 707 | 2020 | 3 | 2020_03_Asomata_english.xlsx
21 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 83.65 | 5960.00000000002 | 41.79 | 3556.8 | -1079.9999999999727 | 2006.6791443850539 | 707 | 10.1 | 87.23568635374941 | 2044.5 | 2379.6791443850266 | 22.17914438505386 | 60 |  | 8.18287037037037 | 707 | 2020 | 3 | 2020_03_Asomata_english.xlsx
22 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 55 | 0 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.45 | 7880.000000000014 | 41.05 | 2691 | 1919.9999999999936 | 2828.9999999999936 | 909 | 10.1 | 85.5916687075068 | 2817.8 | 0 | 71.1999999999939 | 60 |  | 10.520833333333334 | 909 | 2020 | 3 | 2020_03_Asomata_english.xlsx
23 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 55 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.15 | 7160.00000000002 | 41.05 | 2691 | -719.9999999999936 | 1808.6397849462428 | 1969.5 | 10.1 | 86.20086207909047 | 1792 | 559.1397849462365 | 76.6397849462428 | 60 |  | 22.79513888888889 | 1969.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
24 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 40 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.35 | 10040 | 41 | 2632.5 | 2879.9999999999727 | 5579.191709844532 | 808 | 10.1 | 83.81467904575926 | 5285.2 | 1891.1917098445595 | 293.9917098445321 | 0 |  | 9.351851851851851 | 808 | 2020 | 3 | 2020_03_Asomata_english.xlsx
25 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 36 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.6 | 5839.999999999993 | 40.99 | 2620.8 | -4200 | 6107.0376344086035 | 656.5 | 10.1 | 87.34053693830923 | 5978 | 9650.537634408603 | 189.03763440860348 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
26 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 36 | 0 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85 | 9200.000000000007 | 40.88 | 2492.1 | 3360.0000000000146 | 8084.921052631593 | 656.5 | 10.1 | 84.49689154962007 | 7935.1 | 4068.4210526315787 | 209.82105263159247 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
27 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 55 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.15 | 7160.00000000002 | 41.01 | 2644.2 | -2039.9999999999873 | 5997.923280423292 | 757.5 | 10.1 | 86.20086207909047 | 5929 | 7280.42328042328 | 128.92328042329245 | 60 |  | 8.76736111111111 | 757.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 55 | 0 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.4 | 7760.00000000002 | 41.05 | 2691 | 600 | 1307 | 707 | 10.1 | 85.69260227909582 | 1253 | 0 | 114 | 60 |  | 8.18287037037037 | 707 | 2020 | 3 | 2020_03_Asomata_english.xlsx
29 | 0 | 145 | 145 | 0 | 0 | 3 | 145 | 55 | 0 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.75 | 8600.000000000007 | 41.65 | 3393 | 839.9999999999873 | 3879.6295336787434 | 1464.5 | 10.1 | 84.9910254183313 | 3700 | 1575.1295336787564 | 179.62953367874343 | 0 |  | 16.95023148148148 | 1464.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
30 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 40 | 0 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.4 | 10160 | 41.49 | 3205.8 | 1560.0000000000127 | 2410.0000000000127 | 850 | 10 | 84.55529953917049 | 2249.9 | 0 | 160.10000000001264 | 0 |  | 9.837962962962964 | 850 | 2020 | 3 | 2020_03_Asomata_english.xlsx
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 83.35 | 5239.999999999993 | 41.48 | 3194.1 | -4920.000000000027 | 3713.844086021478 | 757.5 | 10.1 | 87.86859338896406 | 3712.2 | 7876.344086021505 | 61.644086021477506 | 60 |  | 8.76736111111111 | 757.5 | 2020 | 3 | 2020_03_Asomata_english.xlsx
1 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 55 | 0 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 84.4 | 7760.00000000002 | 41.89 | 3673.8 | 2520.0000000000273 | 3479.5000000000273 | 959.5 | 10.1 | 85.69260227909582 | 2953.99 | 0 | 525.5100000000275 | 0 |  | 11.105324074074074 | 959.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
2 | 5 | 60 | 65 | 0 | 0 | 3 | 65 | 95 | 0.09999999999854481 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.5 | 8000.000000000007 | 41.47 | 3182.4 | 239.99999999998727 | 896.4999999999873 | 656.5 | 10.1 | 85.49097262667443 | 735 | 0 | 221.49999999998727 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
3 | 190 | 0 | 190 | 0 | 0 | 2 | 190 | 35 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.7 | 8480.000000000015 | 41.69 | 3439.8 | 480.0000000000073 | 2399.0000000000073 | 1919 | 10.1 | 85.09054652537853 | 2131.6 | 0 | 327.40000000000737 | 60 |  | 22.21064814814815 | 1919 | 2020 | 4 | 2020_04_Asomata_english.xlsx
4 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 50 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 85.15 | 9560.00000000002 | 41.33 | 3018.6 | 1080.0000000000055 | 3824.8421052631634 | 808 | 10.1 | 84.20315959753565 | 3372.6 | 1936.842105263158 | 512.2421052631635 | 60 |  | 9.351851851851851 | 808 | 2020 | 4 | 2020_04_Asomata_english.xlsx
5 | 215 | 280 | 495 | 0 | 0 | 4 | 495 | 110 | 4.69999999999709 | 6.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.9 | 8960.00000000002 | 41.76 | 3521.7 | -600 | 4488.041666666667 | 4999.5 | 10.1 | 84.6938540007847 | 3585.6 | 88.54166666666667 | 962.4416666666666 | 60 |  | 57.864583333333336 | 4999.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
6 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.6 | 8239.999999999993 | 41.01 | 2644.2 | -720.0000000000273 | 5048.202127659547 | 656.5 | 10.1 | 85.29028959233953 | 4365.4 | 5111.702127659574 | 742.8021276595473 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
7 | 25 | 260 | 285 | 0 | 0 | 4 | 285 | 90 | 0.7000000000043656 | 5.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 7 | 84.65 | 8360.00000000002 | 41.69 | 3439.8 | 120.00000000002728 | 3482.5425531915166 | 2878.5 | 10.1 | 85.19030097617029 | 3233.9 | 484.04255319148933 | 308.6425531915165 | 60 |  | 33.31597222222222 | 2878.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
8 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 40 | 0 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 85.1 | 9439.999999999993 | 40.76 | 2351.7 | 1079.9999999999727 | 2725.8617021276323 | 656.5 | 10.1 | 84.30084307734718 | 2372.5 | 989.3617021276596 | 353.36170212763227 | 0 |  | 7.59837962962963 | 656.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
9 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.6 | 8239.999999999993 | 40.52 | 2070.9000000000055 | -1200 | 1568.0106382978724 | 959.5 | 10.1 | 85.29028959233953 | 1321.3 | 1808.5106382978724 | 306.7106382978725 | 60 |  | 11.105324074074074 | 959.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
10 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 1.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.85 | 8839.999999999993 | 40.05 | 1520.9999999999945 | 600 | 1269.5 | 669.5 | 10.3 | 83.14622016290741 | 1036.6 | 0 | 252.9 | 20 |  | 7.748842592592593 | 669.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
11 | 205 | 0 | 205 | 0 | 0 | 3 | 205 | 55 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 85.05 | 9320 | 40.75 | 2340 | 480.0000000000073 | 4976.031914893624 | 2070.5 | 10.1 | 84.3987534641966 | 4818 | 2425.531914893617 | 178.03191489362416 | 20 |  | 23.96412037037037 | 2070.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
12 | 95 | 130 | 225 | 0 | 0 | 4 | 225 | 108 | 2 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.85 | 8839.999999999993 | 41.3 | 2983.5 | -480.0000000000073 | 2547.819148936163 | 2272.5 | 10.1 | 84.79267996811352 | 2299.5 | 755.3191489361702 | 308.31914893616295 | 60 |  | 26.302083333333332 | 2272.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
13 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 40 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.25 | 7400.000000000007 | 40.74 | 2328.3 | -1439.9999999999854 | 985.3617021276741 | 686 | 9.8 | 88.62939258543653 | 883.3 | 1739.3617021276596 | 162.06170212767415 | 60 |  | 7.939814814814815 | 686 | 2020 | 4 | 2020_04_Asomata_english.xlsx
14 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 40 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.9 | 8960.00000000002 | 40.38 | 1907.1000000000054 | 1560.0000000000127 | 3910.0000000000127 | 850 | 10 | 85.54079254079252 | 3655.6 | 1500 | 254.40000000001237 | 0 |  | 9.837962962962964 | 850 | 2020 | 4 | 2020_04_Asomata_english.xlsx
15 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 55 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.65 | 8360.00000000002 | 41.07 | 2714.4 | -600 | 3469.3494623655915 | 2171.5 | 10.1 | 85.19030097617029 | 3367 | 1897.8494623655913 | 162.34946236559153 | 60 |  | 25.13310185185185 | 2171.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
16 | 0 | 150 | 150 | 0 | 0 | 4 | 150 | 55 | 0 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85 | 9200.000000000007 | 41.12 | 2772.9 | 839.9999999999873 | 3071.0051546391624 | 1447.5 | 9.65 | 88.43716110374744 | 3017 | 783.5051546391752 | 54.005154639162356 | 0 |  | 16.75347222222222 | 1447.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
17 | 135 | 135 | 270 | 0 | 0 | 4 | 270 | 80 | 3.099999999998545 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.7 | 8480.000000000015 | 42.1 | 3919.5 | -719.9999999999927 | 4336.78723404256 | 2727 | 10.1 | 85.09054652537853 | 4151 | 2329.7872340425533 | 185.78723404256016 | 0 |  | 31.5625 | 2727 | 2020 | 4 | 2020_04_Asomata_english.xlsx
18 | 0 | 125 | 125 | 0 | 0 | 3 | 125 | 40 | 0 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.3 | 7520 | 41.88 | 3662.1 | -960.0000000000146 | 2641.159793814418 | 1312.5 | 10.5 | 82.6229877293707 | 2525.8 | 2288.6597938144328 | 115.35979381441848 | 0 |  | 15.190972222222221 | 1312.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
19 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.7 | 6080.000000000014 | 41.62 | 3357.9 | -1439.9999999999864 | 1716.5000000000136 | 656.5 | 10.1 | 87.13108720944037 | 1634.59 | 2500 | 81.91000000001372 | 0 |  | 7.59837962962963 | 656.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
20 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 35 | 0 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.1 | 7039.999999999993 | 41.63 | 3369.6 | 959.9999999999791 | 1919.499999999979 | 959.5 | 10.1 | 86.3032383998495 | 1817.7 | 0 | 161.79999999997904 | 60 |  | 11.105324074074074 | 959.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
21 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.2 | 7280.000000000014 | 41.42 | 3123.9 | 240.00000000002092 | 2123.160621761679 | 650 | 10 | 86.95971563981043 | 1962.45 | 1233.160621761658 | 160.71062176167925 | 0 |  | 7.523148148148148 | 650 | 2020 | 4 | 2020_04_Asomata_english.xlsx
22 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 1.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.3 | 7520 | 41.2 | 2866.5 | 239.99999999998636 | 3675.7499999999864 | 685.75 | 10.55 | 82.23140958847321 | 3528 | 2750 | 147.74999999998636 | 0 |  | 7.936921296296297 | 685.75 | 2020 | 4 | 2020_04_Asomata_english.xlsx
23 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.2 | 7280.000000000014 | 41 | 2632.5 | -239.99999999998636 | 1889.5918367347074 | 650 | 10 | 86.95971563981043 | 1730.1 | 1479.5918367346937 | 159.49183673470748 | 0 |  | 7.523148148148148 | 650 | 2020 | 4 | 2020_04_Asomata_english.xlsx
24 | 0 | 115 | 115 | 0 | 0 | 4 | 115 | 55 | 0 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 85.05 | 9320 | 41.25 | 2925 | 2039.9999999999864 | 5190.861702127646 | 1161.5 | 10.1 | 84.3987534641966 | 5095.4 | 1989.3617021276596 | 155.46170212764628 | 60 |  | 13.443287037037036 | 1161.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
25 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.1 | 7039.999999999993 | 41.24 | 2913.3 | -2280.0000000000073 | 1738.202127659567 | 656.5 | 10.1 | 86.3032383998495 | 1700.9 | 3361.702127659574 | 97.30212765956708 | 60 |  | 7.59837962962963 | 656.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
26 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 40 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 83.4 | 5360.00000000002 | 41.3 | 2983.5 | -1679.9999999999727 | 3993.59139784949 | 808 | 10.1 | 87.76247189936385 | 3909.6 | 4865.591397849463 | 143.9913978494901 | 60 |  | 9.351851851851851 | 808 | 2020 | 4 | 2020_04_Asomata_english.xlsx
27 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.7 | 8480.000000000015 | 41.25 | 2925 | 3119.9999999999945 | 3869.9999999999945 | 750 | 10 | 85.94145199063232 | 3612 | 0 | 257.99999999999454 | 0 |  | 8.680555555555555 | 750 | 2020 | 4 | 2020_04_Asomata_english.xlsx
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 40 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.85 | 8839.999999999993 | 41.2 | 2866.5 | 359.9999999999782 | 1059.9999999999782 | 700 | 10 | 85.64060676779464 | 849.6 | 0 | 210.39999999997815 | 0 |  | 8.101851851851851 | 700 | 2020 | 4 | 2020_04_Asomata_english.xlsx
29 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.2 | 9680.000000000015 | 41.14 | 2796.3 | 840.0000000000218 | 1490.0000000000218 | 650 | 10 | 84.94675925925925 | 1311.2 | 0 | 178.80000000002178 | 0 |  | 7.523148148148148 | 650 | 2020 | 4 | 2020_04_Asomata_english.xlsx
30 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 40 | 0 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.1 | 9439.999999999993 | 41.52 | 3240.9 | -240.00000000002183 | 1022.4999999999782 | 1262.5 | 10.1 | 84.30084307734718 | 1014.7 | 0 | 67.79999999997824 | 60 |  | 14.612268518518519 | 1262.5 | 2020 | 4 | 2020_04_Asomata_english.xlsx
1 | 135 | 0 | 135 | 0 | 0 | 3 | 135 | 40 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.95 | 9080.000000000015 | 41.81 | 3580.2 | -359.9999999999782 | 990.0000000000218 | 1350 | 10 | 85.44121071012806 | 751.9 | 0 | 238.10000000002185 | 0 |  | 15.625 | 1350 | 2020 | 5 | 2020_05_Asomata_english.xlsx
2 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 55 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.1 | 9439.999999999993 | 41.65 | 3393 | 359.9999999999782 | 1369.9999999999782 | 1010 | 10.1 | 84.30084307734718 | 1043.9 | 0 | 326.0999999999783 | 0 |  | 11.689814814814815 | 1010 | 2020 | 5 | 2020_05_Asomata_english.xlsx
3 | 40 | 180 | 220 | 0 | 0 | 3 | 220 | 54 | 1.0999999999985448 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.2 | 7280.000000000014 | 41.46 | 3170.7 | -2159.999999999979 | 3264.127659574489 | 2222 | 10.1 | 86.09872835624795 | 3315.12 | 3202.127659574468 | 9.007659574489026 | 60 |  | 25.71759259259259 | 2222 | 2020 | 5 | 2020_05_Asomata_english.xlsx
4 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.6 | 8239.999999999993 | 41.75 | 3510 | 959.9999999999791 | 2575.999999999979 | 1616 | 10.1 | 85.29028959233953 | 2336 | 0 | 239.99999999997908 | 0 |  | 18.703703703703702 | 1616 | 2020 | 5 | 2020_05_Asomata_english.xlsx
5 | 190 | 0 | 190 | 0 | 0 | 3 | 190 | 55 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.45 | 7880.000000000014 | 41.94 | 3732.3 | -359.9999999999791 | 1635.000000000021 | 1995 | 10.5 | 82.33103370912558 | 1387 | 0 | 248.00000000002092 | 0 |  | 23.09027777777778 | 1995 | 2020 | 5 | 2020_05_Asomata_english.xlsx
6 | 0 | 195 | 195 | 0 | 0 | 3 | 195 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.6 | 8239.999999999993 | 41.1 | 2749.5 | 359.9999999999791 | 2417.249999999979 | 2057.25 | 10.55 | 81.65231515475158 | 2346 | 0 | 131.24999999997908 | 60 |  | 23.81076388888889 | 2057.25 | 2020 | 5 | 2020_05_Asomata_english.xlsx
7 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 40 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.75 | 8600.000000000007 | 40.99 | 2620.8 | 360.00000000001455 | 1882.5000000000146 | 1522.5 | 10.5 | 81.75327206906154 | 1620.6 | 0 | 261.9000000000144 | 0 |  | 17.62152777777778 | 1522.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
8 | 75 | 365 | 440 | 0 | 0 | 3 | 440 | 110 | 1.7999999999956344 | 7.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.4 | 7760.00000000002 | 41.77 | 3533.4 | -839.9999999999873 | 6869.625000000013 | 4444 | 10.1 | 85.69260227909582 | 6825.6 | 3265.625 | 104.02500000001237 | 60 |  | 51.43518518518518 | 4444 | 2020 | 5 | 2020_05_Asomata_english.xlsx
9 | 220 | 5 | 225 | 0 | 0 | 4 | 225 | 55 | 4.30000000000291 | 0.09999999999854481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.5 | 8000.000000000007 | 42.02 | 3825.9 | 239.99999999998727 | 2512.4999999999873 | 2272.5 | 10.1 | 85.49097262667443 | 2350.6 | 0 | 221.89999999998736 | 60 |  | 26.302083333333332 | 2272.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
10 | 0 | 225 | 225 | 0 | 0 | 3 | 225 | 55 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.8 | 8720 | 42.1 | 3919.5 | 719.9999999999927 | 2992.4999999999927 | 2272.5 | 10.1 | 84.89173683723513 | 2844.45 | 0 | 188.0499999999929 | 40 |  | 26.302083333333332 | 2272.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
11 | 305 | 0 | 305 | 0 | 0 | 4 | 305 | 45 | 7.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.65 | 8360.00000000002 | 42.1 | 3919.5 | -359.99999999998 | 2842.50000000002 | 3202.5 | 10.5 | 81.9449561770781 | 2587.5 | 0 | 255.00000000002 | 0 |  | 37.06597222222222 | 3202.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
12 | 0 | 305 | 305 | 0 | 0 | 3 | 305 | 55 | 0 | 6.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.7 | 8480.000000000015 | 41.94 | 3732.3 | 119.99999999999454 | 3322.4999999999945 | 3202.5 | 10.5 | 81.8490018958403 | 3234 | 0 | 88.49999999999454 | 0 |  | 37.06597222222222 | 3202.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
13 | 80 | 235 | 315 | 0 | 0 | 3 | 315 | 54 | 1.5 | 4.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.85 | 8839.999999999993 | 41.5 | 3217.5 | 359.9999999999782 | 3541.499999999978 | 3181.5 | 10.1 | 84.79267996811352 | 3435 | 0 | 106.49999999997817 | 0 |  | 36.822916666666664 | 3181.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
14 | 0 | 310 | 310 | 0 | 0 | 4 | 310 | 45 | 0 | 7.80000000000291 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 |  | 14 | 84.9 | 8960.00000000002 | 41.41 | 3112.2 | 120.00000000002728 | 3290.990000000027 | 3170.99 | 10.229 | 83.62576257776179 | 3047.05 | 0 | 243.94000000002688 | 0 |  | 36.70127314814815 | 3170.99 | 2020 | 5 | 2020_05_Asomata_english.xlsx
15 | 330 | 0 | 330 | 0 | 0 | 3 | 330 | 55 | 7.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85 | 9200.000000000007 | 41.43 | 3135.6 | 239.99999999998727 | 3572.9999999999873 | 3333 | 10.1 | 84.49689154962007 | 3350.7 | 0 | 222.29999999998745 | 0 |  | 38.576388888888886 | 3333 | 2020 | 5 | 2020_05_Asomata_english.xlsx
16 | 0 | 445 | 445 | 0 | 0 | 4 | 445 | 45 | 0 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.9 | 8960.00000000002 | 41.96 | 3755.7 | -239.99999999998727 | 4254.500000000013 | 4494.5 | 10.1 | 84.6938540007847 | 4117.2 | 0 | 197.30000000001291 | 60 |  | 52.019675925925924 | 4494.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
17 | 115 | 350 | 465 | 0 | 0 | 3 | 465 | 110 | 2.6999999999970896 | 7.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 17 | 84.75 | 8600.000000000007 | 41.59 | 3322.8 | -360.00000000001273 | 4336.499999999987 | 4696.5 | 10.1 | 84.9910254183313 | 4234 | 0 | 162.49999999998727 | 60 |  | 54.357638888888886 | 4696.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
18 | 0 | 490 | 490 | 0 | 0 | 4 | 490 | 55 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.7 | 8480.000000000015 | 41.75 | 3510 | -119.99999999999272 | 4829.000000000007 | 4949 | 10.1 | 85.09054652537853 | 4726.3 | 0 | 102.7000000000071 | 0 |  | 57.280092592592595 | 4949 | 2020 | 5 | 2020_05_Asomata_english.xlsx
19 | 475 | 0 | 475 | 0 | 0 | 3 | 475 | 55 | 9.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.7 | 8480.000000000015 | 41.98 | 3779.1 | 0 | 4797.5 | 4797.5 | 10.1 | 85.09054652537853 | 4623.15 | 0 | 174.35 | 0 |  | 55.526620370370374 | 4797.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
20 | 0 | 490 | 490 | 0 | 0 | 4 | 490 | 55 | 0 | 10.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.8 | 8720 | 42 | 3802.5 | 239.99999999998545 | 5188.999999999985 | 4949 | 10.1 | 84.89173683723513 | 4942.1 | 0 | 246.89999999998508 | 0 |  | 57.280092592592595 | 4949 | 2020 | 5 | 2020_05_Asomata_english.xlsx
21 | 450 | 0 | 450 | 0 | 0 | 3 | 450 | 50 | 9.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.9 | 8960.00000000002 | 42.05 | 3861 | 240.00000000002 | 4740.00000000002 | 4500 | 10 | 85.54079254079252 | 4507.25 | 0 | 232.75000000002 | 0 |  | 52.083333333333336 | 4500 | 2020 | 5 | 2020_05_Asomata_english.xlsx
22 | 0 | 455 | 455 | 0 | 0 | 4 | 455 | 55 | 0 | 9.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.8 | 6320 | 42.05 | 3861 | -2640.00000000002 | 4502.010869565198 | 4663.75 | 10.25 | 85.6506010036177 | 4395.3 | 2478.2608695652175 | 166.71086956519775 | 60 |  | 53.97858796296296 | 4663.75 | 2020 | 5 | 2020_05_Asomata_english.xlsx
23 | 445 | 0 | 445 | 0 | 0 | 3 | 445 | 55 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 85 | 9200.000000000007 | 41.8 | 3568.5 | 2880.0000000000073 | 7374.500000000007 | 4494.5 | 10.1 | 84.49689154962007 | 6965 | 0 | 409.5000000000073 | 0 |  | 52.019675925925924 | 4494.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
24 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 55 | 0 | 9.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85.15 | 9560.00000000002 | 41.6 | 3334.5 | 360.00000000001273 | 5208.000000000013 | 4848 | 10.1 | 84.20315959753565 | 4952.8 | 0 | 255.20000000001346 | 0 |  | 56.111111111111114 | 4848 | 2020 | 5 | 2020_05_Asomata_english.xlsx
25 | 170 | 305 | 475 | 0 | 0 | 3 | 475 | 55 | 3.2000000000043656 | 5.899999999994179 | 0 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ Απ/Ζ16 | 25 | 85.1 | 9439.999999999993 | 41.77 | 3533.4 | -120.00000000002728 | 4796.249999999973 | 4916.25 | 10.35 | 82.26459082910209 | 4725 | 0 | 131.24999999997272 | 60 |  | 56.901041666666664 | 4916.25 | 2020 | 5 | 2020_05_Asomata_english.xlsx
26 | 0 | 490 | 490 | 0 | 0 | 4 | 490 | 55 | 0 | 9.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 85.4 | 10160 | 41.94 | 3732.3 | 720.0000000000273 | 5767.000000000027 | 5047 | 10.3 | 82.09252382443736 | 5180 | 0 | 587.0000000000273 | 0 |  | 58.414351851851855 | 5047 | 2020 | 5 | 2020_05_Asomata_english.xlsx
27 | 510 | 50 | 560 | 0 | 0 | 3 | 560 | 70 | 10.89999999999418 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 85.15 | 9560.00000000002 | 42 | 3802.5 | -600 | 5056 | 5656 | 10.1 | 84.20315959753565 | 4854.5 | 0 | 261.5 | 60 |  | 65.46296296296296 | 5656 | 2020 | 5 | 2020_05_Asomata_english.xlsx
28 | 0 | 525 | 525 | 0 | 0 | 3 | 525 | 55 | 0 | 10.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.2 | 9680.000000000015 | 41.81 | 3580.2 | 119.99999999999454 | 5422.4999999999945 | 5302.5 | 10.1 | 84.10570223689035 | 5274.6 | 0 | 147.89999999999418 | 0 |  | 61.37152777777778 | 5302.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
29 | 625 | 0 | 625 | 0 | 0 | 4 | 625 | 55 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85 | 9200.000000000007 | 42 | 3802.5 | -480.0000000000073 | 5832.499999999993 | 6312.5 | 10.1 | 84.49689154962007 | 5593 | 0 | 239.49999999999272 | 0 |  | 73.0613425925926 | 6312.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
30 | 180 | 335 | 515 | 0 | 0 | 3 | 515 | 54 | 3.400000000001455 | 6.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.9 | 8960.00000000002 | 41.52 | 3240.9 | -239.99999999998727 | 4961.500000000013 | 5201.5 | 10.1 | 84.6938540007847 | 4950 | 0 | 71.50000000001273 | 60 |  | 60.2025462962963 | 5201.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
31 | 535 | 0 | 535 | 0 | 0 | 4 | 535 | 55 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.85 | 8839.999999999993 | 42.1 | 3919.5 | -120.00000000002728 | 6501.585106382951 | 5403.5 | 10.1 | 84.79267996811352 | 6249.6 | 1218.0851063829787 | 251.98510638295102 | 0 |  | 62.54050925925926 | 5403.5 | 2020 | 5 | 2020_05_Asomata_english.xlsx
1 | 480 | 0 | 480 | 0 | 0 | 4 | 480 | 54 | 10.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.1 | 9439.999999999993 | 41.92 | 3708.9 | 600 | 6126.756476683938 | 4848 | 10.1 | 84.30084307734718 | 5749.8 | 678.7564766839378 | 376.9564766839376 | 0 |  | 56.111111111111114 | 4848 | 2020 | 6 | 2020_06_Asomata_english.xlsx
2 | 0 | 585 | 585 | 0 | 0 | 3 | 585 | 55 | 0 | 11.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.75 | 8600.000000000007 | 41.92 | 3708.9 | -839.9999999999854 | 5068.500000000015 | 5908.5 | 10.1 | 84.9910254183313 | 5095.4 | 0 | 33.100000000014916 | 60 |  | 68.38541666666667 | 5908.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
3 | 490 | 75 | 565 | 0 | 0 | 3 | 565 | 70 | 10.099999999998545 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.85 | 8839.999999999993 | 41.67 | 3416.4 | 239.99999999998545 | 5946.499999999985 | 5706.5 | 10.1 | 84.79267996811352 | 5565.6 | 0 | 380.8999999999851 | 0 |  | 66.04745370370371 | 5706.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
4 | 0 | 575 | 575 | 0 | 0 | 4 | 575 | 55 | 0 | 11.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.65 | 8360.00000000002 | 42.1 | 3919.5 | -479.9999999999727 | 5327.500000000027 | 5807.5 | 10.1 | 85.19030097617029 | 5234.1 | 0 | 153.40000000002692 | 60 |  | 67.21643518518519 | 5807.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
5 | 510 | 0 | 510 | 0 | 0 | 3 | 510 | 50 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480.000000000015 | 42.1 | 3919.5 | 119.99999999999454 | 5270.9999999999945 | 5151 | 10.1 | 85.09054652537853 | 5115 | 0 | 155.99999999999454 | 0 |  | 59.61805555555556 | 5151 | 2020 | 6 | 2020_06_Asomata_english.xlsx
6 | 0 | 675 | 675 | 0 | 0 | 4 | 675 | 54 | 0 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.6 | 8239.999999999993 | 41.85 | 3627 | -240.00000000002183 | 8659.55128205126 | 6817.5 | 10.1 | 85.29028959233953 | 8369.4 | 2082.0512820512818 | 290.151282051258 | 0 |  | 78.90625 | 6817.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
7 | 520 | 0 | 520 | 0 | 0 | 4 | 520 | 54 | 10.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 83.5 | 5600.000000000007 | 42.07 | 3884.4 | -2639.9999999999854 | 5460.314606741587 | 5252 | 10.1 | 87.55099606346177 | 5188.4 | 2848.3146067415732 | 331.9146067415877 | 60 |  | 60.78703703703704 | 5252 | 2020 | 6 | 2020_06_Asomata_english.xlsx
8 | 30 | 550 | 580 | 0 | 0 | 3 | 580 | 54 | 0.5 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.2 | 7280.000000000014 | 42.02 | 3825.9 | 1680.0000000000064 | 7538.000000000006 | 5858 | 10.1 | 86.09872835624795 | 7540.75 | 0 | 57.25000000000637 | 60 |  | 67.80092592592592 | 5858 | 2020 | 6 | 2020_06_Asomata_english.xlsx
9 | 535 | 0 | 535 | 0 | 0 | 3 | 535 | 54 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 84.1 | 7039.999999999993 | 42.11 | 3931.2 | -240.00000000002092 | 5828.825531914873 | 5478.4 | 10.24 | 85.12331131235156 | 5621 | 590.4255319148937 | 207.82553191487295 | 0 |  | 63.40740740740742 | 5478.4 | 2020 | 6 | 2020_06_Asomata_english.xlsx
10 | 0 | 495 | 495 | 0 | 0 | 4 | 495 | 50 | 0 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 84.75 | 8600.000000000007 | 42.02 | 3825.9 | 1560.0000000000146 | 6717.900000000014 | 5157.9 | 10.42 | 82.38093634598333 | 6351 | 0 | 366.9000000000151 | 0 |  | 59.697916666666664 | 5157.9 | 2020 | 6 | 2020_06_Asomata_english.xlsx
11 | 525 | 0 | 525 | 0 | 0 | 3 | 525 | 50 | 10.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.87 | 8888.000000000018 | 42 | 3802.5 | 288.0000000000109 | 5590.500000000011 | 5302.5 | 10.1 | 84.75312191821001 | 5358.15 | 0 | 232.35000000001128 | 0 |  | 61.37152777777778 | 5302.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
12 | 0 | 520 | 520 | 0 | 0 | 3 | 520 | 54 | 0 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.8 | 8720 | 41.88 | 3662.1 | -168.0000000000182 | 5135.999999999982 | 5304 | 10.2 | 84.05946490745832 | 4909.8 | 0 | 226.19999999998254 | 0 |  | 61.388888888888886 | 5304 | 2020 | 6 | 2020_06_Asomata_english.xlsx
13 | 555 | 0 | 555 | 0 | 0 | 4 | 555 | 55 | 11.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.05 | 9320 | 41.98 | 3779.1 | 600 | 6205.5 | 5605.5 | 10.1 | 84.3987534641966 | 6000.6 | 0 | 204.9 | 0 |  | 64.87847222222223 | 5605.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
14 | 0 | 540 | 540 | 0 | 0 | 3 | 540 | 50 | 0 | 11.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 85.3 | 9920 | 41.95 | 3744 | 600 | 6000 | 5400 | 10 | 84.75057736720554 | 5721.1 | 0 | 278.9 | 0 |  | 62.5 | 5400 | 2020 | 6 | 2020_06_Asomata_english.xlsx
15 | 545 | 170 | 715 | 0 | 0 | 4 | 715 | 100 | 10.900000000001455 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 15 | 84.6 | 8239.999999999993 | 41.81 | 3580.2 | -1680.0000000000073 | 5541.499999999993 | 7221.5 | 10.1 | 85.29028959233953 | 5569.9 | 0 | 11.599999999993088 | 40 |  | 83.58217592592592 | 7221.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
16 | 0 | 590 | 590 | 0 | 0 | 3 | 590 | 55 | 0 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000.000000000007 | 42 | 3802.5 | -239.99999999998545 | 5984.500000000015 | 6224.5 | 10.55 | 81.84443824923333 | 5884.45 | 0 | 100.05000000001382 | 0 |  | 72.04282407407408 | 6224.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
17 | 560 | 0 | 560 | 0 | 0 | 4 | 560 | 50 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.65 | 8360.00000000002 | 42.05 | 3861 | 360.00000000001273 | 6016.000000000013 | 5656 | 10.1 | 85.19030097617029 | 6041.95 | 0 | 34.050000000012005 | 60 |  | 65.46296296296296 | 5656 | 2020 | 6 | 2020_06_Asomata_english.xlsx
18 | 0 | 630 | 630 | 0 | 0 | 3 | 630 | 55 | 0 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.6 | 8239.999999999993 | 41.75 | 3510 | -120.00000000002728 | 6242.999999999973 | 6363 | 10.1 | 85.29028959233953 | 5959.5 | 0 | 283.4999999999727 | 0 |  | 73.64583333333333 | 6363 | 2020 | 6 | 2020_06_Asomata_english.xlsx
19 | 570 | 0 | 570 | 0 | 0 | 4 | 570 | 55 | 11.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 83.9 | 6560.00000000002 | 41.82 | 3591.9 | -1679.9999999999727 | 6034.4468085106655 | 5757 | 10.1 | 86.71518703182966 | 5803.5 | 1957.4468085106384 | 230.9468085106655 | 0 |  | 66.63194444444444 | 5757 | 2020 | 6 | 2020_06_Asomata_english.xlsx
20 | 0 | 600 | 600 | 0 | 0 | 3 | 600 | 55 | 0 | 12.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.9 | 6560.00000000002 | 41.9 | 3685.5 | 0 | 6060 | 6060 | 10.1 | 86.71518703182966 | 6027 | 0 | 63 | 30 |  | 70.13888888888889 | 6060 | 2020 | 6 | 2020_06_Asomata_english.xlsx
21 | 570 | 0 | 570 | 0 | 0 | 4 | 570 | 55 | 11.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 84.15 | 7160.00000000002 | 42.04 | 3849.3 | 600 | 6357 | 5757 | 10.1 | 86.20086207909047 | 6276.4 | 0 | 80.60000000000036 | 0 |  | 66.63194444444444 | 5757 | 2020 | 6 | 2020_06_Asomata_english.xlsx
22 | 0 | 610 | 610 | 0 | 0 | 3 | 610 | 55 | 0 | 12.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.15 | 7160.00000000002 | 42.01 | 3814.2 | 0 | 6161 | 6161 | 10.1 | 86.20086207909047 | 6127.55 | 0 | 93.44999999999982 | 60 |  | 71.30787037037037 | 6161 | 2020 | 6 | 2020_06_Asomata_english.xlsx
23 | 630 | 0 | 630 | 0 | 0 | 4 | 630 | 50 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.3 | 7520 | 42.1 | 3919.5 | 359.99999999998 | 6722.99999999998 | 6363 | 10.1 | 85.89518526320718 | 6504.3 | 0 | 218.69999999998072 | 0 |  | 73.64583333333333 | 6363 | 2020 | 6 | 2020_06_Asomata_english.xlsx
24 | 0 | 595 | 595 | 0 | 0 | 3 | 595 | 55 | 0 | 11.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.58 | 8192 | 41.97 | 3767.4 | 672.0000000000036 | 6681.5 | 6009.5 | 10.1 | 85.33035078989346 | 6482.4 | 0 | 199.100000000004 | 0 |  | 69.55439814814815 | 6009.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
25 | 610 | 0 | 610 | 0 | 0 | 4 | 610 | 50 | 12.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.75 | 8600.000000000007 | 42.08 | 3896.1 | 408.00000000000364 | 6569 | 6161 | 10.1 | 84.9910254183313 | 6349.2 | 0 | 219.8000000000029 | 0 |  | 71.30787037037037 | 6161 | 2020 | 6 | 2020_06_Asomata_english.xlsx
26 | 0 | 550 | 550 | 0 | 0 | 3 | 550 | 50 | 0 | 11.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.95 | 9080.000000000015 | 41.97 | 3767.4 | 480.0000000000073 | 5980.000000000007 | 5500 | 10 | 85.44121071012806 | 5805 | 0 | 175.00000000000728 | 0 |  | 63.657407407407405 | 5500 | 2020 | 6 | 2020_06_Asomata_english.xlsx
27 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 55 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 85.1 | 9439.999999999993 | 41.57 | 3299.4 | 359.9999999999782 | 5809.999999999978 | 5450 | 10 | 85.14385150812066 | 5600.7 | 0 | 209.29999999997835 | 0 |  | 63.0787037037037 | 5450 | 2020 | 6 | 2020_06_Asomata_english.xlsx
28 | 0 | 635 | 635 | 0 | 0 | 4 | 635 | 55 | 0 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85 | 9200.000000000007 | 42.1 | 3919.5 | -239.99999999998545 | 6046.500000000015 | 6286.5 | 9.9 | 86.20389945971341 | 5723.2 | 0 | 323.30000000001473 | 0 |  | 72.76041666666667 | 6286.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
29 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 55 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.1 | 9439.999999999993 | 41.84 | 3615.3 | 239.99999999998545 | 6754.499999999985 | 6514.5 | 10.1 | 84.30084307734718 | 6663.8 | 0 | 90.69999999998436 | 0 |  | 75.39930555555556 | 6514.5 | 2020 | 6 | 2020_06_Asomata_english.xlsx
30 | 120 | 670 | 790 | 0 | 0 | 3 | 790 | 70 | 3.1000000000058208 | 14.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.35 | 7639.999999999993 | 42.1 | 3919.5 | -1800 | 6179 | 7979 | 10.1 | 85.79377418261309 | 5914.3 | 0 | 324.7000000000007 | 60 |  | 92.34953703703704 | 7979 | 2020 | 6 | 2020_06_Asomata_english.xlsx
1 | 685 | 15 | 700 | 0 | 0 | 4 | 700 | 55 | 13 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.25 | 7400.000000000007 | 42 | 3802.5 | -239.99999999998545 | 6830.000000000015 | 7070 | 10.1 | 85.99683637002754 | 6720 | 0 | 170.00000000001455 | 60 |  | 81.82870370370371 | 7070 | 2020 | 7 | 2020_07_Asomata_english.xlsx
2 | 0 | 605 | 605 | 0 | 0 | 3 | 605 | 54 | 0 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.7 | 8480.000000000015 | 41.74 | 3498.3 | 1080.0000000000073 | 7190.500000000007 | 6110.5 | 10.1 | 85.09054652537853 | 7121.4 | 0 | 129.10000000000673 | 60 |  | 70.72337962962963 | 6110.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
3 | 640 | 0 | 640 | 0 | 0 | 3 | 640 | 50 | 13.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.05 | 9320 | 41.76 | 3521.7 | 839.9999999999854 | 7303.999999999985 | 6464 | 10.1 | 84.3987534641966 | 7208.31 | 0 | 95.68999999998505 | 0 |  | 74.81481481481481 | 6464 | 2020 | 7 | 2020_07_Asomata_english.xlsx
4 | 0 | 640 | 640 | 0 | 0 | 4 | 640 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85 | 9200.000000000007 | 41.9 | 3685.5 | -119.99999999999272 | 6344.000000000007 | 6464 | 10.1 | 84.49689154962007 | 6376.32 | 0 | 27.680000000007567 | 60 |  | 74.81481481481481 | 6464 | 2020 | 7 | 2020_07_Asomata_english.xlsx
5 | 590 | 0 | 590 | 0 | 0 | 4 | 590 | 50 | 13.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 5 | 85.1 | 9439.999999999993 | 41.88 | 3662.1 | 239.99999999998545 | 7613.893617021262 | 5959 | 10.1 | 84.30084307734718 | 7364.7 | 1414.8936170212767 | 249.19361702126298 | 0 |  | 68.9699074074074 | 5959 | 2020 | 7 | 2020_07_Asomata_english.xlsx
6 | 10 | 580 | 590 | 0 | 0 | 3 | 590 | 50 | 0.19999999999708962 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85 | 9200.000000000007 | 42.1 | 3919.5 | -239.99999999998545 | 5719.000000000015 | 5959 | 10.1 | 84.49689154962007 | 5225.6 | 0 | 493.4000000000142 | 0 |  | 68.9699074074074 | 5959 | 2020 | 7 | 2020_07_Asomata_english.xlsx
7 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 50 | 8.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.05 | 9320 | 41.13 | 2784.6 | 119.99999999999272 | 4260.999999999993 | 4141 | 10.1 | 84.3987534641966 | 3890.9 | 0 | 430.0999999999931 | 60 |  | 47.92824074074074 | 4141 | 2020 | 7 | 2020_07_Asomata_english.xlsx
8 | 0 | 370 | 370 | 0 | 0 | 4 | 370 | 45 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.15 | 9560.00000000002 | 40.55 | 2106 | 240.00000000002 | 3977.00000000002 | 3737 | 10.1 | 84.20315959753565 | 3869 | 0 | 168.00000000002 | 60 |  | 43.25231481481482 | 3737 | 2020 | 7 | 2020_07_Asomata_english.xlsx
9 | 395 | 0 | 395 | 0 | 0 | 3 | 395 | 45 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.1 | 9439.999999999993 | 40.64 | 2211.3 | -120.00000000002728 | 3869.4999999999727 | 3989.5 | 10.1 | 84.30084307734718 | 3757.5 | 0 | 111.99999999997272 | 0 |  | 46.17476851851852 | 3989.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
10 | 0 | 395 | 395 | 0 | 0 | 4 | 395 | 46 | 0 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.15 | 7160.00000000002 | 40.98 | 2609.1 | -2279.9999999999727 | 4340.904255319176 | 4147.5 | 10.5 | 82.91701971417272 | 4068 | 2473.404255319149 | 272.9042553191757 | 0 |  | 48.00347222222222 | 4147.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
11 | 495 | 0 | 495 | 0 | 0 | 3 | 495 | 50 | 10.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.4 | 7760.00000000002 | 41.72 | 3474.9 | 600 | 5772.75 | 5172.75 | 10.45 | 82.82251512142275 | 5490.8 | 0 | 281.95 | 0 |  | 59.869791666666664 | 5172.75 | 2020 | 7 | 2020_07_Asomata_english.xlsx
12 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 50 | 0 | 9.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.5 | 8000.000000000007 | 42.02 | 3825.9 | 239.99999999998727 | 5279.999999999987 | 5040 | 10.5 | 82.2341736694678 | 5183 | 0 | 96.99999999998727 | 0 |  | 58.333333333333336 | 5040 | 2020 | 7 | 2020_07_Asomata_english.xlsx
13 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 54 | 8.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 82.65 | 3630.0000000000127 | 41.77 | 3533.4 | -4369.9999999999945 | -44.49999999999454 | 4325.5 | 10.55 | 85.56921588173226 | 0 | 0 | 15.500000000005457 | 60 |  | 50.063657407407405 | 4325.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
14 | 0 | 225 | 225 | 0 | 0 | 3 | 225 | 50 | 0 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 81.6 | 1319.9999999999875 | 40.65 | 2223 | -2310.0000000000255 | -37.500000000025466 | 2272.5 | 10.1 | 91.75167516751677 | 0 | 0 | 22.499999999974534 | 60 |  | 26.302083333333332 | 2272.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
15 | 285 | 0 | 285 | 0 | 0 | 4 | 285 | 53 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 82.1 | 2419.9999999999873 | 39.94 | 1392.3 | 1100 | 4092.5 | 2992.5 | 10.5 | 87.15591972449829 | 2688 | 0 | 64.5 | 60 |  | 34.635416666666664 | 2992.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
16 | 135 | 460 | 595 | 0 | 0 | 3 | 595 | 70 | 3.6999999999970896 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.25 | 7400.000000000007 | 40.88 | 2492.1 | 4980.00000000002 | 10989.5 | 6009.5 | 10.1 | 85.99683637002754 | 10600.3 | 0 | 389.20000000002074 | 0 |  | 69.55439814814815 | 6009.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
17 | 515 | 105 | 620 | 0 | 0 | 4 | 620 | 85 | 11.200000000004366 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.3 | 7520 | 41.37 | 3065.4 | 119.99999999999272 | 6381.999999999993 | 6262 | 10.1 | 85.89518526320718 | 6317.6 | 0 | 64.39999999999236 | 0 |  | 72.47685185185185 | 6262 | 2020 | 7 | 2020_07_Asomata_english.xlsx
18 | 10 | 670 | 680 | 0 | 0 | 3 | 680 | 55 | 0.09999999999854481 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.75 | 8600.000000000007 | 41.94 | 3732.3 | 1080.0000000000073 | 7948.000000000007 | 6868 | 10.1 | 84.9910254183313 | 7978.95 | 0 | 29.05000000000655 | 60 |  | 79.49074074074075 | 6868 | 2020 | 7 | 2020_07_Asomata_english.xlsx
19 | 565 | 0 | 565 | 0 | 0 | 4 | 565 | 55 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.8 | 8720 | 41.82 | 3591.9 | 119.99999999999272 | 5826.499999999993 | 5706.5 | 10.1 | 84.89173683723513 | 5768 | 0 | 118.49999999999272 | 60 |  | 66.04745370370371 | 5706.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
20 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 55 | 0 | 12.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.25 | 9800.000000000007 | 41.87 | 3650.4 | 1080.0000000000073 | 7493.500000000007 | 6413.5 | 10.1 | 84.00847021118297 | 7293.3 | 0 | 200.200000000008 | 0 |  | 74.23032407407408 | 6413.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
21 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 13.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.25 | 7400.000000000007 | 42.05 | 3861 | -2400 | 5587.791666666666 | 6868 | 10.1 | 85.99683637002754 | 5563.95 | 1119.7916666666665 | 23.841666666666242 | 0 |  | 79.49074074074075 | 6868 | 2020 | 7 | 2020_07_Asomata_english.xlsx
22 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 55 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.85 | 8839.999999999993 | 41.86 | 3638.7 | 1439.9999999999854 | 8004.999999999985 | 6565 | 10.1 | 84.79267996811352 | 7821.8 | 0 | 183.19999999998527 | 0 |  | 75.98379629629629 | 6565 | 2020 | 7 | 2020_07_Asomata_english.xlsx
23 | 615 | 130 | 745 | 0 | 0 | 4 | 745 | 85 | 13.60000000000582 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.85 | 8839.999999999993 | 41.95 | 3744 | 0 | 7450 | 7450 | 10 | 85.64060676779464 | 7400 | 0 | 109.99999999999909 | 60 |  | 86.22685185185185 | 7450 | 2020 | 7 | 2020_07_Asomata_english.xlsx
24 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 55 | 0 | 12.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85.05 | 9320 | 41.88 | 3662.1 | 480.0000000000073 | 7045.000000000007 | 6565 | 10.1 | 84.3987534641966 | 6995.55 | 0 | 109.4500000000071 | 60 |  | 75.98379629629629 | 6565 | 2020 | 7 | 2020_07_Asomata_english.xlsx
25 | 655 | 0 | 655 | 0 | 0 | 4 | 655 | 55 | 12.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 85.1 | 9439.999999999993 | 42.08 | 3896.1 | 119.99999999999272 | 6735.499999999993 | 6615.5 | 10.1 | 84.30084307734718 | 6560.95 | 0 | 174.5499999999929 | 0 |  | 76.56828703703704 | 6615.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
26 | 0 | 685 | 685 | 0 | 0 | 3 | 685 | 55 | 0 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.9 | 8960.00000000002 | 41.98 | 3779.1 | -479.9999999999727 | 6609.750000000027 | 7089.75 | 10.35 | 82.64810873506525 | 6621.35 | 0 | 48.40000000002692 | 60 |  | 82.05729166666667 | 7089.75 | 2020 | 7 | 2020_07_Asomata_english.xlsx
27 | 590 | 0 | 590 | 0 | 0 | 4 | 590 | 55 | 11.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.95 | 9080.000000000015 | 41.7 | 3451.5 | 119.99999999999454 | 6078.9999999999945 | 5959 | 10.1 | 84.59525812883966 | 5938.8 | 0 | 140.19999999999527 | 0 |  | 68.9699074074074 | 5959 | 2020 | 7 | 2020_07_Asomata_english.xlsx
28 | 0 | 695 | 695 | 0 | 0 | 3 | 695 | 55 | 0 | 13.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.05 | 9320 | 42.08 | 3896.1 | 239.99999999998545 | 7259.499999999985 | 7019.5 | 10.1 | 84.3987534641966 | 7168.74 | 0 | 90.75999999998567 | 0 |  | 81.24421296296296 | 7019.5 | 2020 | 7 | 2020_07_Asomata_english.xlsx
29 | 690 | 0 | 690 | 0 | 0 | 4 | 690 | 55 | 13.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85 | 9200.000000000007 | 42.1 | 3919.5 | -119.99999999999272 | 6849.000000000007 | 6969 | 10.1 | 84.49689154962007 | 6600.7 | 0 | 248.30000000000746 | 0 |  | 80.65972222222223 | 6969 | 2020 | 7 | 2020_07_Asomata_english.xlsx
30 | 0 | 675 | 675 | 0 | 0 | 3 | 675 | 55 | 0 | 12.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.8 | 8720 | 42.1 | 3919.5 | -480.0000000000073 | 6269.999999999993 | 6750 | 10 | 85.74065420560747 | 6092.85 | 0 | 177.14999999999327 | 0 |  | 78.125 | 6750 | 2020 | 7 | 2020_07_Asomata_english.xlsx
31 | 700 | 0 | 700 | 0 | 0 | 4 | 700 | 55 | 13.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.9 | 8960.00000000002 | 42.1 | 3919.5 | 240.00000000002 | 7310.00000000002 | 7070 | 10.1 | 84.6938540007847 | 7112.25 | 0 | 197.75000000002 | 0 |  | 81.82870370370371 | 7070 | 2020 | 7 | 2020_07_Asomata_english.xlsx
1 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 55 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.2 | 9680.000000000015 | 42.06 | 3872.7 | 719.9999999999945 | 7335.4999999999945 | 6615.5 | 10.1 | 84.10570223689035 | 7226.5 | 0 | 138.99999999999454 | 30 |  | 76.56828703703704 | 6615.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
2 | 0 | 635 | 635 | 0 | 0 | 4 | 635 | 55 | 0 | 12.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.25 | 9800.000000000007 | 41.89 | 3673.8 | 119.99999999999272 | 6533.499999999993 | 6413.5 | 10.1 | 84.00847021118297 | 6502.5 | 0 | 30.999999999992724 | 0 |  | 74.23032407407408 | 6413.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
3 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.1 | 9439.999999999993 | 42.1 | 3919.5 | -360.00000000001455 | 6356.499999999985 | 6716.5 | 10.1 | 84.30084307734718 | 6387.5 | 0 | 28.999999999985448 | 60 |  | 77.73726851851852 | 6716.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
4 | 0 | 690 | 690 | 0 | 0 | 4 | 690 | 55 | 0 | 13.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.1 | 9439.999999999993 | 42.03 | 3837.6 | 0 | 6969 | 6969 | 10.1 | 84.30084307734718 | 6874.6 | 0 | 94.39999999999964 | 0 |  | 80.65972222222223 | 6969 | 2020 | 8 | 2020_08_Asomata_english.xlsx
5 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 85.2 | 9680.000000000015 | 42.05 | 3861 | 240.00000000002183 | 6956.500000000022 | 6716.5 | 10.1 | 84.10570223689035 | 6874.6 | 0 | 81.90000000002146 | 0 |  | 77.73726851851852 | 6716.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
6 | 0 | 645 | 645 | 0 | 0 | 4 | 645 | 55 | 0 | 12.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.95 | 9080.000000000015 | 41.95 | 3744 | -600 | 5914.5 | 6514.5 | 10.1 | 84.59525812883966 | 5357.6 | 0 | 556.9 | 0 |  | 75.39930555555556 | 6514.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
7 | 660 | 0 | 660 | 0 | 0 | 4 | 660 | 55 | 12.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.9 | 8960.00000000002 | 42.05 | 3861 | -119.99999999999454 | 6546.0000000000055 | 6666 | 10.1 | 84.6938540007847 | 6195 | 0 | 351.00000000000546 | 0 |  | 77.15277777777777 | 6666 | 2020 | 8 | 2020_08_Asomata_english.xlsx
8 | 105 | 250 | 355 | 0 | 0 | 4 | 355 | 70 | 2.8000000000029104 | 6.350000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.9 | 8960.00000000002 | 41.8 | 3568.5 | 0 | 3585.5 | 3585.5 | 10.1 | 84.6938540007847 | 3367.3 | 0 | 218.2 | 0 |  | 41.498842592592595 | 3585.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
9 | 260 | 85 | 345 | 0 | 0 | 3 | 345 | 70 | 6.94999999999709 | 2.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 83.65 | 5960.00000000002 | 41.78 | 3545.1 | -3000 | 5285.575268817204 | 3484.5 | 10.1 | 87.23568635374941 | 5367.6 | 4801.075268817204 | 17.97526881720387 | 100 |  | 40.329861111111114 | 3484.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
10 | 55 | 415 | 470 | 0 | 0 | 4 | 470 | 109 | 1.1000000000058208 | 9.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.8 | 6320 | 41.97 | 3767.4 | 359.99999999998 | 5106.99999999998 | 4747 | 10.1 | 86.9226396323843 | 5058.9 | 0 | 108.09999999998035 | 60 |  | 54.942129629629626 | 4747 | 2020 | 8 | 2020_08_Asomata_english.xlsx
11 | 380 | 0 | 380 | 0 | 0 | 3 | 380 | 54 | 8.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.6 | 8239.999999999993 | 41.72 | 3474.9 | 1919.9999999999927 | 6194.17021276595 | 3838 | 10.1 | 85.29028959233953 | 6119.8 | 436.17021276595744 | 74.37021276594987 | 0 |  | 44.4212962962963 | 3838 | 2020 | 8 | 2020_08_Asomata_english.xlsx
12 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 55 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.65 | 8360.00000000002 | 41.89 | 3673.8 | 120.00000000002728 | 4362.000000000027 | 4242 | 10.1 | 85.19030097617029 | 4239.05 | 0 | 122.9500000000271 | 0 |  | 49.09722222222222 | 4242 | 2020 | 8 | 2020_08_Asomata_english.xlsx
13 | 340 | 70 | 410 | 0 | 0 | 3 | 410 | 80 | 8.69999999999709 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.55 | 8120 | 41.76 | 3521.7 | -240.00000000002 | 3900.99999999998 | 4141 | 10.1 | 85.39051319938106 | 3951.6 | 0 | 9.399999999979627 | 60 |  | 47.92824074074074 | 4141 | 2020 | 8 | 2020_08_Asomata_english.xlsx
14 | 0 | 455 | 455 | 0 | 0 | 4 | 455 | 40 | 0 | 10.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.55 | 8120 | 41.96 | 3755.7 | 0 | 4595.5 | 4595.5 | 10.1 | 85.39051319938106 | 4591.7 | 0 | 63.80000000000018 | 60 |  | 53.188657407407405 | 4595.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
15 | 440 | 0 | 440 | 0 | 0 | 3 | 440 | 40 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.75 | 8600.000000000007 | 41.93 | 3720.6 | 480.0000000000073 | 4924.000000000007 | 4444 | 10.1 | 84.9910254183313 | 4943.2 | 0 | 40.80000000000655 | 60 |  | 51.43518518518518 | 4444 | 2020 | 8 | 2020_08_Asomata_english.xlsx
16 | 0 | 380 | 380 | 0 | 0 | 4 | 380 | 40 | 0 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.8 | 8720 | 41.07 | 2714.4 | 119.99999999999272 | 3957.9999999999927 | 3838 | 10.1 | 84.89173683723513 | 3959 | 0 | 58.99999999999227 | 60 |  | 44.4212962962963 | 3838 | 2020 | 8 | 2020_08_Asomata_english.xlsx
17 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 55 | 10.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.8 | 8720 | 41.42 | 3123.9 | 0 | 4305 | 4305 | 10.5 | 81.65776591010237 | 4126.8 | 0 | 178.2 | 0 |  | 49.826388888888886 | 4305 | 2020 | 8 | 2020_08_Asomata_english.xlsx
18 | 0 | 480 | 480 | 0 | 0 | 3 | 480 | 45 | 0 | 11.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.5 | 8000.000000000007 | 41.98 | 3779.1 | -719.9999999999927 | 4032.0000000000073 | 4752 | 9.9 | 87.21806298276887 | 3877.5 | 0 | 184.50000000000728 | 30 |  | 55 | 4752 | 2020 | 8 | 2020_08_Asomata_english.xlsx
19 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 45 | 9.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.63 | 8312 | 41.52 | 3240.9 | 311.9999999999891 | 4503.499999999989 | 4191.5 | 10.1 | 85.23026827665174 | 4530 | 0 | 73.49999999998909 | 100 |  | 48.51273148148148 | 4191.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
20 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 45 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.7 | 8480.000000000015 | 42.02 | 3825.9 | 168.0000000000182 | 4612.000000000018 | 4444 | 10.1 | 85.09054652537853 | 4522.5 | 0 | 89.50000000001819 | 0 |  | 51.43518518518518 | 4444 | 2020 | 8 | 2020_08_Asomata_english.xlsx
21 | 485 | 0 | 485 | 0 | 0 | 4 | 485 | 55 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.6 | 8239.999999999993 | 41.82 | 3591.9 | -240.00000000002183 | 4658.499999999978 | 4898.5 | 10.1 | 85.29028959233953 | 4605 | 0 | 93.49999999997817 | 40 |  | 56.695601851851855 | 4898.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
22 | 0 | 400 | 400 | 0 | 0 | 3 | 400 | 40 | 0 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.5 | 8000.000000000007 | 41.89 | 3673.8 | -239.99999999998545 | 3800.0000000000146 | 4040 | 10.1 | 85.49097262667443 | 3772.5 | 0 | 87.50000000001455 | 60 |  | 46.75925925925926 | 4040 | 2020 | 8 | 2020_08_Asomata_english.xlsx
23 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 40 | 9.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.36 | 7664.0000000000055 | 41.88 | 3662.1 | -336.0000000000018 | 4075.042553191487 | 3927 | 10.2 | 84.93260382528838 | 4117.5 | 484.04255319148933 | 57.54255319148706 | 100 |  | 45.451388888888886 | 3927 | 2020 | 8 | 2020_08_Asomata_english.xlsx
24 | 0 | 365 | 365 | 0 | 0 | 4 | 365 | 40 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.47 | 7928 | 41.76 | 3521.7 | 263.9999999999982 | 4060 | 3796 | 10.4 | 83.08353407835395 | 4033 | 0 | 86.99999999999818 | 60 |  | 43.93518518518518 | 3796 | 2020 | 8 | 2020_08_Asomata_english.xlsx
25 | 85 | 480 | 565 | 0 | 0 | 3 | 565 | 95 | 1.6999999999970896 | 10.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.6 | 8239.999999999993 | 41.55 | 3276 | 311.9999999999891 | 6018.499999999989 | 5706.5 | 10.1 | 85.29028959233953 | 5905.7 | 0 | 172.79999999998927 | 60 |  | 66.04745370370371 | 5706.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
26 | 0 | 393 | 393 | 0 | 0 | 4 | 393 | 54 | 0 | 9.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.6 | 8239.999999999993 | 41.66 | 3404.7 | 0 | 3969.3 | 3969.3 | 10.1 | 85.29028959233953 | 3944.2 | 0 | 85.09999999999945 | 60 |  | 45.940972222222214 | 3969.3 | 2020 | 8 | 2020_08_Asomata_english.xlsx
27 | 465 | 32 | 497 | 0 | 0 | 3 | 497 | 75 | 11.099999999998545 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.8 | 8720 | 41.85 | 3627 | 480.0000000000073 | 5499.700000000007 | 5019.7 | 10.1 | 84.89173683723513 | 5321.7 | 0 | 178.00000000000728 | 0 |  | 58.098379629629626 | 5019.7 | 2020 | 8 | 2020_08_Asomata_english.xlsx
28 | 0 | 395 | 395 | 0 | 0 | 4 | 395 | 40 | 0 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.9 | 8960.00000000002 | 41.65 | 3393 | 240.00000000002 | 4229.50000000002 | 3989.5 | 10.1 | 84.6938540007847 | 4102.6 | 0 | 126.90000000002055 | 0 |  | 46.17476851851852 | 3989.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
29 | 390 | 0 | 390 | 0 | 0 | 3 | 390 | 40 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.05 | 9320 | 41.75 | 3510 | 359.99999999998 | 4454.99999999998 | 4095 | 10.5 | 81.18356285603673 | 4270.5 | 0 | 184.49999999998 | 0 |  | 47.395833333333336 | 4095 | 2020 | 8 | 2020_08_Asomata_english.xlsx
30 | 0 | 385 | 385 | 0 | 0 | 4 | 385 | 40 | 0 | 9.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.35 | 10040 | 41.9 | 3685.5 | 719.9999999999927 | 4608.499999999993 | 3888.5 | 10.1 | 83.81467904575926 | 4518.7 | 0 | 89.7999999999929 | 0 |  | 45.00578703703704 | 3888.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
31 | 505 | 320 | 825 | 0 | 0 | 4 | 825 | 80 | 10.75 | 6.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 85.1 | 9439.999999999993 | 42.1 | 3919.5 | -600 | 7732.5 | 8332.5 | 10.1 | 84.30084307734718 | 7645.19 | 0 | 87.30999999999949 | 0 |  | 96.44097222222223 | 8332.5 | 2020 | 8 | 2020_08_Asomata_english.xlsx
1 | 655 | 460 | 1115 | 0 | 0 | 3 | 1115 | 110 | 15.75 | 11.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.57 | 8167.999999999991 | 42 | 3802.5 | -1272 | 10101 | 11373 | 10.2 | 84.51362692128768 | 10130.4 | 0 | 70.59999999999673 | 100 |  | 131.63194444444446 | 11373 | 2020 | 9 | 2020_09_Asomata_english.xlsx
2 | 0 | 685 | 685 | 0 | 0 | 4 | 685 | 55 | 0 | 15.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.3 | 7520 | 41.83 | 3603.6 | -647.9999999999909 | 6202.000000000009 | 6850 | 10 | 86.75413711583924 | 6098.4 | 0 | 103.60000000000855 | 0 |  | 79.2824074074074 | 6850 | 2020 | 9 | 2020_09_Asomata_english.xlsx
3 | 590 | 32 | 622 | 0 | 0 | 3 | 622 | 70 | 13.69999999999709 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 85.05 | 9320 | 42.04 | 3849.3 | 1800 | 8020 | 6220 | 10 | 85.24274099883856 | 7761.6 | 0 | 258.4 | 0 |  | 71.99074074074075 | 6220 | 2020 | 9 | 2020_09_Asomata_english.xlsx
4 | 0 | 378 | 378 | 0 | 0 | 4 | 378 | 40 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.05 | 9320 | 41.35 | 3042 | 0 | 3987.9 | 3987.9 | 10.55 | 80.7988066339702 | 3781.4 | 0 | 206.5 | 0 |  | 46.15625 | 3987.9 | 2020 | 9 | 2020_09_Asomata_english.xlsx
5 | 405 | 0 | 405 | 0 | 0 | 3 | 405 | 40 | 9.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480.000000000015 | 41.55 | 3276 | -839.9999999999854 | 3169.5000000000146 | 4009.5 | 9.9 | 86.80954746528516 | 3075 | 0 | 94.50000000001455 | 0 |  | 46.40625 | 4009.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
6 | 0 | 390 | 390 | 0 | 0 | 4 | 390 | 45 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 84.9 | 8960.00000000002 | 41.84 | 3615.3 | 480.00000000000546 | 4419.0000000000055 | 3939 | 10.1 | 84.6938540007847 | 4270.5 | 0 | 148.50000000000546 | 0 |  | 45.59027777777778 | 3939 | 2020 | 9 | 2020_09_Asomata_english.xlsx
7 | 365 | 0 | 365 | 0 | 0 | 3 | 365 | 55 | 8.099999999998545 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 84.85 | 8839.999999999993 | 41.69 | 3439.8 | -120.00000000002728 | 3566.4999999999727 | 3686.5 | 10.1 | 84.79267996811352 | 3486.1 | 0 | 140.3999999999728 | 60 |  | 42.667824074074076 | 3686.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
8 | 90 | 380 | 470 | 0 | 0 | 3 | 470 | 80 | 2.25 | 9.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.5 | 8000.000000000007 | 41.76 | 3521.7 | -839.9999999999854 | 3907.0000000000146 | 4747 | 10.1 | 85.49097262667443 | 3745 | 0 | 222.00000000001455 | 60 |  | 54.942129629629626 | 4747 | 2020 | 9 | 2020_09_Asomata_english.xlsx
9 | 370 | 0 | 370 | 0 | 0 | 4 | 370 | 55 | 8.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.5 | 8000.000000000007 | 41.77 | 3533.4 | 0 | 3737 | 3737 | 10.1 | 85.49097262667443 | 3679.2 | 0 | 117.8 | 60 |  | 43.25231481481482 | 3737 | 2020 | 9 | 2020_09_Asomata_english.xlsx
10 | 0 | 380 | 380 | 0 | 0 | 3 | 380 | 55 | 0 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 85.25 | 9800.000000000007 | 41.98 | 3779.1 | 1800 | 5638 | 3838 | 10.1 | 84.00847021118297 | 5396 | 0 | 242 | 0 |  | 44.4212962962963 | 3838 | 2020 | 9 | 2020_09_Asomata_english.xlsx
11 | 0 | 410 | 410 | 0 | 0 | 4 | 410 | 55 | 0 | 9.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 85 | 9200.000000000007 | 41.77 | 3533.4 | -600 | 3541 | 4141 | 10.1 | 84.49689154962007 | 3427.2 | 0 | 113.8 | 0 |  | 47.92824074074074 | 4141 | 2020 | 9 | 2020_09_Asomata_english.xlsx
12 | 235 | 120 | 355 | 0 | 0 | 3 | 355 | 54 | 5.75 | 3.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 85.05 | 9320 | 41.88 | 3662.1 | 119.99999999999272 | 3705.4999999999927 | 3585.5 | 10.1 | 84.3987534641966 | 3491.4 | 0 | 214.09999999999263 | 0 |  | 41.498842592592595 | 3585.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
13 | 0 | 330 | 330 | 0 | 0 | 3 | 330 | 54 | 0 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 13 | 85 | 9200.000000000007 | 41.75 | 3510 | -119.99999999999272 | 3213.0000000000073 | 3333 | 10.1 | 84.49689154962007 | 3203.2 | 0 | 69.800000000007 | 60 |  | 38.576388888888886 | 3333 | 2020 | 9 | 2020_09_Asomata_english.xlsx
14 | 0 | 355 | 355 | 0 | 0 | 4 | 355 | 40 | 0 | 9.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 85.1 | 9439.999999999993 | 41.87 | 3650.4 | 239.99999999998545 | 3825.4999999999854 | 3585.5 | 10.1 | 84.30084307734718 | 3752.2 | 0 | 123.29999999998563 | 50 |  | 41.498842592592595 | 3585.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
15 | 0 | 315 | 315 | 0 | 0 | 3 | 315 | 40 | 0 | 7.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 85.2 | 9680.000000000015 | 41.6 | 3334.5 | 240.00000000002183 | 3421.500000000022 | 3181.5 | 10.1 | 84.10570223689035 | 3174 | 0 | 247.50000000002183 | 0 |  | 36.822916666666664 | 3181.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
16 | 440 | 265 | 705 | 0 | 0 | 4 | 705 | 80 | 10.25 | 5.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.85 | 8839.999999999993 | 41.98 | 3779.1 | -840.0000000000218 | 6280.499999999978 | 7120.5 | 10.1 | 84.79267996811352 | 6209 | 0 | 131.49999999997817 | 60 |  | 82.41319444444444 | 7120.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
17 | 505 | 0 | 505 | 0 | 0 | 3 | 505 | 40 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.8 | 8720 | 41.75 | 3510 | -119.99999999999272 | 5081.500000000007 | 5201.5 | 10.3 | 83.24335359767717 | 5016.3 | 0 | 125.2000000000071 | 60 |  | 60.2025462962963 | 5201.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
18 | 260 | 225 | 485 | 0 | 0 | 4 | 485 | 80 | 6.69999999999709 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 85 | 9200.000000000007 | 41.8 | 3568.5 | 480.0000000000073 | 5378.500000000007 | 4898.5 | 10.1 | 84.49689154962007 | 5270.6 | 0 | 167.90000000000782 | 60 |  | 56.695601851851855 | 4898.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
19 | 290 | 0 | 290 | 0 | 0 | 3 | 290 | 40 | 7.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 85.05 | 9320 | 41.53 | 3252.6 | 119.99999999999272 | 3610.4255319148865 | 2900 | 10 | 85.24274099883856 | 3374 | 590.4255319148937 | 236.4255319148865 | 0 |  | 33.56481481481482 | 2900 | 2020 | 9 | 2020_09_Asomata_english.xlsx
20 | 0 | 275 | 275 | 0 | 0 | 4 | 275 | 55 | 0 | 6.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.65 | 8360.00000000002 | 41.36 | 3053.7 | -959.99999999998 | 3308.6702127659773 | 2832.5 | 10.3 | 83.53612037469125 | 3292.3 | 1436.1702127659573 | 116.37021276597761 | 100 |  | 32.78356481481482 | 2832.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
21 | 555 | 80 | 635 | 0 | 0 | 3 | 635 | 108 | 12.25 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.75 | 8600.000000000007 | 41.84 | 3615.3 | 239.99999999998727 | 6653.499999999987 | 6413.5 | 10.1 | 84.9910254183313 | 6496.5 | 0 | 156.99999999998818 | 0 |  | 74.23032407407408 | 6413.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
22 | 200 | 365 | 565 | 0 | 0 | 4 | 565 | 110 | 4.69999999999709 | 8.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 85.05 | 9320 | 42.02 | 3825.9 | 719.9999999999927 | 6426.499999999993 | 5706.5 | 10.1 | 84.3987534641966 | 6380.2 | 0 | 106.2999999999929 | 60 |  | 66.04745370370371 | 5706.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
23 | 625 | 175 | 800 | 0 | 0 | 3 | 800 | 110 | 14.400000000001455 | 4.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480.000000000015 | 41.8 | 3568.5 | -839.9999999999854 | 7240.000000000015 | 8080 | 10.1 | 85.09054652537853 | 7135.5 | 0 | 164.50000000001455 | 60 |  | 93.51851851851852 | 8080 | 2020 | 9 | 2020_09_Asomata_english.xlsx
24 | 45 | 315 | 360 | 0 | 0 | 3 | 360 | 70 | 1.25 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 85.05 | 9320 | 41.79 | 3556.8 | 839.9999999999854 | 4475.999999999985 | 3636 | 10.1 | 84.3987534641966 | 4326.3 | 0 | 209.69999999998527 | 60 |  | 42.083333333333336 | 3636 | 2020 | 9 | 2020_09_Asomata_english.xlsx
25 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 40 | 8.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.6 | 8239.999999999993 | 41.67 | 3416.4 | -1080.0000000000073 | 2707.4999999999927 | 3787.5 | 10.1 | 85.29028959233953 | 2613.4 | 0 | 154.09999999999263 | 60 |  | 43.83680555555556 | 3787.5 | 2020 | 9 | 2020_09_Asomata_english.xlsx
26 | 0 | 240 | 240 | 0 | 0 | 3 | 240 | 50 | 0 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.4 | 7760.00000000002 | 41.37 | 3065.4 | -479.9999999999727 | 2779.106382978751 | 2424 | 10.1 | 85.69260227909582 | 2562.3 | 835.1063829787234 | 276.8063829787511 | 60 |  | 28.055555555555557 | 2424 | 2020 | 9 | 2020_09_Asomata_english.xlsx
27 | 300 | 0 | 300 | 0 | 0 | 4 | 300 | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.25 | 7400.000000000007 | 41.69 | 3439.8 | -360.00000000001273 | 2669.9999999999873 | 3030 | 10.1 | 85.99683637002754 | 2635.3 | 0 | 94.69999999998754 | 60 |  | 35.06944444444444 | 3030 | 2020 | 9 | 2020_09_Asomata_english.xlsx
28 | 115 | 605 | 720 | 0 | 0 | 4 | 720 | 110 | 2.3000000000029104 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.65 | 8360.00000000002 | 41.85 | 3627 | 960.0000000000127 | 8232.000000000013 | 7272 | 10.1 | 85.19030097617029 | 8161.4 | 0 | 130.6000000000131 | 60 |  | 84.16666666666667 | 7272 | 2020 | 9 | 2020_09_Asomata_english.xlsx
29 | 290 | 0 | 290 | 0 | 0 | 3 | 290 | 40 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.65 | 8360.00000000002 | 41.34 | 3030.3 | 0 | 4609.851063829788 | 2929 | 10.1 | 85.19030097617029 | 4478.4 | 1680.8510638297873 | 191.45106382978702 | 60 |  | 33.90046296296296 | 2929 | 2020 | 9 | 2020_09_Asomata_english.xlsx
30 | 0 | 317 | 317 | 0 | 0 | 3 | 317 | 55 | 0 | 7.470000000001164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.05 | 9320 | 41.81 | 3580.2 | 959.99999999998 | 4082.44999999998 | 3122.45 | 9.85 | 86.54085380592748 | 3873.15 | 0 | 209.29999999998017 | 0 |  | 36.139467592592595 | 3122.45 | 2020 | 9 | 2020_09_Asomata_english.xlsx
1 | 260 | 0 | 260 | 0 | 0 | 4 | 260 | 40 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85 | 9200.000000000007 | 41.9 | 3685.5 | -119.99999999999272 | 2506.0000000000073 | 2626 | 10.1 | 84.49689154962007 | 2385.8 | 0 | 120.20000000000755 | 0 |  | 30.39351851851852 | 2626 | 2020 | 10 | 2020_10_Asomata_english.xlsx
2 | 100 | 133 | 233 | 0 | 0 | 3 | 233 | 54 | 2.099999999998545 | 2.8300000000017462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 85.05 | 9320 | 41.65 | 3393 | 119.99999999999272 | 2543.1999999999925 | 2423.2 | 10.4 | 81.96417403734479 | 2467.4 | 0 | 75.7999999999929 | 0 |  | 28.046296296296298 | 2423.2 | 2020 | 10 | 2020_10_Asomata_english.xlsx
3 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 40 | 6.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.95 | 9080.000000000015 | 41.61 | 3346.2 | -239.99999999998545 | 2234.5000000000146 | 2474.5 | 10.1 | 84.59525812883966 | 2072 | 0 | 162.50000000001455 | 0 |  | 28.640046296296298 | 2474.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
4 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 40 | 0 | 5.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.9 | 8960.00000000002 | 41.73 | 3486.6 | -119.99999999999454 | 2354.5000000000055 | 2474.5 | 10.1 | 84.6938540007847 | 2189.5 | 0 | 165.00000000000546 | 0 |  | 28.640046296296298 | 2474.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
5 | 355 | 180 | 535 | 0 | 0 | 3 | 535 | 100 | 6.94999999999709 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.65 | 8360.00000000002 | 41.64 | 3381.3 | -600 | 4803.5 | 5403.5 | 10.1 | 85.19030097617029 | 4730.4 | 0 | 133.1 | 60 |  | 62.54050925925926 | 5403.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
6 | 0 | 380 | 380 | 0 | 0 | 4 | 380 | 55 | 0 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.3 | 9920 | 41.9 | 3685.5 | 1559.99999999998 | 5871.404255319129 | 3838 | 10.1 | 83.91146273980748 | 5577.2 | 473.40425531914894 | 294.2042553191295 | 0 |  | 44.4212962962963 | 3838 | 2020 | 10 | 2020_10_Asomata_english.xlsx
7 | 360 | 0 | 360 | 0 | 0 | 3 | 360 | 55 | 7.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.8 | 8720 | 41.61 | 3346.2 | -1200 | 2436 | 3636 | 10.1 | 84.89173683723513 | 2264.8 | 0 | 171.2 | 0 |  | 42.083333333333336 | 3636 | 2020 | 10 | 2020_10_Asomata_english.xlsx
8 | 0 | 235 | 235 | 0 | 0 | 4 | 235 | 40 | 0 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.15 | 9560.00000000002 | 41.47 | 3182.4 | 840.00000000002 | 5218.763157894757 | 2373.5 | 10.1 | 84.20315959753565 | 5115 | 2005.2631578947369 | 103.76315789475666 | 0 |  | 27.471064814814813 | 2373.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
9 | 285 | 0 | 285 | 0 | 0 | 3 | 285 | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85 | 9200.000000000007 | 41.72 | 3474.9 | -360.00000000001273 | 2518.4999999999873 | 2878.5 | 10.1 | 84.49689154962007 | 2372.5 | 0 | 145.99999999998727 | 0 |  | 33.31597222222222 | 2878.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
10 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 40 | 0 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85 | 9200.000000000007 | 41.32 | 3006.9 | 0 | 1749 | 1749 | 10.6 | 80.51118911803422 | 1597.5 | 0 | 151.5 | 0 |  | 20.243055555555557 | 1749 | 2020 | 10 | 2020_10_Asomata_english.xlsx
11 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 40 | 3.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85 | 9200.000000000007 | 40.9 | 2515.5 | 0 | 2015.0362694300518 | 1414 | 10.1 | 84.49689154962007 | 1849.75 | 601.0362694300518 | 165.2862694300518 | 0 |  | 16.36574074074074 | 1414 | 2020 | 10 | 2020_10_Asomata_english.xlsx
12 | 0 | 265 | 265 | 0 | 0 | 3 | 265 | 55 | 0 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.7 | 8480.000000000015 | 41.22 | 2889.9 | -719.9999999999927 | 1956.5000000000073 | 2676.5 | 10.1 | 85.09054652537853 | 1788.5 | 0 | 168.00000000000728 | 0 |  | 30.97800925925926 | 2676.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
13 | 260 | 0 | 260 | 0 | 0 | 3 | 260 | 55 | 6.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.7 | 8480.000000000015 | 41.69 | 3439.8 | 0 | 2626 | 2626 | 10.1 | 85.09054652537853 | 2528.4 | 0 | 97.59999999999991 | 0 |  | 30.39351851851852 | 2626 | 2020 | 10 | 2020_10_Asomata_english.xlsx
14 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 40 | 0 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.65 | 8360.00000000002 | 41.53 | 3252.6 | -119.99999999999454 | 1568.0000000000055 | 1688 | 10.55 | 81.5565914558597 | 1366.55 | 0 | 201.4500000000055 | 0 |  | 19.537037037037038 | 1688 | 2020 | 10 | 2020_10_Asomata_english.xlsx
15 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 55 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.6 | 8239.999999999993 | 41.45 | 3159 | -120.00000000002728 | 1682.499999999973 | 1802.5 | 10.3 | 83.63416746433293 | 1570.4 | 0 | 142.09999999997308 | 30 |  | 20.862268518518523 | 1802.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
16 | 0 | 180 | 180 | 0 | 0 | 4 | 180 | 54 | 0 | 3.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.7 | 8480.000000000015 | 41.5 | 3217.5 | 240.00000000002183 | 2058.000000000022 | 1818 | 10.1 | 85.09054652537853 | 1778 | 0 | 280.0000000000218 | 0 |  | 21.041666666666668 | 1818 | 2020 | 10 | 2020_10_Asomata_english.xlsx
17 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 54 | 1.3499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.15 | 9560.00000000002 | 40.7 | 2281.5 | 1080.0000000000055 | 3868.88297872341 | 682.5 | 10.5 | 80.9954201842962 | 3620.8 | 2106.3829787234044 | 248.08297872340972 | 0 |  | 7.899305555555555 | 682.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
18 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 55 | 0 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85.15 | 9560.00000000002 | 40.05 | 1520.9999999999945 | 0 | 858.5 | 858.5 | 10.1 | 84.20315959753565 | 788.4 | 0 | 130.1 | 60 |  | 9.936342592592593 | 858.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
19 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85.25 | 9800.000000000007 | 39.57 | 959.4 | 239.99999999998727 | 1031.9999999999873 | 792 | 9.9 | 85.7056110235301 | 836.2 | 0 | 195.79999999998722 | 0 |  | 9.166666666666666 | 792 | 2020 | 10 | 2020_10_Asomata_english.xlsx
20 | 0 | 125 | 125 | 0 | 0 | 3 | 125 | 42 | 0 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.1 | 9439.999999999993 | 39.74 | 1158.3 | -360.00000000001455 | 902.4999999999854 | 1262.5 | 10.1 | 84.30084307734718 | 722.7 | 0 | 179.79999999998552 | 0 |  | 14.612268518518519 | 1262.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
21 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 40 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 85.35 | 10040 | 40.73 | 2316.599999999995 | 600 | 2728.5 | 2128.5 | 9.9 | 85.50790488506752 | 2475 | 0 | 253.5 | 0 |  | 24.635416666666668 | 2128.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
22 | 0 | 115 | 115 | 0 | 0 | 4 | 115 | 55 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85.25 | 9800.000000000007 | 41 | 2632.5 | -239.99999999998545 | 3647.8157894736987 | 1161.5 | 10.1 | 84.00847021118297 | 3555.1 | 2726.315789473684 | 92.7157894736988 | 0 |  | 13.443287037037036 | 1161.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
23 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 40 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.2 | 9680.000000000015 | 41.42 | 3123.9 | -119.99999999999272 | 1193.0000000000073 | 1313 | 10.1 | 84.10570223689035 | 1168 | 0 | 85.00000000000728 | 60 |  | 15.19675925925926 | 1313 | 2020 | 10 | 2020_10_Asomata_english.xlsx
24 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.25 | 9800.000000000007 | 41.32 | 3006.9 | 119.99999999999272 | 769.9999999999927 | 650 | 10 | 84.84855491329479 | 737.2 | 0 | 32.79999999999279 | 0 |  | 7.523148148148148 | 650 | 2020 | 10 | 2020_10_Asomata_english.xlsx
25 | 0 | 140 | 140 | 0 | 0 | 3 | 140 | 35 | 0 | 4.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.5 | 8000.000000000007 | 41.9 | 3685.5 | -1800 | 2528.3404255319147 | 1456 | 10.4 | 83.02488687782805 | 2401.7 | 2872.3404255319147 | 186.64042553191484 | 60 |  | 16.85185185185185 | 1456 | 2020 | 10 | 2020_10_Asomata_english.xlsx
26 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.6 | 8239.999999999993 | 41.62 | 3357.9 | 239.99999999998545 | 960.9999999999854 | 721 | 10.3 | 83.63416746433293 | 773.8 | 0 | 247.1999999999855 | 60 |  | 8.344907407407407 | 721 | 2020 | 10 | 2020_10_Asomata_english.xlsx
27 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.7 | 8480.000000000015 | 41.48 | 3194.1 | 240.00000000002183 | 982.5000000000218 | 742.5 | 9.9 | 86.80954746528516 | 851.2 | 0 | 131.3000000000219 | 0 |  | 8.59375 | 742.5 | 2020 | 10 | 2020_10_Asomata_english.xlsx
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.6 | 8239.999999999993 | 41.51 | 3229.2 | -240.00000000002183 | 2041.1914893616804 | 728 | 10.4 | 82.82999277717589 | 1949.1 | 1553.1914893617022 | 92.09148936168049 | 0 |  | 8.425925925925926 | 728 | 2020 | 10 | 2020_10_Asomata_english.xlsx
29 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.5 | 8000.000000000007 | 41.58 | 3311.1 | -239.99999999998545 | 5283.914893617036 | 742 | 10.6 | 81.4583795782464 | 5069.2 | 4781.914893617021 | 214.71489361703607 | 0 |  | 8.587962962962964 | 742 | 2020 | 10 | 2020_10_Asomata_english.xlsx
30 | 0 | 150 | 150 | 0 | 0 | 3 | 150 | 54 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 83.2 | 4880.000000000014 | 41.62 | 3357.9 | -3119.9999999999936 | 636.9354838709742 | 1515 | 10.1 | 88.18850331635105 | 674.5 | 2241.935483870968 | 22.435483870974167 | 60 |  | 17.53472222222222 | 1515 | 2020 | 10 | 2020_10_Asomata_english.xlsx
31 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 40 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 83.65 | 5960.00000000002 | 41.69 | 3439.8 | 1080.0000000000064 | 2508.2500000000064 | 1428.25 | 9.85 | 89.44979006831157 | 2316.95 | 0 | 191.3000000000061 | 0 |  | 16.530671296296298 | 1428.25 | 2020 | 10 | 2020_10_Asomata_english.xlsx
1 | 140 | 10 | 150 | 0 | 0 | 4 | 150 | 55 | 3.0500000000029104 | 0.19999999999708962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 85.1 | 9439.999999999993 | 41.42 | 3123.9 | 3479.9999999999727 | 4994.999999999973 | 1515 | 10.1 | 84.30084307734718 | 4883.7 | 0 | 171.2999999999729 | 60 |  | 17.53472222222222 | 1515 | 2020 | 11 | 2020_11_Asomata_english.xlsx
2 | 235 | 270 | 505 | 0 | 0 | 4 | 505 | 110 | 4.849999999998545 | 5.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 2 | 84 | 6800.000000000007 | 41.62 | 3357.9 | -2639.9999999999854 | 2662.5000000000146 | 5302.5 | 10.5 | 83.21315192743764 | 2635.3 | 0 | 87.20000000001482 | 60 |  | 61.37152777777778 | 5302.5 | 2020 | 11 | 2020_11_Asomata_english.xlsx
3 | 115 | 90 | 205 | 0 | 0 | 3 | 205 | 110 | 2.400000000001455 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.3 | 7520 | 41.47 | 3182.4 | 719.9999999999927 | 2790.4999999999927 | 2070.5 | 10.1 | 85.89518526320718 | 2499 | 0 | 291.4999999999927 | 0 |  | 23.96412037037037 | 2070.5 | 2020 | 11 | 2020_11_Asomata_english.xlsx
4 | 35 | 40 | 75 | 0 | 0 | 4 | 75 | 35 | 0.7999999999956344 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.35 | 7639.999999999993 | 41.38 | 3077.1 | 119.99999999999272 | 907.4999999999927 | 787.5 | 10.5 | 82.52543992803734 | 730 | 0 | 237.49999999999272 | 60 |  | 9.114583333333334 | 787.5 | 2020 | 11 | 2020_11_Asomata_english.xlsx
5 | 85 | 20 | 105 | 0 | 0 | 3 | 105 | 80 | 2.6000000000058208 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.1 | 7039.999999999993 | 41.38 | 3077.1 | -600 | 4215.196808510638 | 1107.75 | 10.55 | 82.62205761502179 | 4167.45 | 3707.446808510638 | 47.7468085106384 | 0 |  | 12.821180555555555 | 1107.75 | 2020 | 11 | 2020_11_Asomata_english.xlsx
6 | 0 | 40 | 40 | 0 | 0 | 4 | 40 | 35 | 0 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83.25 | 5000.000000000007 | 41.13 | 2784.6 | -2039.9999999999854 | 2953.148936170227 | 424 | 10.6 | 83.92681532304174 | 2970 | 4569.148936170212 | 43.14893617022699 | 60 |  | 4.907407407407407 | 424 | 2020 | 11 | 2020_11_Asomata_english.xlsx
7 | 100 | 60 | 160 | 0 | 0 | 3 | 160 | 95 | 1.8999999999941792 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 83.45 | 5480.000000000014 | 41.85 | 3627 | 480.00000000000637 | 5553.617021276603 | 1680 | 10.5 | 84.31730713998506 | 5467.7 | 3393.617021276596 | 145.917021276603 | 60 |  | 19.444444444444443 | 1680 | 2020 | 11 | 2020_11_Asomata_english.xlsx
8 | 90 | 260 | 350 | 0 | 0 | 4 | 350 | 103 | 1.8000000000029104 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 8 | 84.65 | 8360.00000000002 | 41.84 | 3615.3 | 2880.0000000000064 | 6415.000000000006 | 3535 | 10.1 | 85.19030097617029 | 6223 | 0 | 252.00000000000637 | 60 |  | 40.914351851851855 | 3535 | 2020 | 11 | 2020_11_Asomata_english.xlsx
9 | 85 | 25 | 110 | 0 | 0 | 3 | 110 | 85 | 2 | 0.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.85 | 8839.999999999993 | 41.47 | 3182.4 | 479.9999999999727 | 1568.9999999999727 | 1089 | 9.9 | 86.50566340181277 | 1305 | 0 | 263.9999999999727 | 0 |  | 12.604166666666666 | 1089 | 2020 | 11 | 2020_11_Asomata_english.xlsx
10 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 84 | 6800.000000000007 | 40.92 | 2538.9 | -2039.9999999999854 | 3818.6387434555118 | 0 | 10.1 |  | 3792.4 | 5858.638743455497 | 86.23874345551212 | 60 |  | 0 | 0 | 2020 | 11 | 2020_11_Asomata_english.xlsx
11 | 140 | 135 | 275 | 0 | 0 | 4 | 275 | 100 | 2.5 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.7 | 8480.000000000015 | 41.56 | 3287.7 | 1680.0000000000073 | 8370.69148936171 | 2887.5 | 10.5 | 81.8490018958403 | 8371.65 | 3803.191489361702 | 59.041489361710774 | 60 |  | 33.420138888888886 | 2887.5 | 2020 | 11 | 2020_11_Asomata_english.xlsx
12 | 200 | 215 | 415 | 0 | 0 | 3 | 415 | 108 | 4.900000000001455 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 12 | 84.55 | 8120 | 42.09 | 3907.8 | -360.00000000001455 | 4832.7105263157755 | 4108.5 | 9.9 | 87.11557407209581 | 4687.5 | 1084.2105263157896 | 145.2105263157755 | 0 |  | 47.552083333333336 | 4108.5 | 2020 | 11 | 2020_11_Asomata_english.xlsx
13 | 110 | 75 | 185 | 0 | 0 | 4 | 185 | 95 | 2.099999999998545 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 83.05 | 4520 | 41.26 | 2936.7 | -3600 | 3097.5851063829787 | 1979.5 | 10.7 | 83.54753150363702 | 3143 | 4718.085106382979 | 104.58510638297867 | 150 |  | 22.91087962962963 | 1979.5 | 2020 | 11 | 2020_11_Asomata_english.xlsx
14 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14 | 83.5 | 5600.000000000007 | 40.73 | 2316.599999999995 | 1080.0000000000073 | 1080.0000000000073 | 0 | 10.1 |  | 767.6 | 0 | 312.40000000000737 | 0 |  | 0 | 0 | 2020 | 11 | 2020_11_Asomata_english.xlsx
15 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 83.5 | 5600.000000000007 | 40.93 | 2550.6 | 0 | 795 | 795 | 10.6 | 83.42123209820414 | 675 | 0 | 120 | 0 |  | 9.20138888888889 | 795 | 2020 | 11 | 2020_11_Asomata_english.xlsx
16 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83.5 | 5600.000000000007 | 41.09 | 2737.8 | 0 | 721 | 721 | 10.3 | 85.85097672242367 | 693.5 | 0 | 92.5 | 65 |  | 8.344907407407407 | 721 | 2020 | 11 | 2020_11_Asomata_english.xlsx
17 | 105 | 85 | 190 | 0 | 0 | 4 | 190 | 110 | 2 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 82.85 | 4069.9999999999873 | 42.02 | 3825.9 | -1530.00000000002 | 611.6382978723204 | 1881 | 9.9 | 90.74094679969834 | 617.7 | 260.63829787234044 | 93.9382978723205 | 100 |  | 21.770833333333332 | 1881 | 2020 | 11 | 2020_11_Asomata_english.xlsx
18 | 35 | 35 | 70 | 0 | 0 | 3 | 70 | 70 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 82.85 | 4069.9999999999873 | 42.14 | 3966.3 | 0 | 707 | 707 | 10.1 | 88.94409636802115 | 693.5 | 0 | 73.5 | 60 |  | 8.18287037037037 | 707 | 2020 | 11 | 2020_11_Asomata_english.xlsx
19 | 30 | 30 | 60 | 0 | 0 | 3 | 60 | 70 | 0.8499999999985448 | 0.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 83.15 | 4760.00000000002 | 41.94 | 3732.3 | 690.0000000000327 | 3046.0000000000327 | 606 | 10.1 | 88.29565824140128 | 2941.9 | 1750 | 134.1000000000331 | 30 |  | 7.013888888888889 | 606 | 2020 | 11 | 2020_11_Asomata_english.xlsx
20 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 83.4 | 5360.00000000002 | 41.45 | 3159 | 600 | 4084.0425531914893 | 0 | 10.1 |  | 3927.4 | 3484.0425531914893 | 186.64255319148924 | 30 |  | 0 | 0 | 2020 | 11 | 2020_11_Asomata_english.xlsx
21 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 83.3 | 5120 | 41 | 2632.5 | -240.00000000002 | 807.872340425512 | 0 | 10.1 |  | 630 | 1047.872340425532 | 177.872340425512 | 0 |  | 0 | 0 | 2020 | 11 | 2020_11_Asomata_english.xlsx
22 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.2 | 4880.000000000014 | 41.22 | 2889.9 | -239.99999999998636 | 1309.8947368421188 | 792 | 9.9 | 89.97008924193389 | 1072.5 | 757.8947368421052 | 237.39473684211885 | 0 |  | 9.166666666666666 | 792 | 2020 | 11 | 2020_11_Asomata_english.xlsx
23 | 154 | 79 | 233 | 0 | 0 | 4 | 233 | 108 | 3.75 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.35 | 10040 | 41.81 | 3580.2 | 5159.999999999979 | 7807.708333333312 | 2330 | 10 | 84.65282583621685 | 7717.5 | 317.7083333333333 | 90.20833333331211 | 0 |  | 26.96759259259259 | 2330 | 2020 | 11 | 2020_11_Asomata_english.xlsx
24 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 84.7 | 8480.000000000015 | 41.16 | 2819.7 | -1559.9999999999782 | 237.87234042555383 | 0 | 10.1 |  | 0 | 1797.872340425532 | 237.87234042555383 | 0 |  | 0 | 0 | 2020 | 11 | 2020_11_Asomata_english.xlsx
25 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 84.7 | 8480.000000000015 | 40.66 | 2234.699999999995 | 0 | 0 | 0 | 10.1 |  | 0 | 0 | 60 | 60 |  | 0 | 0 | 2020 | 11 | 2020_11_Asomata_english.xlsx
26 | 0 | 71 | 71 | 0 | 0 | 3 | 71 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600.000000000007 | 40.79 | 2386.8 | 119.99999999999272 | 822.8999999999927 | 702.9 | 9.9 | 86.70801583082284 | 712.5 | 0 | 110.3999999999927 | 0 |  | 8.135416666666666 | 702.9 | 2020 | 11 | 2020_11_Asomata_english.xlsx
27 | 71 | 0 | 71 | 0 | 0 | 4 | 71 | 35 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.75 | 8600.000000000007 | 40.88 | 2492.1 | 0 | 745.5 | 745.5 | 10.5 | 81.75327206906154 | 675 | 0 | 70.5 | 0 |  | 8.628472222222221 | 745.5 | 2020 | 11 | 2020_11_Asomata_english.xlsx
28 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.1 | 9439.999999999993 | 41.01 | 2644.2 | 839.9999999999854 | 3298.0769230769083 | 735 | 10.5 | 81.08938238868635 | 3207.2 | 1723.076923076923 | 90.8769230769085 | 0 |  | 8.506944444444445 | 735 | 2020 | 11 | 2020_11_Asomata_english.xlsx
29 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.2 | 7280.000000000014 | 41.14 | 2796.3 | -2159.999999999979 | 1313.6684491978817 | 848 | 10.6 | 82.03746758472681 | 1365.1 | 2625.668449197861 | 48.56844919788182 | 100 |  | 9.814814814814815 | 848 | 2020 | 11 | 2020_11_Asomata_english.xlsx
30 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 47 | 0 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.1 | 7039.999999999993 | 41.33 | 3018.6 | -240.00000000002092 | 3000.514999999979 | 912.39 | 10.734 | 81.20576745281163 | 2835 | 2328.125 | 165.51499999997895 | 0 |  | 10.560069444444444 | 912.39 | 2020 | 11 | 2020_11_Asomata_english.xlsx
1 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 55 | 5.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 3 | 0 | ΒΛΑΒΗ ΟΡΙΟΥ ΦΟΡΤΙΟΥ | 1 | 85.2 | 9680.000000000015 | 41.83 | 3603.6 | 2640.000000000022 | 8130.638297872362 | 1980 | 9.9 | 85.8048073325851 | 7862.1 | 3510.6382978723404 | 268.5382978723628 | 0 |  | 22.916666666666668 | 1980 | 2020 | 12 | 2020_12_Asomata_english.xlsx
2 | 85 | 90 | 175 | 0 | 0 | 4 | 175 | 55 | 1.7000000000043656 | 1.7000000000043656 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΧΑΜΗΛΗ ΣΤΑΘΜΗ ΩΣΤΙΚΟΥ - ΟΔΗΓΟΥ ΕΔΡ | 2 | 85.3 | 9920 | 42.03 | 3837.6 | 239.99999999998545 | 5483.138297872326 | 1732.5 | 9.9 | 85.60664380525813 | 5511.5 | 3510.6382978723404 | 71.6382978723268 | 100 |  | 20.052083333333332 | 1732.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
3 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 55 | 3.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.55 | 8120 | 41.34 | 3030.3 | -1800 | 1785.4166666666665 | 1575 | 10.5 | 82.13754126797606 | 1547.6 | 2010.4166666666665 | 237.8166666666666 | 0 |  | 18.229166666666668 | 1575 | 2020 | 12 | 2020_12_Asomata_english.xlsx
4 | 105 | 140 | 245 | 0 | 0 | 4 | 245 | 110 | 2.2000000000043656 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 85.35 | 10040 | 41.72 | 3474.9 | 1919.9999999999927 | 4909.602564102557 | 2425.5 | 9.9 | 85.50790488506752 | 4672.5 | 564.1025641025641 | 237.10256410255715 | 0 |  | 28.072916666666668 | 2425.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
5 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.8 | 8720 | 41.43 | 3135.6 | -1319.9999999999927 | 2896.794871794879 | 945 | 10.5 | 81.65776591010237 | 2902.5 | 3271.7948717948716 | 94.29487179487887 | 100 |  | 10.9375 | 945 | 2020 | 12 | 2020_12_Asomata_english.xlsx
6 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.35 | 7639.999999999993 | 41.7 | 3451.5 | -1080.0000000000073 | 3268.4585492227907 | 892.5 | 10.5 | 82.52543992803734 | 3212 | 3455.958549222798 | 116.45854922279068 | 60 |  | 10.32986111111111 | 892.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
7 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 83.25 | 5000.000000000007 | 41.23 | 2901.6 | -2639.9999999999854 | 1616.2765957446954 | 735 | 10.5 | 84.72611832611832 | 1620.6 | 3521.276595744681 | 95.67659574469553 | 100 |  | 8.506944444444445 | 735 | 2020 | 12 | 2020_12_Asomata_english.xlsx
8 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.6 | 5839.999999999993 | 41.19 | 2854.8 | 839.9999999999854 | 3196.7461928933863 | 707 | 10.1 | 87.34053693830923 | 3123.75 | 1649.746192893401 | 72.99619289338625 | 0 |  | 8.18287037037037 | 707 | 2020 | 12 | 2020_12_Asomata_english.xlsx
9 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.2 | 7280.000000000014 | 41.28 | 2960.1 | 1440.000000000021 | 3886.795918367368 | 707 | 10.1 | 86.09872835624795 | 3737.6 | 1739.795918367347 | 149.195918367368 | 0 |  | 8.18287037037037 | 707 | 2020 | 12 | 2020_12_Asomata_english.xlsx
10 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.65 | 5960.00000000002 | 41.46 | 3170.7 | -1319.9999999999936 | 3091.735106382985 | 943.65 | 10.485 | 84.03246849526649 | 3146.3 | 3468.0851063829787 | 25.435106382985396 | 80 |  | 10.921875 | 943.65 | 2020 | 12 | 2020_12_Asomata_english.xlsx
11 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 55 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.5 | 5600.000000000007 | 41.52 | 3240.9 | -360.00000000001273 | 2905.622448979579 | 959.5 | 10.1 | 87.55099606346177 | 2868.9 | 2306.122448979592 | 76.72244897957899 | 40 |  | 11.105324074074074 | 959.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
12 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 83.35 | 5239.999999999993 | 41.5 | 3217.5 | -360.00000000001455 | 2616.8877551020264 | 757.5 | 10.1 | 87.86859338896406 | 2555 | 2219.387755102041 | 61.887755102026404 | 0 |  | 8.76736111111111 | 757.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
13 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 45 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 82.95 | 4290.000000000006 | 41.52 | 3240.9 | -949.9999999999864 | 3089.6428571428705 | 682.5 | 10.5 | 85.34682248967962 | 3124.4 | 3357.142857142857 | 25.242857142870434 | 60 |  | 7.899305555555555 | 682.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
14 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 82.5 | 3300 | 41.56 | 3287.7 | -990.0000000000064 | 1638.7712765957383 | 1011.75 | 10.65 | 85.07969628470411 | 1587.75 | 1617.0212765957447 | 111.0212765957383 | 60 |  | 11.710069444444445 | 1011.75 | 2020 | 12 | 2020_12_Asomata_english.xlsx
15 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15 | 83.9 | 6560.00000000002 | 41.09 | 2737.8 | 3260.00000000002 | 5531.3567839196185 | 0 | 10.1 |  | 5350.8 | 2271.356783919598 | 180.55678391961828 | 0 |  | 0 | 0 | 2020 | 12 | 2020_12_Asomata_english.xlsx
16 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83.8 | 6320 | 41.24 | 2913.3 | -240.00000000002 | 3851.3829787233844 | 735 | 10.5 | 83.61130097972203 | 3832.5 | 3356.3829787234044 | 78.88297872338444 | 60 |  | 8.506944444444445 | 735 | 2020 | 12 | 2020_12_Asomata_english.xlsx
17 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.9 | 6560.00000000002 | 41.53 | 3252.6 | 240.00000000002 | 4541.3829787234245 | 945 | 10.5 | 83.41175133537901 | 4526 | 3356.3829787234044 | 75.38297872342446 | 60 |  | 10.9375 | 945 | 2020 | 12 | 2020_12_Asomata_english.xlsx
18 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 35 | 0 | 2.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.8 | 6320 | 41.34 | 3030.3 | -240.00000000002 | 4594.736842105243 | 840 | 10.5 | 83.61130097972203 | 4627.5 | 3994.7368421052633 | 67.23684210524334 | 100 |  | 9.722222222222221 | 840 | 2020 | 12 | 2020_12_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.65 | 5960.00000000002 | 41.4 | 3100.5 | -359.99999999998 | 4369.680851063849 | 735 | 10.5 | 83.91242211170182 | 4350.8 | 3994.68085106383 | 78.88085106384915 | 60 |  | 8.506944444444445 | 735 | 2020 | 12 | 2020_12_Asomata_english.xlsx
20 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 83.1 | 4639.999999999993 | 41.5 | 3217.5 | -1320.0000000000273 | 3787.894736842078 | 1050 | 10.5 | 85.03533773606767 | 3781.4 | 4057.8947368421054 | 66.49473684207805 | 60 |  | 12.152777777777779 | 1050 | 2020 | 12 | 2020_12_Asomata_english.xlsx
21 | 45 | 0 | 45 | 0 | 0 | 3 | 45 | 35 | 1.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 82.85 | 4069.9999999999873 | 41.31 | 2995.2 | -570.0000000000055 | 3961.7430687830633 | 462.96 | 10.288 | 87.31875712645932 | 3934.7 | 4068.7830687830688 | 87.04306878306352 | 60 |  | 5.358333333333334 | 462.96 | 2020 | 12 | 2020_12_Asomata_english.xlsx
22 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 50 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.4 | 5360.00000000002 | 41.48 | 3194.1 | 1290.0000000000327 | 2148.5000000000327 | 858.5 | 10.1 | 87.76247189936385 | 1980 | 0 | 168.50000000003274 | 0 |  | 9.936342592592593 | 858.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
23 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.95 | 6680.000000000014 | 41.46 | 3170.7 | 1319.9999999999936 | 2026.9999999999936 | 707 | 10.1 | 86.61183162416361 | 1970.55 | 0 | 56.44999999999368 | 0 |  | 8.18287037037037 | 707 | 2020 | 12 | 2020_12_Asomata_english.xlsx
24 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.95 | 6680.000000000014 | 41.51 | 3229.2 | 0 | 707 | 707 | 10.1 | 86.61183162416361 | 641.75 | 0 | 65.25 | 0 |  | 8.18287037037037 | 707 | 2020 | 12 | 2020_12_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84 | 6800.000000000007 | 41.5 | 3217.5 | 119.99999999999363 | 826.9999999999936 | 707 | 10.1 | 86.50872230080151 | 671.95 | 0 | 155.0499999999937 | 0 |  | 8.18287037037037 | 707 | 2020 | 12 | 2020_12_Asomata_english.xlsx
26 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 83.45 | 5480.000000000014 | 41.56 | 3287.7 | -1319.9999999999936 | 3605.8575129533738 | 858.5 | 10.1 | 87.65660643265774 | 3555.1 | 4067.3575129533674 | 50.75751295337386 | 0 |  | 9.936342592592593 | 858.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
27 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.25 | 5000.000000000007 | 41.55 | 3276 | -480.00000000000637 | 2369.3782383419625 | 1010 | 10.1 | 88.08160816081609 | 2256.45 | 1839.3782383419689 | 112.9282383419627 | 0 |  | 11.689814814814815 | 1010 | 2020 | 12 | 2020_12_Asomata_english.xlsx
28 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 1.8999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 83 | 4400 | 41.47 | 3182.4 | -600.0000000000073 | 3691.2499999999927 | 791.25 | 10.55 | 84.8387469656687 | 3686.4 | 3500 | 64.84999999999263 | 60 |  | 9.15798611111111 | 791.25 | 2020 | 12 | 2020_12_Asomata_english.xlsx
29 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 83 | 4400 | 41.06 | 2702.7 | 0 | 4479.722222222222 | 757.5 | 10.1 | 88.61869113740643 | 4403 | 3722.2222222222217 | 76.72222222222172 | 0 |  | 8.76736111111111 | 757.5 | 2020 | 12 | 2020_12_Asomata_english.xlsx
30 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 83.15 | 4760.00000000002 | 40.9 | 2515.5 | 360.00000000002 | 4328.780104712062 | 707 | 10.1 | 88.29565824140128 | 4365.4 | 3261.780104712042 | 23.380104712062348 | 60 |  | 8.18287037037037 | 707 | 2020 | 12 | 2020_12_Asomata_english.xlsx
31 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 82.95 | 4290.000000000006 | 40.91 | 2527.199999999995 | -470.00000000001364 | 4332.74468085105 | 707 | 10.1 | 88.72689466748872 | 4282.85 | 4095.744680851064 | 109.89468085105 | 60 |  | 8.18287037037037 | 707 | 2020 | 12 | 2020_12_Asomata_english.xlsx
1 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.2 | 4880.000000000014 | 40.93 | 2550.6 | 590.0000000000073 | 4482.567010309285 | 707 | 10.1 | 88.18850331635105 | 4496.8 | 3185.5670103092784 | 45.76701030928507 | 60 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
2 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 83.25 | 5000.000000000007 | 40.9 | 2515.5 | 119.99999999999363 | 4451.999999999994 | 707 | 10.1 | 88.08160816081609 | 4462.55 | 3625 | 49.44999999999345 | 60 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
3 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.15 | 4760.00000000002 | 40.9 | 2515.5 | -239.99999999998727 | 4558.492063492076 | 735 | 10.5 | 84.93201411791934 | 4572 | 4063.4920634920636 | 46.49206349207634 | 60 |  | 8.506944444444445 | 735 | 2021 | 1 | 2021_01_Asomata_english.xlsx
4 | 0 | 100 | 100 | 0 | 0 | 3 | 100 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 83.5 | 5600.000000000007 | 41.16 | 2819.7 | 839.9999999999873 | 5979.473684210514 | 1050 | 10.5 | 84.21572002294894 | 5860.8 | 4089.4736842105262 | 178.67368421051378 | 60 |  | 12.152777777777779 | 1050 | 2021 | 1 | 2021_01_Asomata_english.xlsx
5 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 83.5 | 5600.000000000007 | 41.17 | 2831.4 | 0 | 735 | 735 | 10.5 | 84.21572002294894 | 627.8 | 0 | 167.2 | 60 |  | 8.506944444444445 | 735 | 2021 | 1 | 2021_01_Asomata_english.xlsx
6 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83.55 | 5720 | 41.26 | 2936.7 | 119.99999999999272 | 826.9999999999927 | 707 | 10.1 | 87.44563987084629 | 657 | 0 | 169.99999999999272 | 0 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
7 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 55 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.45 | 7880.000000000014 | 41.3 | 2983.5 | 2160.0000000000136 | 3290.6122448979727 | 850 | 10 | 86.44758539458186 | 3042.65 | 280.61224489795916 | 247.9622448979726 | 0 |  | 9.837962962962964 | 850 | 2021 | 1 | 2021_01_Asomata_english.xlsx
8 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.9 | 6560.00000000002 | 41.32 | 3006.9 | -1319.9999999999936 | 2925.638297872347 | 735 | 10.5 | 83.41175133537901 | 2867.15 | 3510.6382978723404 | 118.48829787234672 | 60 |  | 8.506944444444445 | 735 | 2021 | 1 | 2021_01_Asomata_english.xlsx
9 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 83.6 | 5839.999999999993 | 41.33 | 3018.6 | -720.0000000000273 | 3350.0851063829514 | 852 | 10.65 | 82.82999277717589 | 3248.5 | 3218.0851063829787 | 161.58510638295138 | 60 |  | 9.86111111111111 | 852 | 2021 | 1 | 2021_01_Asomata_english.xlsx
10 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.6 | 5839.999999999993 | 41.23 | 2901.6 | 0 | 1267.2094240837696 | 707 | 10.1 | 87.34053693830923 | 1073 | 560.2094240837696 | 194.2094240837696 | 0 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
11 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.5 | 5600.000000000007 | 41.38 | 3077.1 | -239.99999999998545 | 3642.5319148936314 | 707 | 10.1 | 87.55099606346177 | 3547.8 | 3175.531914893617 | 154.7319148936317 | 60 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
12 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 83.55 | 5720 | 41.5 | 3217.5 | 119.99999999999272 | 3757.4361702127585 | 738.5 | 10.55 | 83.71573106118933 | 3372.6 | 2898.936170212766 | 444.8361702127586 | 60 |  | 8.547453703703704 | 738.5 | 2021 | 1 | 2021_01_Asomata_english.xlsx
13 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 83.5 | 5600.000000000007 | 41.5 | 3217.5 | -119.99999999999272 | 4538.4574468085175 | 892.5 | 10.5 | 84.21572002294894 | 4387.3 | 3765.9574468085107 | 211.1574468085173 | 60 |  | 10.32986111111111 | 892.5 | 2021 | 1 | 2021_01_Asomata_english.xlsx
14 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.9 | 8960.00000000002 | 41.57 | 3299.4 | 3360.0000000000127 | 6456.702127659588 | 735 | 10.5 | 81.46742146742146 | 6394.8 | 2361.7021276595747 | 121.90212765958859 | 60 |  | 8.506944444444445 | 735 | 2021 | 1 | 2021_01_Asomata_english.xlsx
15 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.75 | 8600.000000000007 | 41.56 | 3287.7 | -360.00000000001273 | 2102.3191489361575 | 707 | 10.1 | 84.9910254183313 | 1992.9 | 1755.3191489361702 | 169.41914893615763 | 60 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.9 | 8960.00000000002 | 41.54 | 3264.3 | 360.00000000001273 | 1067.0000000000127 | 707 | 10.1 | 84.6938540007847 | 1014.7 | 0 | 52.3000000000128 | 0 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
17 | 165 | 70 | 235 | 0 | 0 | 3 | 235 | 85 | 3.5 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 85.35 | 10040 | 41.64 | 3381.3 | 1079.9999999999727 | 3406.4999999999727 | 2326.5 | 9.9 | 85.50790488506752 | 3210.9 | 0 | 195.59999999997262 | 0 |  | 26.927083333333332 | 2326.5 | 2021 | 1 | 2021_01_Asomata_english.xlsx
18 | 45 | 100 | 145 | 0 | 0 | 4 | 145 | 45 | 1 | 2.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 2 | 2 | ΒΛΑΒΗ ΑΝΤΛΙΑΣ ΜΙΤΣΕΛ | 18 | 84.55 | 8120 | 40.93 | 2550.6 | -1919.9999999999927 | 890.8310810810883 | 1529.75 | 10.55 | 81.7482638212084 | 812 | 1281.081081081081 | 228.8310810810883 | 150 |  | 17.705439814814813 | 1529.75 | 2021 | 1 | 2021_01_Asomata_english.xlsx
19 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.6 | 8239.999999999993 | 40.55 | 2106 | 119.99999999999272 | 877.4999999999927 | 757.5 | 10.1 | 85.29028959233953 | 676.2 | 0 | 201.2999999999928 | 0 |  | 8.76736111111111 | 757.5 | 2021 | 1 | 2021_01_Asomata_english.xlsx
20 | 90 | 460 | 550 | 0 | 0 | 3 | 550 | 100 | 2.1999999999970896 | 10.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 85.3 | 9920 | 41.75 | 3510 | 1680.0000000000073 | 7345.000000000007 | 5665 | 10.3 | 82.28211394874324 | 7282.5 | 0 | 62.500000000007276 | 0 |  | 65.56712962962963 | 5665 | 2021 | 1 | 2021_01_Asomata_english.xlsx
21 | 190 | 105 | 295 | 0 | 0 | 2 | 295 | 45 | 4.5 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 21 | 84.7 | 8480.000000000015 | 41.72 | 3474.9 | -1439.9999999999854 | 1598.5000000000146 | 3038.5 | 10.3 | 83.4383029035265 | 1530 | 0 | 68.50000000001455 | 0 |  | 35.167824074074076 | 3038.5 | 2021 | 1 | 2021_01_Asomata_english.xlsx
22 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.8 | 8720 | 41.22 | 2889.9 | 239.99999999998545 | 946.9999999999854 | 707 | 10.1 | 84.89173683723513 | 678.9 | 0 | 328.09999999998547 | 60 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
23 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 43 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.8 | 8720 | 40.9 | 2515.5 | 0 | 800 | 800 | 10 | 85.74065420560747 | 715.2 | 0 | 84.8 | 0 |  | 9.25925925925926 | 800 | 2021 | 1 | 2021_01_Asomata_english.xlsx
24 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.9 | 8960.00000000002 | 40.67 | 2246.4 | 240.00000000002 | 940.00000000002 | 700 | 10 | 85.54079254079252 | 762.2 | 0 | 177.80000000001996 | 0 |  | 8.101851851851851 | 700 | 2021 | 1 | 2021_01_Asomata_english.xlsx
25 | 130 | 150 | 280 | 0 | 0 | 3 | 280 | 70 | 3.599999999998545 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.1 | 7039.999999999993 | 41.31 | 2995.2 | -1920.0000000000273 | 879.9999999999727 | 2800 | 10 | 87.16627078384799 | 737.3 | 0 | 142.69999999997276 | 0 |  | 32.407407407407405 | 2800 | 2021 | 1 | 2021_01_Asomata_english.xlsx
26 | 300 | 470 | 770 | 0 | 0 | 3 | 770 | 109 | 5.700000000004366 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84.9 | 8960.00000000002 | 41.72 | 3474.9 | 1920.0000000000273 | 9912.553191489389 | 7700 | 10 | 85.54079254079252 | 9752.6 | 292.5531914893617 | 159.9531914893887 | 0 |  | 89.12037037037037 | 7700 | 2021 | 1 | 2021_01_Asomata_english.xlsx
27 | 460 | 370 | 830 | 0 | 0 | 4 | 830 | 110 | 10 | 7.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 85.1 | 9439.999999999993 | 41.85 | 3627 | 479.9999999999727 | 9111.999999999973 | 8632 | 10.4 | 81.86908798857756 | 9075 | 0 | 36.999999999972715 | 0 |  | 99.9074074074074 | 8632 | 2021 | 1 | 2021_01_Asomata_english.xlsx
28 | 160 | 610 | 770 | 0 | 0 | 4 | 770 | 110 | 3.5 | 15.14999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84.4 | 7760.00000000002 | 41.67 | 3416.4 | -1679.9999999999727 | 6097.000000000027 | 7777 | 10.1 | 85.69260227909582 | 5905.7 | 0 | 191.30000000002747 | 0 |  | 90.01157407407408 | 7777 | 2021 | 1 | 2021_01_Asomata_english.xlsx
29 | 570 | 20 | 590 | 0 | 0 | 3 | 590 | 110 | 14 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.5 | 8000.000000000007 | 41.74 | 3498.3 | 239.99999999998727 | 6198.999999999987 | 5959 | 10.1 | 85.49097262667443 | 6141.6 | 0 | 57.3999999999869 | 0 |  | 68.9699074074074 | 5959 | 2021 | 1 | 2021_01_Asomata_english.xlsx
30 | 45 | 390 | 435 | 0 | 0 | 4 | 435 | 110 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.4 | 7760.00000000002 | 41.98 | 3779.1 | -239.99999999998727 | 4153.500000000013 | 4393.5 | 10.1 | 85.69260227909582 | 3974.4 | 0 | 179.10000000001264 | 0 |  | 50.85069444444444 | 4393.5 | 2021 | 1 | 2021_01_Asomata_english.xlsx
31 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.4 | 7760.00000000002 | 41.24 | 2913.3 | 0 | 1866.5744680851064 | 707 | 10.1 | 85.69260227909582 | 1689.8 | 1159.5744680851064 | 176.7744680851065 | 0 |  | 8.18287037037037 | 707 | 2021 | 1 | 2021_01_Asomata_english.xlsx
1 | 240 | 0 | 240 | 0 | 0 | 3 | 240 | 54 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.9 | 8960.00000000002 | 41.15 | 2808 | 1200 | 3624 | 2424 | 10.1 | 84.6938540007847 | 3460.2 | 0 | 163.8 | 0 |  | 28.055555555555557 | 2424 | 2021 | 2 | 2021_02_Asomata_english.xlsx
2 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.35 | 10040 | 41.18 | 2843.1 | 1079.9999999999727 | 1786.9999999999727 | 707 | 10.1 | 83.81467904575926 | 1642.8 | 0 | 144.19999999997253 | 0 |  | 8.18287037037037 | 707 | 2021 | 2 | 2021_02_Asomata_english.xlsx
3 | 105 | 340 | 445 | 0 | 0 | 4 | 445 | 108 | 2.599999999998545 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 85.45 | 10320 | 41.44 | 3147.3 | 280.0000000000073 | 4774.500000000007 | 4494.5 | 10.1 | 83.62177989950894 | 4717.5 | 0 | 57.000000000007276 | 0 |  | 52.019675925925924 | 4494.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
4 | 0 | 610 | 610 | 0 | 0 | 3 | 610 | 55 | 0 | 14.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85.1 | 9439.999999999993 | 41.64 | 3381.3 | -880.0000000000073 | 5219.999999999993 | 6100 | 10 | 85.14385150812066 | 5067.75 | 0 | 152.24999999999272 | 0 |  | 70.60185185185185 | 6100 | 2021 | 2 | 2021_02_Asomata_english.xlsx
5 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 45 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85 | 9200.000000000007 | 40.74 | 2328.3 | -239.99999999998545 | 600.0000000000146 | 840 | 10.5 | 81.27796234772978 | 572.7 | 0 | 87.3000000000145 | 60 |  | 9.722222222222221 | 840 | 2021 | 2 | 2021_02_Asomata_english.xlsx
6 | 35 | 270 | 305 | 0 | 0 | 3 | 305 | 80 | 0.9500000000043656 | 6.899999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 |  | 6 | 84.2 | 7280.000000000014 | 40.96 | 2585.7 | -1919.9999999999936 | 1160.5000000000064 | 3080.5 | 10.1 | 86.09872835624795 | 904.05 | 0 | 256.4500000000064 | 0 |  | 35.65393518518518 | 3080.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
7 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.2 | 7280.000000000014 | 41.08 | 2726.1 | 0 | 4570.157894736842 | 707 | 10.1 | 86.09872835624795 | 4555.2 | 3863.1578947368416 | 74.95789473684181 | 60 |  | 8.18287037037037 | 707 | 2021 | 2 | 2021_02_Asomata_english.xlsx
8 | 25 | 155 | 180 | 0 | 0 | 4 | 180 | 45 | 0.5 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 83.95 | 6680.000000000014 | 41.32 | 3006.9 | -600 | 1774.3589743589744 | 1800 | 10 | 87.47794994040524 | 1646.4 | 574.3589743589744 | 127.9589743589745 | 0 |  | 20.833333333333332 | 1800 | 2021 | 2 | 2021_02_Asomata_english.xlsx
9 | 155 | 130 | 285 | 0 | 0 | 3 | 285 | 70 | 4.099999999998545 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 83.75 | 6200.000000000007 | 41.63 | 3369.6 | -480.00000000000637 | 4137.861702127653 | 2878.5 | 10.1 | 87.02673860200392 | 4161 | 1739.3617021276596 | 36.86170212765319 | 60 |  | 33.31597222222222 | 2878.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
10 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.9 | 8960.00000000002 | 41.3 | 2983.5 | 2760.0000000000127 | 7251.5425531915025 | 2257.5 | 10.5 | 81.46742146742146 | 7161.3 | 2234.0425531914893 | 150.24255319150325 | 60 |  | 26.12847222222222 | 2257.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
11 | 375 | 345 | 720 | 0 | 0 | 4 | 720 | 110 | 8.400000000001455 | 7.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 |  | 11 | 85 | 9200.000000000007 | 41.77 | 3533.4 | 239.99999999998727 | 11050 | 7560 | 10.5 | 81.27796234772978 | 11059.5 | 3250 | 90.49999999998727 | 100 |  | 87.5 | 7560 | 2021 | 2 | 2021_02_Asomata_english.xlsx
12 | 0 | 405 | 405 | 0 | 0 | 3 | 405 | 55 | 0 | 9.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85.1 | 9439.999999999993 | 41.23 | 2901.6 | 239.99999999998545 | 6625.836787564753 | 4090.5 | 10.1 | 84.30084307734718 | 6556.2 | 2295.336787564767 | 69.63678756475292 | 0 |  | 47.34375 | 4090.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
13 | 705 | 80 | 785 | 0 | 0 | 4 | 785 | 110 | 13.099999999998545 | 1.6500000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85.1 | 9439.999999999993 | 41.8 | 3568.5 | 0 | 8886.649214659687 | 7850 | 10 | 85.14385150812066 | 8627.1 | 1036.6492146596859 | 259.5492146596862 | 0 |  | 90.85648148148148 | 7850 | 2021 | 2 | 2021_02_Asomata_english.xlsx
14 | 715 | 0 | 715 | 0 | 0 | 4 | 715 | 55 | 13.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 1 | 0 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 14 | 83.7 | 6080.000000000014 | 41.67 | 3416.4 | -3359.999999999979 | 6965.9670329670535 | 7293 | 10.2 | 86.27686086424978 | 6881 | 3032.967032967033 | 144.96703296705346 | 60 |  | 84.40972222222221 | 7293 | 2021 | 2 | 2021_02_Asomata_english.xlsx
15 | 650 | 0 | 650 | 0 | 0 | 3 | 650 | 55 | 12.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 0 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 15 | 83.55 | 5720 | 41.59 | 3322.8 | -360.00000000001364 | 9340.464480874303 | 6695 | 10.3 | 85.74766628112113 | 9338 | 3005.464480874317 | 62.46448087430326 | 60 |  | 77.48842592592594 | 6695 | 2021 | 2 | 2021_02_Asomata_english.xlsx
16 | 225 | 415 | 640 | 0 | 0 | 4 | 640 | 55 | 4.5 | 12.25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0 | 1 | 2 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 16 | 84.1 | 7039.999999999993 | 41.75 | 3510 | 1319.9999999999927 | 9848.51612903225 | 6464 | 10.1 | 86.3032383998495 | 9828 | 2064.516129032258 | 80.51612903225032 | 60 |  | 74.81481481481481 | 6464 | 2021 | 2 | 2021_02_Asomata_english.xlsx
17 | 850 | 0 | 850 | 0 | 0 | 3 | 850 | 55 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.75 | 6200.000000000007 | 41.69 | 3439.8 | -839.9999999999854 | 10813.040540540555 | 8712.5 | 10.25 | 85.7531765736819 | 10885 | 2940.5405405405404 | 28.040540540554503 | 100 |  | 100.83912037037037 | 8712.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
18 | 785 | 305 | 1090 | 0 | 0 | 4 | 1090 | 85 | 16.299999999995634 | 6.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.4 | 7760.00000000002 | 41.64 | 3381.3 | 1560.0000000000127 | 17079.468085106397 | 11445 | 10.5 | 82.42812219227312 | 17056.8 | 4074.468085106383 | 82.66808510639748 | 60 |  | 132.46527777777777 | 11445 | 2021 | 2 | 2021_02_Asomata_english.xlsx
19 | 705 | 0 | 705 | 0 | 0 | 3 | 705 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.9 | 8960.00000000002 | 41.68 | 3428.1 | 1200 | 8320.5 | 7120.5 | 10.1 | 84.6938540007847 | 7999.4 | 0 | 321.09999999999945 | 0 |  | 82.41319444444444 | 7120.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
20 | 245 | 450 | 695 | 0 | 0 | 4 | 695 | 90 | 5.25 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 0 | 1 | 1 | Ασυμμετρία θέσεως πόλων Δ/Κ Μον. ΝοΙΙ (Ρ25) | 20 | 84.85 | 8839.999999999993 | 41.63 | 3369.6 | -120.00000000002728 | 6899.499999999973 | 7019.5 | 10.1 | 84.79267996811352 | 6762 | 0 | 137.49999999997362 | 0 |  | 81.24421296296296 | 7019.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
21 | 255 | 275 | 530 | 0 | 0 | 4 | 530 | 55 | 4.650000000001455 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.9 | 6560.00000000002 | 41.6 | 3334.5 | -2279.9999999999727 | 5290.095531914922 | 5479.67 | 10.339 | 84.7106479370809 | 5219.5 | 2090.425531914894 | 70.59553191492068 | 0 |  | 63.42210648148148 | 5479.67 | 2021 | 2 | 2021_02_Asomata_english.xlsx
22 | 265 | 360 | 625 | 0 | 0 | 4 | 625 | 90 | 5.05000000000291 | 7.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 84.05 | 6920 | 41.61 | 3346.2 | 359.99999999998 | 6672.49999999998 | 6312.5 | 10.1 | 86.4058581839159 | 6608.2 | 0 | 64.29999999998017 | 0 |  | 73.0613425925926 | 6312.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
23 | 0 | 365 | 365 | 0 | 0 | 3 | 365 | 55 | 0 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 83.7 | 6080.000000000014 | 41.05 | 2691 | -839.9999999999864 | 2919.500000000014 | 3759.5 | 10.3 | 85.43922143838327 | 2954 | 0 | 25.500000000014097 | 60 |  | 43.51273148148149 | 3759.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
24 | 20 | 385 | 405 | 0 | 0 | 3 | 405 | 55 | 0.5499999999956344 | 8.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84 | 6800.000000000007 | 41.34 | 3030.3 | 719.9999999999936 | 5584.202127659568 | 4252.5 | 10.5 | 83.21315192743764 | 5481.2 | 611.7021276595744 | 103.00212765956803 | 0 |  | 49.21875 | 4252.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
25 | 515 | 160 | 675 | 0 | 0 | 4 | 675 | 80 | 12 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 83.95 | 6680.000000000014 | 41.1 | 2749.5 | -119.99999999999363 | 6963.457446808517 | 6817.5 | 10.1 | 86.61183162416361 | 6902 | 265.9574468085106 | 91.45744680851658 | 30 |  | 78.90625 | 6817.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
26 | 35 | 220 | 255 | 0 | 0 | 3 | 255 | 50 | 0.9000000000014552 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.35 | 7639.999999999993 | 41.05 | 2691 | 959.9999999999791 | 3535.499999999979 | 2575.5 | 10.1 | 85.79377418261309 | 3571.92 | 0 | 23.57999999997901 | 60 |  | 29.80902777777778 | 2575.5 | 2021 | 2 | 2021_02_Asomata_english.xlsx
27 | 245 | 45 | 290 | 0 | 0 | 2 | 290 | 65 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 83.45 | 5480.000000000014 | 41.05 | 2691 | -2159.999999999979 | 1955.1702127659782 | 2929 | 10.1 | 87.65660643265774 | 1958.4 | 1186.1702127659573 | 56.77021276597816 | 60 |  | 33.90046296296296 | 2929 | 2021 | 2 | 2021_02_Asomata_english.xlsx
28 | 0 | 280 | 280 | 0 | 0 | 3 | 280 | 55 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.05 | 4520 | 41.18 | 2843.1 | -960.0000000000136 | 3298.851063829774 | 2828 | 10.1 | 88.51075119692239 | 3297.6 | 1430.8510638297873 | 61.25106382977356 | 60 |  | 32.73148148148148 | 2828 | 2021 | 2 | 2021_02_Asomata_english.xlsx
1 | 280 | 135 | 415 | 0 | 0 | 3 | 415 | 55 | 6.599999999998545 | 3.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 1 | 84 | 6800.000000000007 | 41.75 | 3510 | 2280.0000000000073 | 6554.500000000007 | 4274.5 | 10.3 | 84.82894128525196 | 6555.2 | 0 | 59.30000000000746 | 60 |  | 49.473379629629626 | 4274.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
2 | 325 | 405 | 730 | 0 | 0 | 3 | 730 | 95 | 7 | 8.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 2 | 85.15 | 9560.00000000002 | 41.71 | 3463.2 | 2760.0000000000127 | 10133 | 7373 | 10.1 | 84.20315959753565 | 10020.11 | 0 | 112.89000000001215 | 0 |  | 85.33564814814815 | 7373 | 2021 | 3 | 2021_03_Asomata_english.xlsx
3 | 300 | 0 | 300 | 0 | 0 | 2 | 300 | 55 | 6.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.85 | 8839.999999999993 | 41.22 | 2889.9 | -720.0000000000273 | 2873.8297872340154 | 3030 | 10.1 | 84.79267996811352 | 2744.8 | 563.8297872340426 | 189.02978723401566 | 60 |  | 35.06944444444444 | 3030 | 2021 | 3 | 2021_03_Asomata_english.xlsx
4 | 0 | 255 | 255 | 0 | 0 | 3 | 255 | 55 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.6 | 8239.999999999993 | 41.24 | 2913.3 | -600 | 1975.5 | 2575.5 | 10.1 | 85.29028959233953 | 1890.7 | 0 | 144.8 | 60 |  | 29.80902777777778 | 2575.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
5 | 175 | 70 | 245 | 0 | 0 | 3 | 245 | 70 | 4.049999999995634 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 5 | 84.65 | 8360.00000000002 | 41.46 | 3170.7 | 120.00000000002728 | 2631.2500000000273 | 2511.25 | 10.25 | 83.94361364481169 | 2595 | 0 | 36.250000000027285 | 0 |  | 29.06539351851852 | 2511.25 | 2021 | 3 | 2021_03_Asomata_english.xlsx
6 | 85 | 260 | 345 | 0 | 0 | 3 | 345 | 85 | 1.8500000000058208 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 6 | 84.1 | 7039.999999999993 | 41.19 | 2854.8 | -1320.0000000000273 | 2164.4999999999727 | 3484.5 | 10.1 | 86.3032383998495 | 2114 | 0 | 110.49999999997272 | 60 |  | 40.329861111111114 | 3484.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
7 | 300 | 225 | 525 | 0 | 0 | 2 | 525 | 55 | 6.599999999998545 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.55 | 8120 | 41.6 | 3334.5 | 1080.0000000000073 | 6382.500000000007 | 5302.5 | 10.1 | 85.39051319938106 | 6029.8 | 0 | 352.700000000008 | 0 |  | 61.37152777777778 | 5302.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
8 | 0 | 180 | 180 | 0 | 0 | 3 | 180 | 55 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.6 | 8239.999999999993 | 41.2 | 2866.5 | 119.99999999999272 | 1937.9999999999927 | 1818 | 10.1 | 85.29028959233953 | 1888.6 | 0 | 109.39999999999281 | 60 |  | 21.041666666666668 | 1818 | 2021 | 3 | 2021_03_Asomata_english.xlsx
9 | 230 | 0 | 230 | 0 | 0 | 3 | 230 | 55 | 6.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.45 | 7880.000000000014 | 41.5 | 3217.5 | -359.9999999999791 | 1963.000000000021 | 2323 | 10.1 | 85.5916687075068 | 1905.3 | 0 | 117.70000000002096 | 60 |  | 26.886574074074073 | 2323 | 2021 | 3 | 2021_03_Asomata_english.xlsx
10 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.5 | 8000.000000000007 | 41.2 | 2866.5 | 119.99999999999363 | 1988.4999999999936 | 1868.5 | 10.1 | 85.49097262667443 | 1890.7 | 0 | 157.7999999999936 | 60 |  | 21.62615740740741 | 1868.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
11 | 235 | 0 | 235 | 0 | 0 | 2 | 235 | 55 | 4.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.35 | 7639.999999999993 | 41.01 | 2644.2 | -360.00000000001455 | 2013.4999999999854 | 2373.5 | 10.1 | 85.79377418261309 | 1898 | 0 | 175.49999999998545 | 60 |  | 27.471064814814813 | 2373.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
12 | 0 | 265 | 265 | 0 | 0 | 3 | 265 | 55 | 0 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84 | 6800.000000000007 | 41.05 | 2691 | -839.9999999999854 | 1902.7500000000146 | 2742.75 | 10.35 | 84.41913963653094 | 1905.3 | 0 | 57.4500000000146 | 60 |  | 31.744791666666668 | 2742.75 | 2021 | 3 | 2021_03_Asomata_english.xlsx
13 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 55 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.2 | 7280.000000000014 | 41.12 | 2772.9 | 480.00000000000637 | 1995.0000000000064 | 1515 | 10.1 | 86.09872835624795 | 1949.1 | 0 | 105.90000000000646 | 60 |  | 17.53472222222222 | 1515 | 2021 | 3 | 2021_03_Asomata_english.xlsx
14 | 40 | 200 | 240 | 0 | 0 | 2 | 240 | 70 | 0.6999999999970896 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.7 | 8480.000000000015 | 41.1 | 2749.5 | 1200 | 3624 | 2424 | 10.1 | 85.09054652537853 | 3529.8 | 0 | 94.20000000000073 | 0 |  | 28.055555555555557 | 2424 | 2021 | 3 | 2021_03_Asomata_english.xlsx
15 | 150 | 130 | 280 | 0 | 0 | 3 | 280 | 110 | 3.099999999998545 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.1 | 7039.999999999993 | 41.32 | 3006.9 | -1440.0000000000218 | 1387.9999999999782 | 2828 | 10.1 | 86.3032383998495 | 1408.9 | 0 | 39.09999999997831 | 60 |  | 32.73148148148148 | 2828 | 2021 | 3 | 2021_03_Asomata_english.xlsx
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.15 | 7160.00000000002 | 41.42 | 3123.9 | 120.00000000002728 | 813.0000000000273 | 693 | 9.9 | 87.9422936362438 | 675 | 0 | 138.00000000002728 | 0 |  | 8.020833333333334 | 693 | 2021 | 3 | 2021_03_Asomata_english.xlsx
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.15 | 7160.00000000002 | 41.42 | 3123.9 | 0 | 757.5 | 757.5 | 10.1 | 86.20086207909047 | 682.5 | 0 | 75 | 0 |  | 8.76736111111111 | 757.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
18 | 0 | 75 | 75 | 0 | 0 | 2 | 75 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.2 | 7280.000000000014 | 41.45 | 3159 | 119.99999999999363 | 877.4999999999936 | 757.5 | 10.1 | 86.09872835624795 | 683.55 | 0 | 193.94999999999368 | 0 |  | 8.76736111111111 | 757.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.2 | 7280.000000000014 | 41.48 | 3194.1 | 0 | 707 | 707 | 10.1 | 86.09872835624795 | 664.3 | 0 | 42.7 | 0 |  | 8.18287037037037 | 707 | 2021 | 3 | 2021_03_Asomata_english.xlsx
20 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 84.2 | 7280.000000000014 | 41.23 | 2901.6 | 0 | 707 | 707 | 10.1 | 86.09872835624795 | 668.85 | 0 | 38.15 | 0 |  | 8.18287037037037 | 707 | 2021 | 3 | 2021_03_Asomata_english.xlsx
21 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.25 | 7400.000000000007 | 41.33 | 3018.6 | 119.99999999999363 | 819.9999999999936 | 700 | 10 | 86.85680473372781 | 703 | 0 | 116.99999999999363 | 0 |  | 8.101851851851851 | 700 | 2021 | 3 | 2021_03_Asomata_english.xlsx
22 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 55 | 0 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.25 | 7400.000000000007 | 41.56 | 3287.7 | 0 | 858.5 | 858.5 | 10.1 | 85.99683637002754 | 680.8 | 0 | 177.7 | 0 |  | 9.936342592592593 | 858.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
23 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 45 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.2 | 7280.000000000014 | 41.55 | 3276 | -119.99999999999363 | 738.5000000000064 | 858.5 | 10.1 | 86.09872835624795 | 658.6 | 0 | 79.90000000000634 | 0 |  | 9.936342592592593 | 858.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
24 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.2 | 7280.000000000014 | 41.43 | 3135.6 | 0 | 757.5 | 757.5 | 10.1 | 86.09872835624795 | 649.7 | 0 | 107.8 | 0 |  | 8.76736111111111 | 757.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
25 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 35 | 2.5 | 0.049999999995634425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.2 | 7280.000000000014 | 41.65 | 3393 | 0 | 900 | 900 | 10 | 86.95971563981043 | 694.6 | 0 | 205.4 | 0 |  | 10.416666666666666 | 900 | 2021 | 3 | 2021_03_Asomata_english.xlsx
26 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.2 | 7280.000000000014 | 41.47 | 3182.4 | 0 | 757.5 | 757.5 | 10.1 | 86.09872835624795 | 660 | 0 | 97.5 | 0 |  | 8.76736111111111 | 757.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
27 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.3 | 7520 | 41.45 | 3159 | 239.99999999998636 | 989.9999999999864 | 750 | 10 | 86.75413711583924 | 727.5 | 0 | 262.49999999998636 | 0 |  | 8.680555555555555 | 750 | 2021 | 3 | 2021_03_Asomata_english.xlsx
28 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.3 | 7520 | 41.63 | 3369.6 | 0 | 757.5 | 757.5 | 10.1 | 85.89518526320718 | 697.5 | 0 | 60 | 0 |  | 8.76736111111111 | 757.5 | 2021 | 3 | 2021_03_Asomata_english.xlsx
29 | 90 | 0 | 90 | 0 | 0 | 2 | 90 | 35 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.3 | 7520 | 41.63 | 3369.6 | 0 | 909 | 909 | 10.1 | 85.89518526320718 | 685.4 | 0 | 223.6 | 0 |  | 10.520833333333334 | 909 | 2021 | 3 | 2021_03_Asomata_english.xlsx
30 | 0 | 70 | 70 | 0 | 0 | 2 | 70 | 35 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.35 | 7639.999999999993 | 41.58 | 3311.1 | 119.99999999999272 | 812.9999999999927 | 693 | 9.9 | 87.52698174185778 | 660 | 0 | 152.99999999999272 | 0 |  | 8.020833333333334 | 693 | 2021 | 3 | 2021_03_Asomata_english.xlsx
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.35 | 7639.999999999993 | 41.42 | 3123.9 | 0 | 750 | 750 | 10 | 86.65171192443921 | 642.4 | 0 | 107.6 | 0 |  | 8.680555555555555 | 750 | 2021 | 3 | 2021_03_Asomata_english.xlsx
1 | 165 | 0 | 165 | 0 | 0 | 3 | 165 | 40 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.2 | 7280.000000000014 | 41.3 | 2983.5 | -359.9999999999791 | 1306.500000000021 | 1666.5 | 10.1 | 86.09872835624795 | 1253.3 | 0 | 53.200000000020964 | 0 |  | 19.288194444444443 | 1666.5 | 2021 | 4 | 2021_04_Asomata_english.xlsx
2 | 20 | 100 | 120 | 0 | 0 | 2 | 120 | 75 | 0.4500000000043656 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84 | 6800.000000000007 | 41.25 | 2925 | -480.00000000000637 | 719.9999999999936 | 1200 | 10 | 87.37380952380953 | 656.85 | 0 | 63.14999999999361 | 0 |  | 13.88888888888889 | 1200 | 2021 | 4 | 2021_04_Asomata_english.xlsx
3 | 85 | 0 | 85 | 0 | 0 | 2 | 85 | 35 | 2.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84 | 6800.000000000007 | 41.42 | 3123.9 | 0 | 850 | 850 | 10 | 87.37380952380953 | 660 | 0 | 190 | 0 |  | 9.837962962962964 | 850 | 2021 | 4 | 2021_04_Asomata_english.xlsx
4 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 82.9 | 4180.000000000013 | 41.64 | 3381.3 | -2619.9999999999945 | 896.8393782383473 | 750 | 10 | 89.72371638141809 | 639.45 | 2766.839378238342 | 257.3893782383474 | 0 |  | 8.680555555555555 | 750 | 2021 | 4 | 2021_04_Asomata_english.xlsx
5 | 95 | 0 | 95 | 0 | 0 | 2 | 95 | 50 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 82.5 | 3300 | 41.2 | 2866.5 | -880.0000000000127 | 834.8191489361575 | 959.5 | 10.1 | 89.71274905268304 | 846.8 | 755.3191489361702 | 48.019148936157535 | 60 |  | 11.105324074074074 | 959.5 | 2021 | 4 | 2021_04_Asomata_english.xlsx
6 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83.95 | 6680.000000000014 | 40.9 | 2515.5 | 3380.0000000000136 | 4073.0000000000136 | 693 | 9.9 | 88.36156559636892 | 3937.5 | 0 | 135.50000000001364 | 0 |  | 8.020833333333334 | 693 | 2021 | 4 | 2021_04_Asomata_english.xlsx
7 | 80 | 0 | 80 | 0 | 0 | 2 | 80 | 35 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 83.95 | 6680.000000000014 | 41.15 | 2808 | 0 | 792 | 792 | 9.9 | 88.36156559636892 | 675 | 0 | 117 | 0 |  | 9.166666666666666 | 792 | 2021 | 4 | 2021_04_Asomata_english.xlsx
8 | 0 | 75 | 75 | 0 | 0 | 2 | 75 | 35 | 0 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.05 | 6920 | 41.35 | 3042 | 239.99999999998636 | 997.4999999999864 | 757.5 | 10.1 | 86.4058581839159 | 788.4 | 0 | 209.09999999998638 | 0 |  | 8.76736111111111 | 757.5 | 2021 | 4 | 2021_04_Asomata_english.xlsx
9 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 82.65 | 3630.0000000000127 | 41.29 | 2971.8 | -3289.9999999999873 | 784.0212765957576 | 707 | 10.1 | 89.38170569824509 | 722.7 | 3367.021276595745 | 61.321276595757695 | 0 |  | 8.18287037037037 | 707 | 2021 | 4 | 2021_04_Asomata_english.xlsx
10 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.8 | 6320 | 41.29 | 2971.8 | 2689.9999999999873 | 3389.9999999999873 | 700 | 10 | 87.79186602870813 | 3307.5 | 0 | 82.49999999998727 | 0 |  | 8.101851851851851 | 700 | 2021 | 4 | 2021_04_Asomata_english.xlsx
11 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.8 | 6320 | 41.25 | 2925 | 0 | 750 | 750 | 10 | 87.79186602870813 | 655.6 | 0 | 94.4 | 0 |  | 8.680555555555555 | 750 | 2021 | 4 | 2021_04_Asomata_english.xlsx
12 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 83.8 | 6320 | 41.25 | 2925 | 0 | 750 | 750 | 10 | 87.79186602870813 | 664.4 | 0 | 85.6 | 0 |  | 8.680555555555555 | 750 | 2021 | 4 | 2021_04_Asomata_english.xlsx
13 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 45 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 83.9 | 6560.00000000002 | 41.5 | 3217.5 | 240.00000000002 | 1440.00000000002 | 1200 | 10 | 87.58233890214795 | 1237.5 | 0 | 202.50000000002 | 0 |  | 13.88888888888889 | 1200 | 2021 | 4 | 2021_04_Asomata_english.xlsx
14 | 200 | 80 | 280 | 0 | 0 | 2 | 280 | 90 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 83.7 | 6080.000000000014 | 41.5 | 3217.5 | -480.00000000000637 | 2319.9999999999936 | 2800 | 10 | 88.00239808153478 | 2138.6 | 0 | 181.39999999999372 | 0 |  | 32.407407407407405 | 2800 | 2021 | 4 | 2021_04_Asomata_english.xlsx
15 | 135 | 0 | 135 | 0 | 0 | 2 | 135 | 40 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.5 | 8000.000000000007 | 40.73 | 2316.599999999995 | 1919.9999999999936 | 3269.9999999999936 | 1350 | 10 | 86.34588235294117 | 3027.55 | 0 | 242.44999999999345 | 0 |  | 15.625 | 1350 | 2021 | 4 | 2021_04_Asomata_english.xlsx
16 | 140 | 0 | 140 | 0 | 0 | 2 | 140 | 55 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 83.9 | 6560.00000000002 | 41.13 | 2784.6 | -1439.9999999999873 | -25.999999999987267 | 1414 | 10.1 | 86.71518703182966 | 0 | 0 | 34.00000000001273 | 60 |  | 16.36574074074074 | 1414 | 2021 | 4 | 2021_04_Asomata_english.xlsx
17 | 125 | 20 | 145 | 0 | 0 | 3 | 145 | 80 | 3.7399999999979627 | 0.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84 | 6800.000000000007 | 41.38 | 3077.1 | 239.99999999998727 | 1689.9999999999873 | 1450 | 10 | 87.37380952380953 | 1457.8 | 0 | 232.19999999998709 | 0 |  | 16.78240740740741 | 1450 | 2021 | 4 | 2021_04_Asomata_english.xlsx
18 | 0 | 135 | 135 | 0 | 0 | 2 | 135 | 45 | 0 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.1 | 7039.999999999993 | 41.64 | 3381.3 | 239.99999999998545 | 1576.4999999999854 | 1336.5 | 9.9 | 88.04673816550302 | 1376.4 | 0 | 200.09999999998536 | 0 |  | 15.46875 | 1336.5 | 2021 | 4 | 2021_04_Asomata_english.xlsx
19 | 100 | 20 | 120 | 0 | 0 | 2 | 120 | 45 | 2.610000000000582 | 0.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 84.3 | 7520 | 41.19 | 2854.8 | 480.0000000000073 | 1680.0000000000073 | 1200 | 10 | 86.75413711583924 | 1447.95 | 0 | 232.05000000000746 | 0 |  | 13.88888888888889 | 1200 | 2021 | 4 | 2021_04_Asomata_english.xlsx
20 | 25 | 175 | 200 | 0 | 0 | 3 | 200 | 70 | 0.6500000000014552 | 4.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 20 | 83.4 | 5360.00000000002 | 41.65 | 3393 | -2159.99999999998 | -49.99999999997999 | 2110 | 10.55 | 84.01904892735305 | 0 | 0 | 50.00000000002001 | 100 |  | 24.421296296296298 | 2110 | 2021 | 4 | 2021_04_Asomata_english.xlsx
21 | 85 | 0 | 85 | 0 | 0 | 2 | 85 | 45 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 83.4 | 5360.00000000002 | 41.5 | 3217.5 | 0 | 850 | 850 | 10 | 88.64009661835748 | 710.4 | 0 | 139.6 | 0 |  | 9.837962962962964 | 850 | 2021 | 4 | 2021_04_Asomata_english.xlsx
22 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.4 | 5360.00000000002 | 41.52 | 3240.9 | 0 | 858.5 | 858.5 | 10.1 | 87.76247189936385 | 683.55 | 0 | 174.95 | 0 |  | 9.936342592592593 | 858.5 | 2021 | 4 | 2021_04_Asomata_english.xlsx
23 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.8 | 6320 | 41.19 | 2854.8 | 959.99999999998 | 1659.99999999998 | 700 | 10 | 87.79186602870813 | 1467.65 | 0 | 192.3499999999799 | 0 |  | 8.101851851851851 | 700 | 2021 | 4 | 2021_04_Asomata_english.xlsx
24 | 0 | 105 | 105 | 0 | 0 | 2 | 105 | 35 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84 | 6800.000000000007 | 41.3 | 2983.5 | 480.0000000000073 | 1540.5000000000073 | 1060.5 | 10.1 | 86.50872230080151 | 1474.6 | 0 | 65.90000000000737 | 0 |  | 12.274305555555555 | 1060.5 | 2021 | 4 | 2021_04_Asomata_english.xlsx
25 | 135 | 0 | 135 | 0 | 0 | 3 | 135 | 45 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.2 | 7280.000000000014 | 41.6 | 3334.5 | 480.00000000000637 | 1809.7500000000064 | 1329.75 | 9.85 | 88.28397526884307 | 1507.5 | 0 | 302.25000000000637 | 0 |  | 15.390625 | 1329.75 | 2021 | 4 | 2021_04_Asomata_english.xlsx
26 | 0 | 150 | 150 | 0 | 0 | 2 | 150 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.3 | 7520 | 41.68 | 3428.1 | 239.99999999998636 | 1754.9999999999864 | 1515 | 10.1 | 85.89518526320718 | 1500 | 0 | 254.99999999998636 | 0 |  | 17.53472222222222 | 1515 | 2021 | 4 | 2021_04_Asomata_english.xlsx
27 | 165 | 25 | 190 | 0 | 0 | 2 | 190 | 80 | 4.069999999999709 | 0.6100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 84.4 | 7760.00000000002 | 42.05 | 3861 | 240.00000000002 | 2140.00000000002 | 1900 | 10 | 86.54952830188678 | 2100 | 0 | 40.00000000002001 | 0 |  | 21.99074074074074 | 1900 | 2021 | 4 | 2021_04_Asomata_english.xlsx
28 | 0 | 160 | 160 | 0 | 0 | 2 | 160 | 45 | 0 | 4.040000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.55 | 8120 | 41.62 | 3357.9 | 359.99999999998 | 1959.99999999998 | 1600 | 10 | 86.24441833137486 | 1897.5 | 0 | 62.49999999997999 | 0 |  | 18.51851851851852 | 1600 | 2021 | 4 | 2021_04_Asomata_english.xlsx
29 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 45 | 4.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.75 | 8600.000000000007 | 41.55 | 3276 | 480.0000000000073 | 2130.0000000000073 | 1650 | 10 | 85.84093567251462 | 1879.95 | 0 | 310.05000000000723 | 60 |  | 19.09722222222222 | 1650 | 2021 | 4 | 2021_04_Asomata_english.xlsx
30 | 0 | 170 | 170 | 0 | 0 | 2 | 170 | 50 | 0 | 4.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.95 | 9080.000000000015 | 41.35 | 3042 | 480.0000000000073 | 2180.0000000000073 | 1700 | 10 | 85.44121071012806 | 1917.7 | 0 | 322.30000000000723 | 60 |  | 19.675925925925927 | 1700 | 2021 | 4 | 2021_04_Asomata_english.xlsx
1 | 230 | 75 | 305 | 0 | 0 | 2 | 305 | 100 | 4.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.62 | 8288.000000000018 | 41.59 | 3322.8 | -791.9999999999964 | 2258 | 3050 | 10 | 86.10276865321444 | 1983.6 | 0 | 274.40000000000373 | 0 |  | 35.300925925925924 | 3050 | 2021 | 5 | 2021_05_Asomata_english.xlsx
2 | 0 | 60 | 60 | 0 | 0 | 2 | 60 | 45 | 0 | 1.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.15 | 9560.00000000002 | 40.82 | 2421.9 | 1272 | 4844.29319371728 | 588 | 9.8 | 86.78080734031734 | 4748.95 | 2984.2931937172775 | 95.34319371727997 | 0 |  | 6.805555555555555 | 588 | 2021 | 5 | 2021_05_Asomata_english.xlsx
3 | 290 | 155 | 445 | 0 | 0 | 3 | 445 | 110 | 6.099999999998545 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.2 | 7280.000000000014 | 41.66 | 3404.7 | -2280.0000000000064 | 2214.4999999999936 | 4494.5 | 10.1 | 86.09872835624795 | 1887 | 0 | 327.49999999999363 | 0 |  | 52.019675925925924 | 4494.5 | 2021 | 5 | 2021_05_Asomata_english.xlsx
4 | 0 | 180 | 180 | 0 | 0 | 2 | 180 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.1 | 7039.999999999993 | 41.42 | 3123.9 | -240.00000000002092 | 2375.872340425511 | 1818 | 10.1 | 86.3032383998495 | 2314.1 | 797.8723404255319 | 121.77234042551117 | 60 |  | 21.041666666666668 | 1818 | 2021 | 5 | 2021_05_Asomata_english.xlsx
5 | 220 | 20 | 240 | 0 | 0 | 2 | 240 | 95 | 4.30000000000291 | 0.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84 | 6800.000000000007 | 41.4 | 3100.5 | -239.99999999998545 | 2184.0000000000146 | 2424 | 10.1 | 86.50872230080151 | 1978.3 | 0 | 205.7000000000146 | 0 |  | 28.055555555555557 | 2424 | 2021 | 5 | 2021_05_Asomata_english.xlsx
6 | 45 | 235 | 280 | 0 | 0 | 3 | 280 | 80 | 1.5999999999985448 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 6 | 83.7 | 6080.000000000014 | 41.86 | 3638.7 | -719.9999999999936 | 2108.0000000000064 | 2828 | 10.1 | 87.13108720944037 | 2000.2 | 0 | 107.80000000000632 | 0 |  | 32.73148148148148 | 2828 | 2021 | 5 | 2021_05_Asomata_english.xlsx
7 | 200 | 125 | 325 | 0 | 0 | 2 | 325 | 109 | 4 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 83.2 | 4880.000000000014 | 41.49 | 3205.8 | -1200 | 4526.6223404255325 | 3428.75 | 10.55 | 84.42690838816544 | 4591.7 | 2297.872340425532 | 84.92234042553264 | 150 |  | 39.68460648148148 | 3428.75 | 2021 | 5 | 2021_05_Asomata_english.xlsx
8 | 0 | 325 | 325 | 0 | 0 | 3 | 325 | 51 | 0 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84 | 6800.000000000007 | 41.61 | 3346.2 | 1919.9999999999936 | 7474.751308900517 | 3282.5 | 10.1 | 86.50872230080151 | 7518.9 | 2272.2513089005233 | 15.851308900517324 | 60 |  | 37.991898148148145 | 3282.5 | 2021 | 5 | 2021_05_Asomata_english.xlsx
9 | 290 | 0 | 290 | 0 | 0 | 2 | 290 | 45 | 7.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 82.4 | 3080.0000000000127 | 41.36 | 3053.7 | -3719.9999999999945 | 5349.857890545005 | 2929 | 10.1 | 89.93481031271443 | 5299 | 6140.8578905449995 | 110.85789054500492 | 60 |  | 33.90046296296296 | 2929 | 2021 | 5 | 2021_05_Asomata_english.xlsx
10 | 0 | 450 | 450 | 0 | 0 | 2 | 450 | 55 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 82.3 | 2859.9999999999936 | 41.92 | 3708.9 | -220.0000000000191 | 4414.999999999981 | 4635 | 10.3 | 88.40733334939411 | 4454.5 | 0 | 20.4999999999809 | 60 |  | 53.645833333333336 | 4635 | 2021 | 5 | 2021_05_Asomata_english.xlsx
11 | 350 | 0 | 350 | 0 | 0 | 3 | 350 | 55 | 8.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 82.65 | 3630.0000000000127 | 41.56 | 3287.7 | 770.0000000000191 | 4305.000000000019 | 3535 | 10.1 | 89.38170569824509 | 4373.25 | 0 | 11.7500000000191 | 80 |  | 40.914351851851855 | 3535 | 2021 | 5 | 2021_05_Asomata_english.xlsx
12 | 0 | 370 | 370 | 0 | 0 | 2 | 370 | 55 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 83.35 | 5239.999999999993 | 41.6 | 3334.5 | 1609.99999999998 | 5309.99999999998 | 3700 | 10 | 88.7472793228537 | 5202.2 | 0 | 107.79999999998017 | 0 |  | 42.824074074074076 | 3700 | 2021 | 5 | 2021_05_Asomata_english.xlsx
13 | 345 | 0 | 345 | 0 | 0 | 2 | 345 | 55 | 8.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.75 | 6200.000000000007 | 41.7 | 3451.5 | 960.0000000000146 | 4444.500000000015 | 3484.5 | 10.1 | 87.02673860200392 | 4299.75 | 0 | 144.75000000001455 | 0 |  | 40.329861111111114 | 3484.5 | 2021 | 5 | 2021_05_Asomata_english.xlsx
14 | 0 | 330 | 330 | 0 | 0 | 3 | 330 | 55 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84 | 6800.000000000007 | 41.8 | 3568.5 | 600 | 3933 | 3333 | 10.1 | 86.50872230080151 | 3655.6 | 0 | 277.4 | 0 |  | 38.576388888888886 | 3333 | 2021 | 5 | 2021_05_Asomata_english.xlsx
15 | 520 | 60 | 580 | 0 | 0 | 1 | 580 | 80 | 11.880000000004657 | 1.5600000000049477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 83.6 | 5839.999999999993 | 41.73 | 3486.6 | -960.0000000000146 | 4897.999999999985 | 5858 | 10.1 | 87.34053693830923 | 4894.65 | 0 | 63.3499999999849 | 60 |  | 67.80092592592592 | 5858 | 2021 | 5 | 2021_05_Asomata_english.xlsx
16 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 45 | 0 | 10.139999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 83.4 | 5360.00000000002 | 41.57 | 3299.4 | -479.9999999999727 | 9134.212765957474 | 4444 | 10.1 | 87.76247189936385 | 9125 | 5170.212765957447 | 69.2127659574744 | 60 |  | 51.43518518518518 | 4444 | 2021 | 5 | 2021_05_Asomata_english.xlsx
17 | 455 | 0 | 455 | 0 | 0 | 4 | 455 | 47 | 9.919999999998254 | 0 | 0 | 0 | 0 | 0 | 15.5 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 17 | 84 | 6800.000000000007 | 41.59 | 3322.8 | 1439.9999999999873 | 7187.332460732971 | 4595.5 | 10.1 | 86.50872230080151 | 6982.5 | 1151.8324607329844 | 264.8324607329714 | 60 |  | 53.188657407407405 | 4595.5 | 2021 | 5 | 2021_05_Asomata_english.xlsx
18 | 510 | 0 | 510 | 0 | 0 | 3 | 510 | 55 | 10.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 3 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 18 | 84.5 | 8000.000000000007 | 41.98 | 3779.1 | 1200 | 6249 | 5049 | 9.9 | 87.21806298276887 | 6107.95 | 0 | 141.05 | 0 |  | 58.4375 | 5049 | 2021 | 5 | 2021_05_Asomata_english.xlsx
19 | 470 | 0 | 470 | 0 | 0 | 3 | 470 | 45 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 19 | 84.85 | 8839.999999999993 | 41.55 | 3276 | 839.9999999999854 | 7153.692307692293 | 4606 | 9.8 | 87.38837425285168 | 6900.8 | 1707.6923076923076 | 252.8923076922929 | 0 |  | 53.31018518518518 | 4606 | 2021 | 5 | 2021_05_Asomata_english.xlsx
20 | 540 | 0 | 540 | 0 | 0 | 2 | 540 | 55 | 11.349999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 20 | 83.9 | 6560.00000000002 | 41.75 | 3510 | -2279.9999999999727 | 4773.4468085106655 | 5346 | 9.9 | 88.46700899206864 | 4591.7 | 1707.4468085106382 | 181.7468085106657 | 0 |  | 61.875 | 5346 | 2021 | 5 | 2021_05_Asomata_english.xlsx
21 | 460 | 0 | 460 | 0 | 0 | 2 | 460 | 55 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 21 | 82.5 | 3300 | 41.56 | 3287.7 | -3260.00000000002 | 4901.95744680849 | 4646 | 10.1 | 89.71274905268304 | 4956.7 | 3515.95744680851 | 45.257446808490386 | 100 |  | 53.773148148148145 | 4646 | 2021 | 5 | 2021_05_Asomata_english.xlsx
22 | 460 | 0 | 460 | 0 | 0 | 2 | 460 | 46 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 22 | 82.8 | 3959.9999999999936 | 41.5 | 3217.5 | 659.9999999999936 | 5305.999999999994 | 4646 | 10.1 | 89.0530964861192 | 5292.5 | 0 | 73.49999999999363 | 60 |  | 53.773148148148145 | 4646 | 2021 | 5 | 2021_05_Asomata_english.xlsx
23 | 480 | 0 | 480 | 0 | 0 | 2 | 480 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 23 | 82.7 | 3740.0000000000064 | 41.72 | 3474.9 | -219.99999999998727 | 4628.000000000013 | 4848 | 10.1 | 89.27190016298927 | 4627 | 0 | 61.00000000001273 | 60 |  | 56.111111111111114 | 4848 | 2021 | 5 | 2021_05_Asomata_english.xlsx
24 | 575 | 0 | 575 | 0 | 0 | 3 | 575 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 24 | 85.35 | 10040 | 41.8 | 3568.5 | 6299.999999999986 | 12107.5 | 5807.5 | 10.1 | 83.81467904575926 | 12070.59 | 0 | 36.9099999999853 | 0 |  | 67.21643518518519 | 5807.5 | 2021 | 5 | 2021_05_Asomata_english.xlsx
25 | 660 | 0 | 660 | 0 | 0 | 2 | 660 | 55 | 12.94999999999709 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 25 | 84.9 | 8960.00000000002 | 41.89 | 3673.8 | -1079.9999999999727 | 5586.000000000027 | 6666 | 10.1 | 84.6938540007847 | 5396 | 0 | 190.00000000002728 | 0 |  | 77.15277777777777 | 6666 | 2021 | 5 | 2021_05_Asomata_english.xlsx
26 | 490 | 0 | 490 | 0 | 0 | 2 | 490 | 50 | 9.910000000003492 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 26 | 84 | 6800.000000000007 | 41.51 | 3229.2 | -2160.0000000000127 | 6241.127659574456 | 4949 | 10.1 | 86.50872230080151 | 6307.2 | 3452.1276595744685 | 33.92765957445499 | 100 |  | 57.280092592592595 | 4949 | 2021 | 5 | 2021_05_Asomata_english.xlsx
27 | 495 | 0 | 495 | 0 | 0 | 3 | 495 | 50 | 9.989999999997963 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 27 | 84.3 | 7520 | 41.39 | 3088.8 | 719.9999999999927 | 5595.749999999993 | 4875.75 | 9.85 | 88.07526610745101 | 5426.4 | 0 | 169.3499999999931 | 0 |  | 56.432291666666664 | 4875.75 | 2021 | 5 | 2021_05_Asomata_english.xlsx
28 | 485 | 0 | 485 | 0 | 0 | 2 | 485 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 28 | 84.3 | 7520 | 41.28 | 2960.1 | 0 | 8542.117021276596 | 4898.5 | 10.1 | 85.89518526320718 | 8452.8 | 3643.6170212765956 | 149.31702127659628 | 60 |  | 56.695601851851855 | 4898.5 | 2021 | 5 | 2021_05_Asomata_english.xlsx
29 | 540 | 0 | 540 | 0 | 0 | 3 | 540 | 55 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 29 | 84.35 | 7639.999999999993 | 41.81 | 3580.2 | 119.99999999999272 | 7882.510638297865 | 5454 | 10.1 | 85.79377418261309 | 7818.3 | 2308.5106382978724 | 124.21063829786544 | 60 |  | 63.125 | 5454 | 2021 | 5 | 2021_05_Asomata_english.xlsx
30 | 520 | 0 | 520 | 0 | 0 | 2 | 520 | 55 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 30 | 84.6 | 8239.999999999993 | 41.87 | 3650.4 | 600 | 5800 | 5200 | 10 | 86.14319248826293 | 5710.95 | 0 | 89.05000000000109 | 0 |  | 60.18518518518518 | 5200 | 2021 | 5 | 2021_05_Asomata_english.xlsx
31 | 540 | 0 | 540 | 0 | 0 | 2 | 540 | 55 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 31 | 84.65 | 8360.00000000002 | 41.9 | 3685.5 | 120.00000000002728 | 5520.000000000027 | 5400 | 10 | 86.04220398593199 | 5445.8 | 0 | 74.20000000002801 | 0 |  | 62.5 | 5400 | 2021 | 5 | 2021_05_Asomata_english.xlsx
1 | 570 | 0 | 570 | 0 | 0 | 2 | 570 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 1 | 85.05 | 9320 | 41.8 | 3568.5 | 959.99999999998 | 6659.99999999998 | 5700 | 10 | 85.24274099883856 | 6405 | 0 | 254.99999999998 | 0 |  | 65.97222222222223 | 5700 | 2021 | 6 | 2021_06_Asomata_english.xlsx
2 | 575 | 0 | 575 | 0 | 0 | 3 | 575 | 55 | 11.150000000001455 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 2 | 85.25 | 9800.000000000007 | 41.9 | 3685.5 | 480.0000000000073 | 6115.000000000007 | 5635 | 9.8 | 86.5801580747906 | 5850 | 0 | 265.0000000000073 | 0 |  | 65.2199074074074 | 5635 | 2021 | 6 | 2021_06_Asomata_english.xlsx
3 | 620 | 0 | 620 | 0 | 0 | 2 | 620 | 55 | 11.75 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 3 | 84.9 | 8960.00000000002 | 41.92 | 3708.9 | -839.9999999999873 | 5360.000000000013 | 6200 | 10 | 85.54079254079252 | 5117.3 | 0 | 242.70000000001255 | 0 |  | 71.75925925925925 | 6200 | 2021 | 6 | 2021_06_Asomata_english.xlsx
4 | 515 | 0 | 515 | 0 | 0 | 3 | 515 | 54 | 10 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 4 | 85.1 | 9439.999999999993 | 41.73 | 3486.6 | 479.9999999999727 | 5578.499999999973 | 5098.5 | 9.9 | 86.0038904122431 | 5340 | 0 | 238.49999999997272 | 0 |  | 59.010416666666664 | 5098.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
5 | 505 | 0 | 505 | 0 | 0 | 3 | 505 | 55 | 9.599999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 5 | 84.55 | 8120 | 41.71 | 3463.2 | -1319.9999999999927 | 5828.37234042554 | 5100.5 | 10.1 | 85.39051319938106 | 5768.16 | 2047.872340425532 | 60.21234042553988 | 0 |  | 59.03356481481482 | 5100.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
6 | 520 | 0 | 520 | 0 | 0 | 2 | 520 | 55 | 9.80000000000291 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 6 | 83.75 | 6200.000000000007 | 41.92 | 3708.9 | -1919.9999999999927 | 8520.17204301076 | 5252 | 10.1 | 87.02673860200392 | 8477 | 5188.1720430107525 | 103.17204301075981 | 60 |  | 60.78703703703704 | 5252 | 2021 | 6 | 2021_06_Asomata_english.xlsx
7 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 13.599999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 7 | 84.6 | 8239.999999999993 | 42.07 | 3884.4 | 2039.9999999999854 | 8623.499999999985 | 6583.5 | 9.9 | 87.01332574572012 | 8354.72 | 0 | 268.7799999999861 | 0 |  | 76.19791666666667 | 6583.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
8 | 555 | 0 | 555 | 0 | 0 | 2 | 555 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 8 | 84.75 | 8600.000000000007 | 41.85 | 3627 | 360.00000000001455 | 7680.525906735766 | 5605.5 | 10.1 | 84.9910254183313 | 7414.8 | 1715.0259067357513 | 265.7259067357654 | 0 |  | 64.87847222222223 | 5605.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
9 | 435 | 0 | 435 | 0 | 0 | 3 | 435 | 50 | 9 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 9 | 84.7 | 8480.000000000015 | 41.7 | 3451.5 | -119.99999999999272 | 7938.393617021284 | 4393.5 | 10.1 | 85.09054652537853 | 7832.9 | 3664.8936170212764 | 165.49361702128408 | 60 |  | 50.85069444444444 | 4393.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
10 | 200 | 240 | 440 | 0 | 0 | 3 | 440 | 50 | 4 | 6.44999999999709 | 0 | 0 | 0 | 0 | 17.5 | 0 | 0 | 0 | 1 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 10 | 84.95 | 9080.000000000015 | 41.57 | 3299.4 | 600 | 8431.434554973821 | 4444 | 10.1 | 84.59525812883966 | 8329.3 | 3387.434554973822 | 102.13455497382165 | 0 |  | 51.43518518518518 | 4444 | 2021 | 6 | 2021_06_Asomata_english.xlsx
11 | 455 | 360 | 815 | 0 | 0 | 4 | 815 | 100 | 10.150000000001455 | 8.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 85.4 | 10160 | 41.9 | 3685.5 | 1080.0000000000055 | 11684.556994818658 | 8231.5 | 10.1 | 83.71811835561435 | 11632.5 | 2373.056994818653 | 52.056994818658495 | 0 |  | 95.27199074074075 | 8231.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
12 | 205 | 245 | 450 | 0 | 0 | 3 | 450 | 55 | 4.55000000000291 | 5.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.9 | 8960.00000000002 | 41.95 | 3744 | -1200 | 3345 | 4545 | 10.1 | 84.6938540007847 | 3082.5 | 0 | 262.5 | 0 |  | 52.604166666666664 | 4545 | 2021 | 6 | 2021_06_Asomata_english.xlsx
13 | 440 | 0 | 440 | 0 | 0 | 3 | 440 | 50 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.15 | 9560.00000000002 | 42 | 3802.5 | 600 | 5000 | 4400 | 10 | 85.045191193511 | 4666.4 | 0 | 333.6 | 0 |  | 50.925925925925924 | 4400 | 2021 | 6 | 2021_06_Asomata_english.xlsx
14 | 20 | 490 | 510 | 0 | 0 | 3 | 510 | 85 | 0.5499999999956344 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.2 | 7280.000000000014 | 41.75 | 3510 | -2280.0000000000064 | 6722.063829787227 | 5151 | 10.1 | 86.09872835624795 | 6745.2 | 3851.0638297872338 | 36.86382978722759 | 60 |  | 59.61805555555556 | 5151 | 2021 | 6 | 2021_06_Asomata_english.xlsx
15 | 460 | 0 | 460 | 0 | 0 | 4 | 460 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.7 | 6080.000000000014 | 42.1 | 3919.5 | -1200 | 4520.468085106383 | 4646 | 10.1 | 87.13108720944037 | 4482.2 | 1074.468085106383 | 68.2680851063833 | 30 |  | 53.773148148148145 | 4646 | 2021 | 6 | 2021_06_Asomata_english.xlsx
16 | 135 | 440 | 575 | 0 | 0 | 3 | 575 | 110 | 12.700000000004366 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.1 | 7039.999999999993 | 41.91 | 3697.2 | 959.9999999999791 | 6767.499999999979 | 5807.5 | 10.1 | 86.3032383998495 | 6585.6 | 0 | 181.89999999997963 | 0 |  | 67.21643518518519 | 5807.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
17 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 55 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.2 | 7280.000000000014 | 41.7 | 3451.5 | 240.00000000002092 | 4790.000000000021 | 4550 | 10 | 86.95971563981043 | 4681.6 | 0 | 108.40000000002146 | 0 |  | 52.66203703703704 | 4550 | 2021 | 6 | 2021_06_Asomata_english.xlsx
18 | 20 | 445 | 465 | 0 | 0 | 3 | 465 | 70 | 0.2999999999956344 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.25 | 7400.000000000007 | 41.7 | 3451.5 | 119.99999999999363 | 4769.999999999994 | 4650 | 10 | 86.85680473372781 | 4527.6 | 0 | 242.39999999999327 | 0 |  | 53.81944444444444 | 4650 | 2021 | 6 | 2021_06_Asomata_english.xlsx
19 | 340 | 110 | 450 | 0 | 0 | 4 | 450 | 100 | 6.5 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.35 | 7639.999999999993 | 41.5 | 3217.5 | 239.99999999998545 | 4739.999999999985 | 4500 | 10 | 86.65171192443921 | 4595.4 | 0 | 144.5999999999849 | 0 |  | 52.083333333333336 | 4500 | 2021 | 6 | 2021_06_Asomata_english.xlsx
20 | 0 | 460 | 460 | 0 | 0 | 3 | 460 | 50 | 0 | 9.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.95 | 6680.000000000014 | 41.5 | 3217.5 | -959.9999999999791 | 3686.000000000021 | 4646 | 10.1 | 86.61183162416361 | 3706.2 | 0 | 39.8000000000211 | 60 |  | 53.773148148148145 | 4646 | 2021 | 6 | 2021_06_Asomata_english.xlsx
21 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 50 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.15 | 7160.00000000002 | 41.5 | 3217.5 | 480.00000000000637 | 5030.000000000006 | 4550 | 10 | 87.06287069988136 | 4787.8 | 0 | 242.20000000000618 | 0 |  | 52.66203703703704 | 4550 | 2021 | 6 | 2021_06_Asomata_english.xlsx
22 | 40 | 445 | 485 | 0 | 0 | 3 | 485 | 90 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.4 | 7760.00000000002 | 41.65 | 3393 | 600 | 6550.583333333333 | 4898.5 | 10.1 | 85.69260227909582 | 6416.55 | 1052.0833333333333 | 134.03333333333376 | 0 |  | 56.695601851851855 | 4898.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
23 | 475 | 215 | 690 | 0 | 0 | 4 | 690 | 110 | 10.849999999998545 | 5.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.65 | 8360.00000000002 | 41.84 | 3615.3 | 600 | 7500 | 6900 | 10 | 86.04220398593199 | 7368.05 | 0 | 131.95 | 0 |  | 79.86111111111111 | 6900 | 2021 | 6 | 2021_06_Asomata_english.xlsx
24 | 25 | 585 | 610 | 0 | 0 | 3 | 610 | 70 | 0.25 | 11.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 85 | 9200.000000000007 | 41.74 | 3498.3 | 839.9999999999873 | 6939.999999999987 | 6100 | 10 | 85.34186046511628 | 6606.5 | 0 | 333.49999999998727 | 0 |  | 70.60185185185185 | 6100 | 2021 | 6 | 2021_06_Asomata_english.xlsx
25 | 630 | 195 | 825 | 0 | 0 | 3 | 825 | 80 | 13.650000000001455 | 5.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.55 | 8120 | 41.65 | 3393 | -1080.0000000000073 | 7252.499999999993 | 8332.5 | 10.1 | 85.39051319938106 | 7234.3 | 0 | 78.19999999999254 | 60 |  | 96.44097222222223 | 8332.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
26 | 75 | 655 | 730 | 0 | 0 | 4 | 730 | 89 | 2 | 12.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.3 | 7520 | 41.9 | 3685.5 | -600 | 6773 | 7373 | 10.1 | 85.89518526320718 | 6759.8 | 0 | 73.20000000000073 | 60 |  | 85.33564814814815 | 7373 | 2021 | 6 | 2021_06_Asomata_english.xlsx
27 | 490 | 230 | 720 | 0 | 0 | 3 | 720 | 110 | 9.950000000004366 | 4.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84 | 6800.000000000007 | 41.97 | 3767.4 | -719.9999999999927 | 6552.000000000007 | 7272 | 10.1 | 86.50872230080151 | 6461 | 0 | 151.00000000000728 | 60 |  | 84.16666666666667 | 7272 | 2021 | 6 | 2021_06_Asomata_english.xlsx
28 | 295 | 580 | 875 | 0 | 0 | 3 | 875 | 90 | 8.39999999999418 | 13.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 28 | 84.4 | 7760.00000000002 | 41.96 | 3755.7 | 960.0000000000127 | 9797.500000000013 | 8837.5 | 10.1 | 85.69260227909582 | 9803.9 | 0 | 53.6000000000131 | 60 |  | 102.28587962962963 | 8837.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
29 | 675 | 30 | 705 | 0 | 0 | 4 | 705 | 105 | 12.450000000004366 | 0.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.8 | 8720 | 41.85 | 3627 | 959.99999999998 | 8080.49999999998 | 7120.5 | 10.1 | 84.89173683723513 | 7861 | 0 | 219.49999999998 | 0 |  | 82.41319444444444 | 7120.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
30 | 130 | 555 | 685 | 0 | 0 | 0 | 685 | 110 | 2.3799999999973807 | 10.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 85.1 | 9439.999999999993 | 42 | 3802.5 | 719.9999999999927 | 7638.499999999993 | 6918.5 | 10.1 | 84.30084307734718 | 7515.12 | 0 | 123.37999999999283 | 0 |  | 80.07523148148148 | 6918.5 | 2021 | 6 | 2021_06_Asomata_english.xlsx
1 | 740 | 0 | 740 | 0 | 0 | 6 | 740 | 54 | 13.970000000001164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.95 | 9080.000000000015 | 41.94 | 3732.3 | -359.9999999999782 | 7114.000000000022 | 7474 | 10.1 | 84.59525812883966 | 6660.3 | 0 | 453.70000000002165 | 0 |  | 86.50462962962963 | 7474 | 2021 | 7 | 2021_07_Asomata_english.xlsx
2 | 340 | 365 | 705 | 0 | 0 | 4 | 705 | 55 | 6.400000000001455 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.8 | 8720 | 42.01 | 3814.2 | -360.00000000001455 | 6760.499999999985 | 7120.5 | 10.1 | 84.89173683723513 | 6681.1 | 0 | 79.399999999986 | 0 |  | 82.41319444444444 | 7120.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
3 | 630 | 30 | 660 | 0 | 0 | 3 | 660 | 60 | 12 | 0.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.6 | 8239.999999999993 | 41.68 | 3428.1 | -480.0000000000073 | 6185.999999999993 | 6666 | 10.1 | 85.29028959233953 | 5985.3 | 0 | 200.69999999999345 | 0 |  | 77.15277777777777 | 6666 | 2021 | 7 | 2021_07_Asomata_english.xlsx
4 | 0 | 665 | 665 | 0 | 0 | 3 | 665 | 55 | 0 | 12.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.25 | 7400.000000000007 | 41.89 | 3673.8 | -839.9999999999854 | 5876.500000000015 | 6716.5 | 10.1 | 85.99683637002754 | 5894.78 | 0 | 41.72000000001481 | 60 |  | 77.73726851851852 | 6716.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
5 | 580 | 120 | 700 | 0 | 0 | 4 | 700 | 80 | 12.099999999998545 | 3.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85.1 | 9439.999999999993 | 41.94 | 3732.3 | 2039.9999999999854 | 9109.999999999985 | 7070 | 10.1 | 84.30084307734718 | 8954.4 | 0 | 155.599999999984 | 0 |  | 81.82870370370371 | 7070 | 2021 | 7 | 2021_07_Asomata_english.xlsx
6 | 240 | 620 | 860 | 0 | 0 | 3 | 860 | 80 | 6.599999999998545 | 13.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.2 | 7280.000000000014 | 42.09 | 3907.8 | -2159.999999999979 | 6526.000000000021 | 8686 | 10.1 | 86.09872835624795 | 6514.2 | 0 | 71.8000000000211 | 60 |  | 100.5324074074074 | 8686 | 2021 | 7 | 2021_07_Asomata_english.xlsx
7 | 670 | 0 | 670 | 0 | 0 | 3 | 670 | 55 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.7 | 8480.000000000015 | 42.08 | 3896.1 | 1200 | 7900 | 6700 | 10 | 85.94145199063232 | 7722.6 | 0 | 177.40000000000146 | 0 |  | 77.54629629629629 | 6700 | 2021 | 7 | 2021_07_Asomata_english.xlsx
8 | 555 | 470 | 1025 | 0 | 0 | 0 | 1025 | 90 | 11.580000000001746 | 9.639999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84 | 6800.000000000007 | 42.03 | 3837.6 | -1680.0000000000073 | 8672.499999999993 | 10352.5 | 10.1 | 86.50872230080151 | 8683.2 | 0 | 49.299999999991996 | 60 |  | 119.82060185185185 | 10352.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
9 | 370 | 325 | 695 | 0 | 0 | 7 | 695 | 55 | 6.989999999997963 | 5.959999999999127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 83.9 | 6560.00000000002 | 42 | 3802.5 | -239.99999999998727 | 6779.500000000013 | 7019.5 | 10.1 | 86.71518703182966 | 6718.74 | 0 | 60.76000000001295 | 0 |  | 81.24421296296296 | 7019.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
10 | 290 | 435 | 725 | 0 | 0 | 3 | 725 | 90 | 5.510000000002037 | 8.819999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.8 | 6320 | 42 | 3802.5 | -240.00000000002 | 7082.49999999998 | 7322.5 | 10.1 | 86.9226396323843 | 7094.12 | 0 | 48.3799999999801 | 60 |  | 84.7511574074074 | 7322.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
11 | 720 | 0 | 720 | 0 | 0 | 4 | 720 | 55 | 14.019999999996799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.2 | 7280.000000000014 | 42.05 | 3861 | 960.0000000000136 | 8124.000000000013 | 7164 | 9.95 | 87.39669913548786 | 7923.3 | 0 | 200.70000000001346 | 0 |  | 82.91666666666666 | 7164 | 2021 | 7 | 2021_07_Asomata_english.xlsx
12 | 20 | 740 | 760 | 0 | 0 | 3 | 760 | 110 | 0.5 | 14.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 84.3 | 7520 | 42 | 3802.5 | 239.99999999998636 | 7915.999999999986 | 7676 | 10.1 | 85.89518526320718 | 7829.25 | 0 | 146.74999999998545 | 60 |  | 88.8425925925926 | 7676 | 2021 | 7 | 2021_07_Asomata_english.xlsx
13 | 735 | 0 | 735 | 0 | 0 | 3 | 735 | 55 | 14.069999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.4 | 7760.00000000002 | 41.96 | 3755.7 | 240.00000000002 | 7663.50000000002 | 7423.5 | 10.1 | 85.69260227909582 | 7497.1 | 0 | 166.40000000002055 | 0 |  | 85.92013888888889 | 7423.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
14 | 30 | 895 | 925 | 0 | 0 | 3 | 925 | 75 | 0.43000000000029104 | 16.9800000000032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.45 | 7880.000000000014 | 42 | 3802.5 | 119.99999999999363 | 9277.499999999993 | 9157.5 | 9.9 | 87.32079332786046 | 9050.24 | 0 | 227.25999999999294 | 0 |  | 105.98958333333333 | 9157.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
15 | 735 | 0 | 735 | 0 | 0 | 3 | 735 | 55 | 14.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.55 | 8120 | 41.93 | 3720.6 | 239.99999999998636 | 7663.499999999986 | 7423.5 | 10.1 | 85.39051319938106 | 7467.9 | 0 | 195.59999999998672 | 0 |  | 85.92013888888889 | 7423.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
16 | 15 | 735 | 750 | 0 | 0 | 3 | 750 | 55 | 0.1500000000014552 | 14.169999999998254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Αποκατάσταση βλάβης Απ/Ζ 16 από ΑΔΜΗΕ | 16 | 84.8 | 8720 | 41.93 | 3720.6 | 600 | 8175 | 7575 | 10.1 | 84.89173683723513 | 8108.1 | 0 | 126.9 | 60 |  | 87.67361111111111 | 7575 | 2021 | 7 | 2021_07_Asomata_english.xlsx
17 | 425 | 775 | 1200 | 0 | 0 | 3 | 1200 | 100 | 8.299999999995634 | 15.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.1 | 7039.999999999993 | 41.9 | 3685.5 | -1680.0000000000073 | 10200 | 11880 | 9.9 | 88.04673816550302 | 10088.6 | 0 | 111.39999999999236 | 0 |  | 137.5 | 11880 | 2021 | 7 | 2021_07_Asomata_english.xlsx
18 | 0 | 740 | 740 | 0 | 0 | 3 | 740 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.35 | 7639.999999999993 | 42.07 | 3884.4 | 600 | 8074 | 7474 | 10.1 | 85.79377418261309 | 8087.76 | 0 | 46.24000000000069 | 60 |  | 86.50462962962963 | 7474 | 2021 | 7 | 2021_07_Asomata_english.xlsx
19 | 760 | 0 | 760 | 0 | 0 | 3 | 760 | 55 | 14.569999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 85 | 9200.000000000007 | 42 | 3802.5 | 1560.0000000000146 | 9160.000000000015 | 7600 | 10 | 85.34186046511628 | 9030.1 | 0 | 129.9000000000142 | 0 |  | 87.96296296296296 | 7600 | 2021 | 7 | 2021_07_Asomata_english.xlsx
20 | 80 | 715 | 795 | 0 | 0 | 3 | 795 | 80 | 2.0800000000017462 | 14.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.95 | 9080.000000000015 | 42.05 | 3861 | -119.99999999999272 | 7830.000000000007 | 7950 | 10 | 85.44121071012806 | 7453.3 | 0 | 376.700000000008 | 0 |  | 92.01388888888889 | 7950 | 2021 | 7 | 2021_07_Asomata_english.xlsx
21 | 675 | 115 | 790 | 0 | 0 | 3 | 790 | 70 | 15.950000000004366 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.75 | 8600.000000000007 | 42.05 | 3861 | -480.0000000000073 | 7459.499999999994 | 7939.5 | 10.05 | 85.41386634081056 | 7444.4 | 0 | 15.099999999993088 | 0 |  | 91.89236111111113 | 7939.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
22 | 40 | 810 | 850 | 0 | 0 | 3 | 850 | 70 | 0.5499999999956344 | 15.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.35 | 7639.999999999993 | 42 | 3802.5 | -960.0000000000146 | 7624.999999999985 | 8585 | 10.1 | 85.79377418261309 | 7539.6 | 0 | 85.39999999998508 | 0 |  | 99.36342592592592 | 8585 | 2021 | 7 | 2021_07_Asomata_english.xlsx
23 | 750 | 0 | 750 | 0 | 0 | 3 | 750 | 55 | 16.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.45 | 7880.000000000014 | 42.05 | 3861 | 240.00000000002092 | 7815.000000000021 | 7575 | 10.1 | 85.5916687075068 | 7587.78 | 0 | 227.22000000002117 | 0 |  | 87.67361111111111 | 7575 | 2021 | 7 | 2021_07_Asomata_english.xlsx
24 | 0 | 715 | 715 | 0 | 0 | 3 | 715 | 55 | 0 | 13.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.35 | 7639.999999999993 | 42.05 | 3861 | -240.00000000002092 | 6981.499999999979 | 7221.5 | 10.1 | 85.79377418261309 | 6956 | 0 | 25.49999999997908 | 0 |  | 83.58217592592592 | 7221.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
25 | 700 | 0 | 700 | 0 | 0 | 3 | 700 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.05 | 6920 | 42.05 | 3861 | -719.9999999999927 | 6350.000000000007 | 7070 | 10.1 | 86.4058581839159 | 6336.4 | 0 | 73.60000000000764 | 60 |  | 81.82870370370371 | 7070 | 2021 | 7 | 2021_07_Asomata_english.xlsx
26 | 0 | 710 | 710 | 0 | 0 | 3 | 710 | 55 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 83.9 | 6560.00000000002 | 42.05 | 3861 | -359.99999999998 | 6811.00000000002 | 7171 | 10.1 | 86.71518703182966 | 6716 | 0 | 95.00000000002001 | 0 |  | 82.99768518518519 | 7171 | 2021 | 7 | 2021_07_Asomata_english.xlsx
27 | 720 | 0 | 720 | 0 | 0 | 3 | 720 | 55 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 83.75 | 6200.000000000007 | 42.05 | 3861 | -360.00000000001273 | 6911.999999999987 | 7272 | 10.1 | 87.02673860200392 | 6921.53 | 0 | 50.46999999998661 | 60 |  | 84.16666666666667 | 7272 | 2021 | 7 | 2021_07_Asomata_english.xlsx
28 | 0 | 705 | 705 | 0 | 0 | 3 | 705 | 55 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 83.7 | 6080.000000000014 | 41.91 | 3697.2 | -119.99999999999363 | 7000.500000000006 | 7120.5 | 10.1 | 87.13108720944037 | 7066.4 | 0 | 34.10000000000673 | 100 |  | 82.41319444444444 | 7120.5 | 2021 | 7 | 2021_07_Asomata_english.xlsx
29 | 655 | 115 | 770 | 0 | 0 | 3 | 770 | 70 | 14 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 83.9 | 6560.00000000002 | 42.05 | 3861 | 480.00000000000637 | 12737.97297297298 | 8085 | 10.5 | 83.41175133537901 | 12789 | 4172.972972972973 | 18.972972972980642 | 70 |  | 93.57638888888889 | 8085 | 2021 | 7 | 2021_07_Asomata_english.xlsx
30 | 175 | 675 | 850 | 0 | 0 | 2 | 850 | 85 | 4.5 | 13.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.2 | 7280.000000000014 | 42 | 3802.5 | 719.9999999999936 | 11060.319148936163 | 8585 | 10.1 | 86.09872835624795 | 10934.55 | 1755.3191489361702 | 125.76914893616413 | 0 |  | 99.36342592592592 | 8585 | 2021 | 7 | 2021_07_Asomata_english.xlsx
31 | 750 | 0 | 750 | 0 | 0 | 3 | 750 | 55 | 9.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.3 | 7520 | 42.02 | 3825.9 | 239.99999999998636 | 7739.999999999986 | 7500 | 10 | 86.75413711583924 | 7599.8 | 0 | 140.19999999998527 | 0 |  | 86.80555555555556 | 7500 | 2021 | 7 | 2021_07_Asomata_english.xlsx
1 | 135 | 605 | 740 | 0 | 0 | 4 | 740 | 109 | 2.2000000000043656 | 11.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 83.85 | 6439.999999999993 | 41.92 | 3708.9 | -1080.0000000000073 | 6393.999999999993 | 7474 | 10.1 | 86.81878940582232 | 6356.6 | 0 | 97.39999999999236 | 60 |  | 86.50462962962963 | 7474 | 2021 | 8 | 2021_08_Asomata_english.xlsx
2 | 170 | 690 | 860 | 0 | 0 | 2 | 860 | 90 | 4.599999999998545 | 13.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 2 | 83.35 | 5239.999999999993 | 41.96 | 3755.7 | -1200 | 7916 | 9116 | 10.6 | 83.72384841778651 | 7931.25 | 0 | 104.75 | 120 |  | 105.50925925925925 | 9116 | 2021 | 8 | 2021_08_Asomata_english.xlsx
3 | 720 | 345 | 1065 | 0 | 0 | 3 | 1065 | 110 | 14 | 7.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.7 | 8480.000000000015 | 41.93 | 3720.6 | 3240.000000000022 | 13996.5 | 10756.5 | 10.1 | 85.09054652537853 | 13862.7 | 0 | 133.8000000000211 | 0 |  | 124.49652777777777 | 10756.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
4 | 445 | 930 | 1375 | 0 | 0 | 3 | 1375 | 110 | 10.5 | 19.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 83.5 | 5600.000000000007 | 42 | 3802.5 | -2880.0000000000073 | 11530 | 14410 | 10.48 | 84.3764370458935 | 11523.3 | 0 | 66.69999999999345 | 60 |  | 166.78240740740742 | 14410 | 2021 | 8 | 2021_08_Asomata_english.xlsx
5 | 600 | 265 | 865 | 0 | 0 | 3 | 865 | 110 | 12.19999999999709 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 5 | 83.75 | 6200.000000000007 | 41.9 | 3685.5 | 600 | 9336.5 | 8736.5 | 10.1 | 87.02673860200392 | 9081.2 | 0 | 255.3000000000011 | 0 |  | 101.11689814814815 | 8736.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
6 | 0 | 645 | 645 | 0 | 0 | 3 | 645 | 55 | 0 | 12.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.15 | 7160.00000000002 | 41.9 | 3685.5 | 960.0000000000127 | 10233.464088397803 | 6837 | 10.6 | 82.13478367913336 | 10267.4 | 2436.46408839779 | 66.06408839780124 | 100 |  | 79.13194444444444 | 6837 | 2021 | 8 | 2021_08_Asomata_english.xlsx
7 | 650 | 0 | 650 | 0 | 0 | 3 | 650 | 55 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 7 | 84.4 | 7760.00000000002 | 41.88 | 3662.1 | 600 | 9443.947368421053 | 6565 | 10.1 | 85.69260227909582 | 9301.8 | 2278.9473684210525 | 142.1473684210523 | 0 |  | 75.98379629629629 | 6565 | 2021 | 8 | 2021_08_Asomata_english.xlsx
8 | 0 | 745 | 745 | 0 | 0 | 3 | 745 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.1 | 7039.999999999993 | 42.01 | 3814.2 | -720.0000000000273 | 6804.499999999973 | 7524.5 | 10.1 | 86.3032383998495 | 6717.6 | 0 | 86.89999999997235 | 0 |  | 87.08912037037037 | 7524.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
9 | 590 | 115 | 705 | 0 | 0 | 3 | 705 | 70 | 14 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 85 | 9200.000000000007 | 41.98 | 3779.1 | 2160.0000000000146 | 9280.500000000015 | 7120.5 | 10.1 | 84.49689154962007 | 9173.58 | 0 | 106.92000000001462 | 0 |  | 82.41319444444444 | 7120.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
10 | 245 | 645 | 890 | 0 | 0 | 3 | 890 | 110 | 6.400000000001455 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.1 | 9439.999999999993 | 41.96 | 3755.7 | 239.99999999998545 | 10622.782383419675 | 8989 | 10.1 | 84.30084307734718 | 10552.4 | 1393.782383419689 | 70.38238341967372 | 0 |  | 104.03935185185185 | 8989 | 2021 | 8 | 2021_08_Asomata_english.xlsx
11 | 630 | 275 | 905 | 0 | 0 | 3 | 905 | 104 | 14.769999999996799 | 7.169999999998254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.6 | 8239.999999999993 | 41.77 | 3533.4 | -1200 | 7804.75 | 9004.75 | 9.95 | 86.57607285252556 | 7561.56 | 0 | 243.19 | 0 |  | 104.22164351851852 | 9004.75 | 2021 | 8 | 2021_08_Asomata_english.xlsx
12 | 0 | 580 | 580 | 0 | 0 | 3 | 580 | 55 | 0 | 11.480000000003201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 12 | 83.9 | 6560.00000000002 | 41.45 | 3159 | -1679.9999999999727 | 7548.967741935511 | 5858 | 10.1 | 86.71518703182966 | 7581 | 3370.967741935484 | 27.967741935511185 | 60 |  | 67.80092592592592 | 5858 | 2021 | 8 | 2021_08_Asomata_english.xlsx
13 | 625 | 0 | 625 | 0 | 0 | 2 | 625 | 55 | 11.580000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.05 | 6920 | 41.83 | 3603.6 | 359.99999999998 | 10151.2234042553 | 6312.5 | 10.1 | 86.4058581839159 | 10257.52 | 3478.723404255319 | 13.703404255298665 | 120 |  | 73.0613425925926 | 6312.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
14 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 55 | 0 | 12.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.85 | 8839.999999999993 | 41.75 | 3510 | 1919.9999999999927 | 8269.999999999993 | 6350 | 10 | 85.64060676779464 | 8187.55 | 0 | 82.44999999999163 | 0 |  | 73.49537037037037 | 6350 | 2021 | 8 | 2021_08_Asomata_english.xlsx
15 | 0 | 630 | 630 | 0 | 0 | 3 | 630 | 55 | 0 | 12.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.65 | 8360.00000000002 | 41.69 | 3439.8 | -479.9999999999727 | 5883.000000000027 | 6363 | 10.1 | 85.19030097617029 | 5848.68 | 0 | 34.320000000026994 | 0 |  | 73.64583333333333 | 6363 | 2021 | 8 | 2021_08_Asomata_english.xlsx
16 | 45 | 650 | 695 | 0 | 0 | 3 | 695 | 80 | 1.0500000000029104 | 12.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.15 | 7160.00000000002 | 41.98 | 3779.1 | -1200 | 9597.148936170213 | 7228 | 10.4 | 83.71429874988593 | 9709.7 | 3569.148936170213 | 7.448936170212619 | 120 |  | 83.6574074074074 | 7228 | 2021 | 8 | 2021_08_Asomata_english.xlsx
17 | 415 | 145 | 560 | 0 | 0 | 3 | 560 | 54 | 8.099999999998545 | 3.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.7 | 8480.000000000015 | 41.33 | 3018.6 | 1319.9999999999945 | 6863.9999999999945 | 5544 | 9.9 | 86.80954746528516 | 6587.52 | 0 | 276.479999999995 | 0 |  | 64.16666666666667 | 5544 | 2021 | 8 | 2021_08_Asomata_english.xlsx
18 | 0 | 790 | 790 | 0 | 0 | 3 | 790 | 55 | 0 | 15.35000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84 | 6800.000000000007 | 41.85 | 3627 | -1680.0000000000073 | 6219.999999999993 | 7900 | 10 | 87.37380952380953 | 5977.5 | 0 | 242.49999999999272 | 0 |  | 91.43518518518519 | 7900 | 2021 | 8 | 2021_08_Asomata_english.xlsx
19 | 695 | 0 | 695 | 0 | 0 | 3 | 695 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.15 | 7160.00000000002 | 42.05 | 3861 | 360.00000000001273 | 7379.500000000013 | 7019.5 | 10.1 | 86.20086207909047 | 7326 | 0 | 53.50000000001273 | 0 |  | 81.24421296296296 | 7019.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
20 | 0 | 700 | 700 | 0 | 0 | 3 | 700 | 55 | 0 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 83.75 | 6200.000000000007 | 42.02 | 3825.9 | -960.0000000000127 | 6109.999999999987 | 7070 | 10.1 | 87.02673860200392 | 6097.5 | 0 | 12.499999999987267 | 0 |  | 81.82870370370371 | 7070 | 2021 | 8 | 2021_08_Asomata_english.xlsx
21 | 690 | 0 | 690 | 0 | 0 | 3 | 690 | 55 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 82.45 | 3190.0000000000064 | 41.92 | 3708.9 | -3010 | 4338.5 | 7348.5 | 10.65 | 85.18486278196579 | 4312 | 0 | 86.49999999999909 | 60 |  | 85.05208333333333 | 7348.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
22 | 0 | 605 | 605 | 0 | 0 | 2 | 605 | 55 | 0 | 11.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 81.9 | 1980.0000000000125 | 41.76 | 3521.7 | -1209.9999999999939 | 5750.872340425538 | 6413 | 10.6 | 86.76644441291909 | 5817 | 547.8723404255319 | 33.872340425537914 | 100 |  | 74.22453703703704 | 6413 | 2021 | 8 | 2021_08_Asomata_english.xlsx
23 | 685 | 0 | 685 | 0 | 0 | 3 | 685 | 55 | 13.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 82.05 | 2309.9999999999936 | 42 | 3802.5 | 329.9999999999811 | 7727.999999999982 | 7398 | 10.8 | 84.84070837379201 | 7797.9 | 0 | 10.099999999981264 | 80 |  | 85.625 | 7398 | 2021 | 8 | 2021_08_Asomata_english.xlsx
24 | 0 | 550 | 550 | 0 | 0 | 3 | 550 | 54 | 0 | 11.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 82.6 | 3519.9999999999873 | 41.92 | 3708.9 | 1209.9999999999936 | 6957.499999999994 | 5747.5 | 10.45 | 86.49444928936764 | 6986.4 | 0 | 31.099999999993997 | 60 |  | 66.52199074074075 | 5747.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
25 | 560 | 0 | 560 | 0 | 0 | 3 | 560 | 55 | 11.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 82.6 | 3519.9999999999873 | 41.88 | 3662.1 | 0 | 5852 | 5852 | 10.45 | 86.49444928936764 | 5876.5 | 0 | 35.5 | 60 |  | 67.73148148148148 | 5852 | 2021 | 8 | 2021_08_Asomata_english.xlsx
26 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 55 | 0 | 11.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 82.6 | 3519.9999999999873 | 41.9 | 3685.5 | 0 | 5951.25 | 5951.25 | 10.35 | 87.33014445158375 | 5934.9 | 0 | 16.350000000000364 | 0 |  | 68.88020833333333 | 5951.25 | 2021 | 8 | 2021_08_Asomata_english.xlsx
27 | 560 | 0 | 560 | 0 | 0 | 3 | 560 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 82.8 | 3959.9999999999936 | 41.84 | 3615.3 | 440.00000000000637 | 6096.000000000006 | 5656 | 10.1 | 89.0530964861192 | 6071.1 | 0 | 84.90000000000691 | 60 |  | 65.46296296296296 | 5656 | 2021 | 8 | 2021_08_Asomata_english.xlsx
28 | 80 | 480 | 560 | 0 | 0 | 2 | 560 | 80 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 82.6 | 3519.9999999999873 | 41.72 | 3474.9 | -440.00000000000637 | 5215.999999999994 | 5656 | 10.1 | 89.49178169048433 | 5247.44 | 0 | 28.559999999993124 | 60 |  | 65.46296296296296 | 5656 | 2021 | 8 | 2021_08_Asomata_english.xlsx
29 | 505 | 0 | 505 | 0 | 0 | 0 | 505 | 50 | 10.340000000003783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 82.6 | 3519.9999999999873 | 41.48 | 3194.1 | 0 | 5226.75 | 5226.75 | 10.35 | 87.33014445158375 | 5204.9 | 0 | 81.85000000000036 | 60 |  | 60.494791666666664 | 5226.75 | 2021 | 8 | 2021_08_Asomata_english.xlsx
30 | 0 | 505 | 505 | 0 | 0 | 6 | 505 | 51 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 82.7 | 3740.0000000000064 | 41.33 | 3018.6 | 220.0000000000191 | 5320.500000000019 | 5100.5 | 10.1 | 89.27190016298927 | 5226.8 | 0 | 93.70000000001892 | 0 |  | 59.03356481481482 | 5100.5 | 2021 | 8 | 2021_08_Asomata_english.xlsx
31 | 495 | 0 | 495 | 0 | 0 | 3 | 495 | 55 | 9.959999999999127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 83.35 | 5239.999999999993 | 41.7 | 3451.5 | 1499.9999999999864 | 6449.999999999986 | 4950 | 10 | 88.7472793228537 | 6274.5 | 0 | 175.49999999998636 | 0 |  | 57.291666666666664 | 4950 | 2021 | 8 | 2021_08_Asomata_english.xlsx
1 | 480 | 0 | 480 | 0 | 0 | 3 | 480 | 55 | 10.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 83.2 | 4880.000000000014 | 41.71 | 3463.2 | -359.9999999999791 | 4488.000000000021 | 4848 | 10.1 | 88.18850331635105 | 4453 | 0 | 95.00000000002092 | 60 |  | 56.111111111111114 | 4848 | 2021 | 9 | 2021_09_Asomata_english.xlsx
2 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 50 | 0 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 83.2 | 4880.000000000014 | 41.57 | 3299.4 | 0 | 4444 | 4444 | 10.1 | 88.18850331635105 | 4462.64 | 0 | 41.35999999999967 | 60 |  | 51.43518518518518 | 4444 | 2021 | 9 | 2021_09_Asomata_english.xlsx
3 | 455 | 30 | 485 | 0 | 0 | 2 | 485 | 80 | 9.099999999998545 | 0.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 83.3 | 5120 | 41.76 | 3521.7 | 239.99999999998636 | 5138.499999999986 | 4898.5 | 10.1 | 87.97497183132359 | 5102.7 | 0 | 95.79999999998654 | 60 |  | 56.695601851851855 | 4898.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
4 | 0 | 430 | 430 | 0 | 0 | 3 | 430 | 55 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 83.1 | 4639.999999999993 | 41.75 | 3510 | -480.0000000000073 | 3862.9999999999927 | 4343 | 10.1 | 88.40307388403076 | 3876.6 | 0 | 46.399999999992815 | 60 |  | 50.2662037037037 | 4343 | 2021 | 9 | 2021_09_Asomata_english.xlsx
5 | 390 | 0 | 390 | 0 | 0 | 3 | 390 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 83.1 | 4639.999999999993 | 41.65 | 3393 | 0 | 3939 | 3939 | 10.1 | 88.40307388403076 | 3911.05 | 0 | 87.94999999999982 | 60 |  | 45.59027777777778 | 3939 | 2021 | 9 | 2021_09_Asomata_english.xlsx
6 | 45 | 380 | 425 | 0 | 0 | 3 | 425 | 90 | 0.09999999999854481 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 82.9 | 4180.000000000013 | 41.7 | 3451.5 | -459.99999999998 | 3832.50000000002 | 4292.5 | 10.1 | 88.8353627538793 | 3822 | 0 | 70.50000000002001 | 60 |  | 49.68171296296296 | 4292.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
7 | 340 | 0 | 340 | 0 | 0 | 0 | 340 | 45 | 9.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 82.9 | 4180.000000000013 | 41.66 | 3404.7 | 0 | 3434 | 3434 | 10.1 | 88.8353627538793 | 3384 | 0 | 110 | 60 |  | 39.745370370370374 | 3434 | 2021 | 9 | 2021_09_Asomata_english.xlsx
8 | 45 | 520 | 565 | 0 | 0 | 0 | 565 | 110 | 0.7899999999935972 | 11.660000000003492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 83.1 | 4639.999999999993 | 41.59 | 3322.8 | 459.99999999998 | 6166.49999999998 | 5706.5 | 10.1 | 88.40307388403076 | 6230 | 0 | 36.49999999997999 | 100 |  | 66.04745370370371 | 5706.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
9 | 340 | 0 | 340 | 0 | 0 | 8 | 340 | 55 | 8.060000000004948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 83.55 | 5720 | 41.49 | 3205.8 | 1080.0000000000073 | 4446.000000000007 | 3366 | 9.9 | 89.21221845409572 | 4335 | 0 | 111.00000000000728 | 0 |  | 38.958333333333336 | 3366 | 2021 | 9 | 2021_09_Asomata_english.xlsx
10 | 0 | 345 | 345 | 0 | 0 | 3 | 345 | 50 | 0 | 8.179999999993015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.5 | 5600.000000000007 | 41.56 | 3287.7 | -119.99999999999272 | 3364.5000000000073 | 3484.5 | 10.1 | 87.55099606346177 | 3452.9 | 0 | 11.600000000007185 | 100 |  | 40.329861111111114 | 3484.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
11 | 160 | 135 | 295 | 0 | 0 | 3 | 295 | 85 | 3.25 | 2.710000000006403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 83.65 | 5960.00000000002 | 41.43 | 3135.6 | 360.00000000001273 | 3310.0000000000127 | 2950 | 10 | 88.1080432172869 | 3045 | 0 | 265.00000000001273 | 0 |  | 34.14351851851852 | 2950 | 2021 | 9 | 2021_09_Asomata_english.xlsx
12 | 0 | 300 | 300 | 0 | 0 | 3 | 300 | 50 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 83.7 | 6080.000000000014 | 41.34 | 3030.3 | 119.99999999999363 | 3149.9999999999936 | 3030 | 10.1 | 87.13108720944037 | 3069.4 | 0 | 80.59999999999354 | 0 |  | 35.06944444444444 | 3030 | 2021 | 9 | 2021_09_Asomata_english.xlsx
13 | 310 | 0 | 310 | 0 | 0 | 2 | 310 | 50 | 6.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.8 | 6320 | 41.3 | 2983.5 | 239.99999999998636 | 3370.9999999999864 | 3131 | 10.1 | 86.9226396323843 | 3291.8 | 0 | 79.19999999998618 | 0 |  | 36.238425925925924 | 3131 | 2021 | 9 | 2021_09_Asomata_english.xlsx
14 | 0 | 275 | 275 | 0 | 0 | 3 | 275 | 50 | 0 | 5.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.9 | 6560.00000000002 | 41.52 | 3240.9 | 240.00000000002 | 3141.25000000002 | 2901.25 | 10.55 | 83.01643497833929 | 2854.3 | 0 | 286.9500000000203 | 0 |  | 33.579282407407405 | 2901.25 | 2021 | 9 | 2021_09_Asomata_english.xlsx
15 | 150 | 140 | 290 | 0 | 0 | 3 | 290 | 50 | 3.1000000000058208 | 2.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 83.9 | 6560.00000000002 | 41.75 | 3510 | 0 | 2929 | 2929 | 10.1 | 86.71518703182966 | 2890.8 | 0 | 98.19999999999982 | 60 |  | 33.90046296296296 | 2929 | 2021 | 9 | 2021_09_Asomata_english.xlsx
16 | 20 | 330 | 350 | 0 | 0 | 3 | 350 | 65 | 0.5 | 7.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 16 | 83.9 | 6560.00000000002 | 41.76 | 3521.7 | 0 | 3535 | 3535 | 10.1 | 86.71518703182966 | 3460.2 | 0 | 134.8 | 60 |  | 40.914351851851855 | 3535 | 2021 | 9 | 2021_09_Asomata_english.xlsx
17 | 295 | 0 | 295 | 0 | 0 | 0 | 295 | 50 | 6.139999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84 | 6800.000000000007 | 41.82 | 3591.9 | 239.99999999998727 | 3219.4999999999873 | 2979.5 | 10.1 | 86.50872230080151 | 3080.6 | 0 | 198.89999999998736 | 60 |  | 34.4849537037037 | 2979.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
18 | 80 | 230 | 310 | 0 | 0 | 0 | 310 | 94 | 2.0099999999947613 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 83.55 | 5720 | 41.69 | 3439.8 | -1080.0000000000073 | 2128.4999999999927 | 3208.5 | 10.35 | 85.3334263473959 | 2191 | 0 | 37.499999999992724 | 100 |  | 37.135416666666664 | 3208.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
19 | 375 | 40 | 415 | 0 | 0 | 8 | 415 | 94 | 8.150000000001455 | 1.2699999999967986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 19 | 83.85 | 6439.999999999993 | 41.64 | 3381.3 | 719.9999999999927 | 4911.499999999993 | 4191.5 | 10.1 | 86.81878940582232 | 4883.7 | 0 | 87.7999999999929 | 60 |  | 48.51273148148148 | 4191.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
20 | 0 | 235 | 235 | 0 | 0 | 4 | 235 | 50 | 0 | 5.1600000000034925 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 20 | 83.85 | 6439.999999999993 | 41.41 | 3112.2 | 0 | 2373.5 | 2373.5 | 10.1 | 86.81878940582232 | 2378.5 | 0 | 55 | 60 |  | 27.471064814814813 | 2373.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
21 | 0 | 265 | 265 | 0 | 0 | 2 | 265 | 54 | 0 | 5.4099999999962165 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 21 | 83.85 | 6439.999999999993 | 41.56 | 3287.7 | 0 | 2769.25 | 2769.25 | 10.45 | 83.91098306208664 | 2841.6 | 0 | 27.65000000000009 | 100 |  | 32.051504629629626 | 2769.25 | 2021 | 9 | 2021_09_Asomata_english.xlsx
22 | 0 | 230 | 230 | 0 | 0 | 2 | 230 | 46 | 0 | 4.960000000006403 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 22 | 84 | 6800.000000000007 | 41.42 | 3123.9 | 360.00000000001455 | 2625.5000000000146 | 2265.5 | 9.85 | 88.70437515107567 | 2307.9 | 0 | 317.60000000001446 | 0 |  | 26.221064814814813 | 2265.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
23 | 0 | 240 | 240 | 0 | 0 | 3 | 240 | 46 | 0 | 5.399999999994179 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 23 | 84 | 6800.000000000007 | 41.46 | 3170.7 | 0 | 2424 | 2424 | 10.1 | 86.50872230080151 | 2365.2 | 0 | 58.80000000000018 | 0 |  | 28.055555555555557 | 2424 | 2021 | 9 | 2021_09_Asomata_english.xlsx
24 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 50 | 0 | 5.100000000005821 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 24 | 83.95 | 6680.000000000014 | 41.54 | 3264.3 | -119.99999999999363 | 2405.9500000000066 | 2525.95 | 10.31 | 84.84767210514572 | 2284.9 | 0 | 121.05000000000655 | 0 |  | 29.235532407407412 | 2525.95 | 2021 | 9 | 2021_09_Asomata_english.xlsx
25 | 0 | 215 | 215 | 0 | 0 | 2 | 215 | 55 | 0 | 4.25 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 25 | 84.2 | 7280.000000000014 | 41.41 | 3112.2 | 600 | 4150.276595744681 | 2279 | 10.6 | 82.03746758472681 | 4103.8 | 1271.276595744681 | 106.47659574468162 | 60 |  | 26.377314814814813 | 2279 | 2021 | 9 | 2021_09_Asomata_english.xlsx
26 | 0 | 240 | 240 | 0 | 0 | 2 | 240 | 54 | 0 | 4.69999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 26 | 84.25 | 7400.000000000007 | 41.54 | 3264.3 | 119.99999999999363 | 3650.382978723398 | 2424 | 10.1 | 85.99683637002754 | 3636 | 1106.3829787234042 | 74.38297872339808 | 60 |  | 28.055555555555557 | 2424 | 2021 | 9 | 2021_09_Asomata_english.xlsx
27 | 0 | 210 | 210 | 0 | 0 | 3 | 210 | 54 | 0 | 4.150000000001455 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 27 | 84.35 | 7639.999999999993 | 41.42 | 3123.9 | 239.99999999998545 | 4110.999999999985 | 2121 | 10.1 | 85.79377418261309 | 3905.5 | 1750 | 205.49999999998545 | 0 |  | 24.54861111111111 | 2121 | 2021 | 9 | 2021_09_Asomata_english.xlsx
28 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 54 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 28 | 84.25 | 7400.000000000007 | 41.3 | 2983.5 | -239.99999999998545 | 4869.839947089962 | 2162.75 | 10.55 | 82.32872486609271 | 4870.6 | 2947.089947089947 | 59.2399470899627 | 60 |  | 25.031828703703702 | 2162.75 | 2021 | 9 | 2021_09_Asomata_english.xlsx
29 | 0 | 210 | 210 | 0 | 0 | 2 | 210 | 55 | 0 | 4.19999999999709 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 29 | 84.3 | 7520 | 41.16 | 2819.7 | 119.99999999999272 | 4012.2765957446736 | 2121 | 10.1 | 85.89518526320718 | 3942 | 1771.276595744681 | 130.2765957446736 | 60 |  | 24.54861111111111 | 2121 | 2021 | 9 | 2021_09_Asomata_english.xlsx
30 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 55 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 30 | 84.35 | 7639.999999999993 | 41.19 | 2854.8 | 119.99999999999272 | 2291.4999999999927 | 2171.5 | 10.1 | 85.79377418261309 | 2197.75 | 0 | 153.74999999999272 | 60 |  | 25.13310185185185 | 2171.5 | 2021 | 9 | 2021_09_Asomata_english.xlsx
1 | 0 | 210 | 210 | 0 | 0 | 2 | 210 | 55 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 84.45 | 7880.000000000014 | 41.14 | 2796.3 | 240.00000000002092 | 2340.000000000021 | 2100 | 10 | 86.44758539458186 | 2184.42 | 0 | 155.58000000002085 | 0 |  | 24.305555555555557 | 2100 | 2021 | 10 | 2021_10_Asomata_english.xlsx
2 | 0 | 190 | 190 | 0 | 0 | 2 | 190 | 55 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 84.45 | 7880.000000000014 | 40.99 | 2620.8 | 0 | 2437.1565656565654 | 1871.5 | 9.85 | 87.76404608586991 | 2166 | 565.6565656565656 | 271.15656565656536 | 0 |  | 21.66087962962963 | 1871.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
3 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 55 | 0 | 4.099999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 3 | 83.2 | 4880.000000000014 | 40.97 | 2597.4 | -3000 | 3655.945945945946 | 2110 | 10.55 | 84.42690838816544 | 3759 | 4545.945945945946 | 16.945945945945823 | 120 |  | 24.421296296296298 | 2110 | 2021 | 10 | 2021_10_Asomata_english.xlsx
4 | 0 | 215 | 215 | 0 | 0 | 2 | 215 | 55 | 0 | 4.200000000004366 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 4 | 83.9 | 6560.00000000002 | 41.12 | 2772.9 | 1680.0000000000064 | 4490.35638297873 | 2225.25 | 10.35 | 84.62061729676132 | 4416.5 | 585.1063829787234 | 133.85638297872993 | 60 |  | 25.755208333333332 | 2225.25 | 2021 | 10 | 2021_10_Asomata_english.xlsx
5 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 50 | 0 | 4.099999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 5 | 83.9 | 6560.00000000002 | 41.23 | 2901.6 | 0 | 2111.5 | 2111.5 | 10.3 | 85.03139699237666 | 2123.8 | 0 | 47.69999999999982 | 60 |  | 24.43865740740741 | 2111.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
6 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 54 | 0 | 4.05000000000291 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 6 | 84 | 6800.000000000007 | 41.33 | 3018.6 | 239.99999999998727 | 4451.86125654449 | 2070.5 | 10.1 | 86.50872230080151 | 4453 | 2141.361256544503 | 58.86125654449006 | 60 |  | 23.96412037037037 | 2070.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
7 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 54 | 0 | 4.049999999995634 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 7 | 84.05 | 6920 | 41.61 | 3346.2 | 119.99999999999272 | 2219.9999999999927 | 2100 | 10.5 | 83.11420644357625 | 2102.4 | 0 | 177.59999999999263 | 60 |  | 24.305555555555557 | 2100 | 2021 | 10 | 2021_10_Asomata_english.xlsx
8 | 0 | 210 | 210 | 0 | 0 | 2 | 210 | 55 | 0 | 4.099999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 8 | 84.25 | 7400.000000000007 | 41.7 | 3451.5 | 480.0000000000073 | 5663.308510638305 | 2236.5 | 10.65 | 81.55568519598854 | 5336.3 | 2946.808510638298 | 387.0085106383058 | 60 |  | 25.885416666666668 | 2236.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
9 | 45 | 130 | 175 | 0 | 0 | 3 | 175 | 80 | 1.8000000000029104 | 2.4500000000043656 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 9 | 84.3 | 7520 | 41.7 | 3451.5 | 119.99999999999272 | 1957.4999999999927 | 1837.5 | 10.5 | 82.6229877293707 | 1795.8 | 0 | 161.69999999999277 | 0 |  | 21.26736111111111 | 1837.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
10 | 0 | 200 | 200 | 0 | 0 | 4 | 200 | 55 | 0 | 4.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 10 | 84.2 | 7280.000000000014 | 41.63 | 3369.6 | -239.99999999998636 | 1780.0000000000136 | 2020 | 10.1 | 86.09872835624795 | 1686.3 | 0 | 93.70000000001392 | 0 |  | 23.37962962962963 | 2020 | 2021 | 10 | 2021_10_Asomata_english.xlsx
11 | 135 | 125 | 260 | 0 | 0 | 2 | 260 | 80 | 3.5 | 3.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 11 | 83.7 | 6080.000000000014 | 41.66 | 3404.7 | -1200 | 5584.382978723404 | 2678 | 10.3 | 85.43922143838327 | 5387.4 | 4106.382978723404 | 256.9829787234048 | 60 |  | 30.99537037037037 | 2678 | 2021 | 10 | 2021_10_Asomata_english.xlsx
12 | 140 | 45 | 185 | 0 | 0 | 3 | 185 | 45 | 3.0499999999956344 | 1.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 7.75 | 0 | 2 | 1 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 12 | 83.8 | 6320 | 41.47 | 3182.4 | 239.99999999998636 | 2460.2499999999864 | 1970.25 | 10.65 | 82.43367702226116 | 2502.63 | 250 | 57.61999999998625 | 100 |  | 22.803819444444443 | 1970.25 | 2021 | 10 | 2021_10_Asomata_english.xlsx
13 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 45 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 13 | 84 | 6800.000000000007 | 41.15 | 2808 | 480.0000000000073 | 3123.5691489361775 | 888.25 | 10.45 | 83.61130097972203 | 2883.5 | 1755.3191489361702 | 240.0691489361775 | 0 |  | 10.280671296296296 | 888.25 | 2021 | 10 | 2021_10_Asomata_english.xlsx
14 | 65 | 0 | 65 | 0 | 0 | 2 | 65 | 35 | 1.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 14 | 84.1 | 7039.999999999993 | 41.12 | 2772.9 | 239.99999999998545 | 2647.7499999999854 | 689 | 10.6 | 82.23233092815849 | 2474.7 | 1718.75 | 173.04999999998518 | 0 |  | 7.974537037037037 | 689 | 2021 | 10 | 2021_10_Asomata_english.xlsx
15 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗ Μον. ΝοΙΙ | 15 | 83.4 | 5360.00000000002 | 41.1 | 2749.5 | -1679.9999999999727 | 844.401069518744 | 749 | 10.7 | 82.84121179285746 | 693 | 1775.4010695187167 | 211.40106951874395 | 60 |  | 8.668981481481481 | 749 | 2021 | 10 | 2021_10_Asomata_english.xlsx
16 | 165 | 0 | 165 | 0 | 0 | 3 | 165 | 55 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 83.55 | 5720 | 41.79 | 3556.8 | 359.99999999998 | 4377.563829787214 | 1666.5 | 10.1 | 87.44563987084629 | 4399.2 | 2351.063829787234 | 38.363829787213945 | 60 |  | 19.288194444444443 | 1666.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
17 | 90 | 0 | 90 | 0 | 0 | 2 | 90 | 45 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.6 | 5839.999999999993 | 41.76 | 3521.7 | 119.99999999999272 | 3408.287234042546 | 958.5 | 10.65 | 82.82999277717589 | 3266 | 2329.7872340425533 | 202.28723404254606 | 60 |  | 11.09375 | 958.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
18 | 325 | 250 | 575 | 0 | 0 | 3 | 575 | 80 | 8.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 83.55 | 5720 | 41.61 | 3346.2 | -119.99999999999272 | 8257.925531914902 | 6037.5 | 10.5 | 84.11437739957596 | 8220.3 | 2340.425531914894 | 97.62553191490224 | 60 |  | 69.87847222222223 | 6037.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
19 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 55 | 0 | 4.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.2 | 7280.000000000014 | 41.98 | 3779.1 | 1560.0000000000136 | 3640.0000000000136 | 2080 | 10.4 | 83.6151111921254 | 3518.6 | 0 | 121.40000000001328 | 0 |  | 24.074074074074073 | 2080 | 2021 | 10 | 2021_10_Asomata_english.xlsx
20 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 55 | 0 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.75 | 6200.000000000007 | 41.7 | 3451.5 | -1080.0000000000064 | 2385.7826086956456 | 1656 | 10.35 | 84.9246434666898 | 2421.9 | 1809.7826086956522 | 63.88260869564556 | 100 |  | 19.166666666666668 | 1656 | 2021 | 10 | 2021_10_Asomata_english.xlsx
21 | 90 | 25 | 115 | 0 | 0 | 2 | 115 | 79 | 2 | 0.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83.65 | 5960.00000000002 | 41.67 | 3416.4 | -239.99999999998727 | 1555.0869565217517 | 1219 | 10.6 | 83.12079548800651 | 1484 | 576.0869565217391 | 131.08695652175174 | 60 |  | 14.108796296296296 | 1219 | 2021 | 10 | 2021_10_Asomata_english.xlsx
22 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.65 | 5960.00000000002 | 41.6 | 3334.5 | 0 | 2664.81914893617 | 909.5 | 10.7 | 82.34396562363263 | 2591.5 | 1755.3191489361702 | 73.31914893617022 | 0 |  | 10.526620370370368 | 909.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
23 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 54 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.95 | 6680.000000000014 | 41.56 | 3287.7 | 719.9999999999936 | 1575.9999999999936 | 856 | 10.7 | 81.7550934022479 | 1452.7 | 0 | 123.29999999999359 | 0 |  | 9.907407407407407 | 856 | 2021 | 10 | 2021_10_Asomata_english.xlsx
24 | 20 | 110 | 130 | 0 | 0 | 3 | 130 | 70 | 0.5 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84 | 6800.000000000007 | 41.68 | 3428.1 | 119.99999999999363 | 1432.9999999999936 | 1313 | 10.1 | 86.50872230080151 | 1413.75 | 0 | 79.24999999999363 | 60 |  | 15.19675925925926 | 1313 | 2021 | 10 | 2021_10_Asomata_english.xlsx
25 | 470 | 285 | 755 | 0 | 0 | 2 | 755 | 90 | 11.700000000004366 | 7.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 |  | 25 | 82.85 | 4069.9999999999873 | 41.09 | 2737.8 | -2730.00000000002 | 5944.920212765937 | 7738.75 | 10.25 | 87.64247544556231 | 5913.3 | 936.1702127659574 | 91.62021276593714 | 60 |  | 89.56886574074075 | 7738.75 | 2021 | 10 | 2021_10_Asomata_english.xlsx
26 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 50 | 0 | 2.0200000000040745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.7 | 6080.000000000014 | 41.2 | 2866.5 | 2010.0000000000264 | 2868.5000000000264 | 858.5 | 10.1 | 87.13108720944037 | 2795.9 | 0 | 132.60000000002628 | 60 |  | 9.936342592592593 | 858.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
27 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.65 | 5960.00000000002 | 41.3 | 2983.5 | -119.99999999999363 | 847.5000000000064 | 967.5 | 10.75 | 81.96097043468549 | 759.2 | 0 | 148.30000000000643 | 60 |  | 11.197916666666666 | 967.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
28 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 40 | 0 | 1.9799999999959255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.3 | 5120 | 41.32 | 3006.9 | -840.00000000002 | 839.1489361701928 | 860 | 10.75 | 82.6555549298947 | 730 | 819.1489361702128 | 109.14893617019277 | 0 |  | 9.953703703703704 | 860 | 2021 | 10 | 2021_10_Asomata_english.xlsx
29 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 29 | 83.55 | 5720 | 41.34 | 3030.3 | 600 | 3232.8076923076924 | 940.5 | 10.45 | 84.5168385354591 | 3197.4 | 1692.3076923076922 | 65.40769230769274 | 30 |  | 10.885416666666666 | 940.5 | 2021 | 10 | 2021_10_Asomata_english.xlsx
30 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 54 | 0 | 2.150000000001455 | 0 | 0 | 2.67 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ Μον. ΝοΙ | 30 | 83 | 4400 | 41.52 | 3240.9 | -1320 | 1593.4435483870968 | 1139.25 | 10.85 | 82.49297516016635 | 1666 | 1774.1935483870968 | 27.443548387096826 | 100 |  | 13.18576388888889 | 1139.25 | 2021 | 10 | 2021_10_Asomata_english.xlsx
31 | 90 | 90 | 180 | 0 | 0 | 3 | 180 | 80 | 2.1999999999970896 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 82.5 | 3300 | 41.76 | 3521.7 | -1100 | 2606.276595744681 | 1935 | 10.75 | 84.28825724949756 | 2569.6 | 1771.276595744681 | 96.67659574468098 | 60 |  | 22.395833333333332 | 1935 | 2021 | 10 | 2021_10_Asomata_english.xlsx
1 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 82.45 | 3190.0000000000064 | 41.54 | 3264.3 | -109.99999999999363 | 750.0000000000064 | 860 | 10.75 | 84.39244545376145 | 671.6 | 0 | 78.40000000000634 | 0 |  | 9.953703703703704 | 860 | 2021 | 11 | 2021_11_Asomata_english.xlsx
2 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 54 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.45 | 5480.000000000014 | 41.42 | 3123.9 | 2290.0000000000073 | 3150.0000000000073 | 860 | 10.75 | 82.35643953207843 | 3044.1 | 0 | 165.90000000000737 | 60 |  | 9.953703703703704 | 860 | 2021 | 11 | 2021_11_Asomata_english.xlsx
3 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.4 | 5360.00000000002 | 41.25 | 2925 | -119.99999999999363 | 671.2500000000064 | 791.25 | 10.55 | 84.01904892735305 | 690 | 0 | 21.250000000006366 | 40 |  | 9.15798611111111 | 791.25 | 2021 | 11 | 2021_11_Asomata_english.xlsx
4 | 20 | 90 | 110 | 0 | 0 | 3 | 110 | 80 | 0.3000000000029104 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 83.3 | 5120 | 41.44 | 3147.3 | -240.00000000002 | 859.99999999998 | 1100 | 10 | 88.8547215496368 | 667.5 | 0 | 192.49999999998 | 0 |  | 12.731481481481481 | 1100 | 2021 | 11 | 2021_11_Asomata_english.xlsx
5 | 95 | 20 | 115 | 0 | 0 | 3 | 115 | 80 | 2 | 0.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 83.1 | 4639.999999999993 | 41.6 | 3334.5 | -480.0000000000073 | 721.7499999999927 | 1201.75 | 10.45 | 85.44220538073786 | 657 | 0 | 124.74999999999272 | 60 |  | 13.909143518518519 | 1201.75 | 2021 | 11 | 2021_11_Asomata_english.xlsx
6 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83 | 4400 | 41.6 | 3334.5 | -239.99999999999272 | 732.0000000000074 | 972 | 10.8 | 82.87488708220415 | 658 | 0 | 134.0000000000074 | 60 |  | 11.25 | 972 | 2021 | 11 | 2021_11_Asomata_english.xlsx
7 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 54 | 2.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 83.05 | 4520 | 41.5 | 3217.5 | 120 | 1022.7 | 902.7 | 10.62 | 84.17689143963428 | 978.2 | 0 | 44.499999999999886 | 0 |  | 10.447916666666666 | 902.7 | 2021 | 11 | 2021_11_Asomata_english.xlsx
8 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 54 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 82.5 | 3300 | 41.5 | 3217.5 | -1220 | 1504.4574468085107 | 958.5 | 10.65 | 85.07969628470411 | 1430.8 | 1765.9574468085107 | 133.6574468085107 | 60 |  | 11.09375 | 958.5 | 2021 | 11 | 2021_11_Asomata_english.xlsx
9 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 35 | 1.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84 | 6800.000000000007 | 41.21 | 2878.2 | 3500.0000000000073 | 5541.653061224497 | 909 | 10.1 | 86.50872230080151 | 5579.84 | 1132.6530612244896 | 21.813061224496778 | 60 |  | 10.520833333333334 | 909 | 2021 | 11 | 2021_11_Asomata_english.xlsx
10 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.15 | 4760.00000000002 | 41.22 | 2889.9 | -2039.9999999999873 | 624.319148936183 | 909 | 10.1 | 88.29565824140128 | 642.4 | 1755.3191489361702 | 41.91914893618298 | 60 |  | 10.520833333333334 | 909 | 2021 | 11 | 2021_11_Asomata_english.xlsx
11 | 95 | 45 | 140 | 0 | 0 | 3 | 140 | 108 | 1.9500000000043656 | 0.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 83.9 | 6560.00000000002 | 41.65 | 3393 | 1800 | 3214 | 1414 | 10.1 | 86.71518703182966 | 3204.7 | 0 | 69.30000000000018 | 60 |  | 16.36574074074074 | 1414 | 2021 | 11 | 2021_11_Asomata_english.xlsx
12 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 54 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.25 | 7400.000000000007 | 41.67 | 3416.4 | 839.9999999999873 | 4040.666666666654 | 909 | 10.1 | 85.99683637002754 | 3981.2 | 2291.6666666666665 | 119.46666666665396 | 60 |  | 10.520833333333334 | 909 | 2021 | 11 | 2021_11_Asomata_english.xlsx
13 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 83.95 | 6680.000000000014 | 41.68 | 3428.1 | -719.9999999999936 | 3535.199481865291 | 949.5 | 10.55 | 82.91748809517084 | 3650 | 3305.6994818652847 | 5.199481865291091 | 120 |  | 10.989583333333334 | 949.5 | 2021 | 11 | 2021_11_Asomata_english.xlsx
14 | 60 | 145 | 205 | 0 | 0 | 3 | 205 | 80 | 1.2999999999956344 | 2.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 83.45 | 5480.000000000014 | 41.95 | 3744 | -1200 | 962.75 | 2162.75 | 10.55 | 83.91769904927422 | 963.6 | 0 | 59.15 | 60 |  | 25.031828703703702 | 2162.75 | 2021 | 11 | 2021_11_Asomata_english.xlsx
15 | 105 | 55 | 160 | 0 | 0 | 4 | 160 | 105 | 2.1000000000058208 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 83 | 4400 | 41.93 | 3720.6 | -1080.0000000000136 | 591.9999999999864 | 1672 | 10.45 | 85.6506010036177 | 616 | 0 | 35.99999999998636 | 60 |  | 19.35185185185185 | 1672 | 2021 | 11 | 2021_11_Asomata_english.xlsx
16 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 54 | 0 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83 | 4400 | 41.93 | 3720.6 | 0 | 4533.904255319148 | 1060.5 | 10.1 | 88.61869113740643 | 4401.9 | 3473.404255319149 | 162.0042553191488 | 30 |  | 12.274305555555555 | 1060.5 | 2021 | 11 | 2021_11_Asomata_english.xlsx
17 | 120 | 40 | 160 | 0 | 0 | 3 | 160 | 80 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 83.15 | 4760.00000000002 | 41.9 | 3685.5 | 360.00000000002 | 1976.00000000002 | 1616 | 10.1 | 88.29565824140128 | 1952.5 | 0 | 83.50000000002001 | 60 |  | 18.703703703703702 | 1616 | 2021 | 11 | 2021_11_Asomata_english.xlsx
18 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 50 | 0 | 2.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 83.4 | 5360.00000000002 | 41.79 | 3556.8 | 600 | 1711 | 1111 | 10.1 | 87.76247189936385 | 1677.9 | 0 | 93.10000000000014 | 60 |  | 12.858796296296296 | 1111 | 2021 | 11 | 2021_11_Asomata_english.xlsx
19 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 50 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.35 | 5239.999999999993 | 41.71 | 3463.2 | -120.00000000002728 | 3034.1989247311553 | 858.5 | 10.1 | 87.86859338896406 | 2919 | 2295.6989247311826 | 175.19892473115533 | 60 |  | 9.936342592592593 | 858.5 | 2021 | 11 | 2021_11_Asomata_english.xlsx
20 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 55 | 0 | 2.1199999999953434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.3 | 5120 | 41.77 | 3533.4 | -119.99999999999272 | 2634.680851063837 | 1010 | 10.1 | 87.97497183132359 | 2471 | 1744.6808510638298 | 223.68085106383705 | 60 |  | 11.689814814814815 | 1010 | 2021 | 11 | 2021_11_Asomata_english.xlsx
21 | 75 | 60 | 135 | 0 | 0 | 2 | 135 | 70 | 1.9499999999970896 | 1.5300000000061118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 83 | 4400 | 41.48 | 3194.1 | -720 | 2413.75 | 1383.75 | 10.25 | 87.32183224271267 | 2456.6 | 1750 | 17.15000000000009 | 60 |  | 16.015625 | 1383.75 | 2021 | 11 | 2021_11_Asomata_english.xlsx
22 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 45 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 82.95 | 4290.000000000006 | 41.43 | 3135.6 | -109.99999999999363 | 2509.138297872347 | 858.5 | 10.1 | 88.72689466748872 | 2422 | 1760.6382978723404 | 147.1382978723468 | 60 |  | 9.936342592592593 | 858.5 | 2021 | 11 | 2021_11_Asomata_english.xlsx
23 | 115 | 40 | 155 | 0 | 0 | 3 | 155 | 80 | 3 | 1.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 82.65 | 3630.0000000000127 | 41.93 | 3720.6 | -659.9999999999936 | 2762.0265957446873 | 1650.75 | 10.65 | 84.76574906594135 | 2868.9 | 1771.276595744681 | 13.126595744687165 | 120 |  | 19.10590277777778 | 1650.75 | 2021 | 11 | 2021_11_Asomata_english.xlsx
24 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 40 | 0 | 2.1300000000046566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83 | 4400 | 41.86 | 3638.7 | 769.9999999999873 | 3504.276595744668 | 963 | 10.7 | 83.64941873717802 | 3615.325 | 1771.276595744681 | 8.951595744668339 | 120 |  | 11.145833333333332 | 963 | 2021 | 11 | 2021_11_Asomata_english.xlsx
25 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.05 | 4520 | 41.75 | 3510 | 120 | 2712.673469387755 | 909 | 10.1 | 88.51075119692239 | 2521.05 | 1683.673469387755 | 191.62346938775545 | 0 |  | 10.520833333333334 | 909 | 2021 | 11 | 2021_11_Asomata_english.xlsx
26 | 95 | 95 | 190 | 0 | 0 | 3 | 190 | 100 | 2 | 2.0199999999967986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 82.5 | 3300 | 41.95 | 3744 | -1220 | 3037.6243386243386 | 1919 | 10.1 | 89.71274905268304 | 3038.75 | 2338.6243386243386 | 58.874338624338634 | 60 |  | 22.21064814814815 | 1919 | 2021 | 11 | 2021_11_Asomata_english.xlsx
27 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 54 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 82.75 | 3850 | 41.68 | 3428.1 | 550 | 1560 | 1010 | 10.1 | 89.16236408916966 | 1542.15 | 0 | 17.84999999999991 | 0 |  | 11.689814814814815 | 1010 | 2021 | 11 | 2021_11_Asomata_english.xlsx
28 | 70 | 95 | 165 | 0 | 0 | 3 | 165 | 108 | 1.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 82.3 | 2859.9999999999936 | 41.66 | 3404.7 | -990.0000000000064 | 1936.0483870967678 | 1732.5 | 10.5 | 86.72338414273898 | 1792 | 1193.5483870967741 | 204.04838709676778 | 60 |  | 20.052083333333332 | 1732.5 | 2021 | 11 | 2021_11_Asomata_english.xlsx
29 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 82.3 | 2859.9999999999936 | 41.48 | 3194.1 | 0 | 798.75 | 798.75 | 10.65 | 85.50192802805252 | 664.3 | 0 | 134.45 | 0 |  | 9.244791666666666 | 798.75 | 2021 | 11 | 2021_11_Asomata_english.xlsx
30 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 82.2 | 2640.0000000000064 | 41.52 | 3240.9 | -219.99999999998727 | 739.5000000000127 | 959.5 | 10.1 | 90.38224717994187 | 664.3 | 0 | 135.20000000001278 | 60 |  | 11.105324074074074 | 959.5 | 2021 | 11 | 2021_11_Asomata_english.xlsx
1 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 40 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 82.15 | 2530.0000000000127 | 41.35 | 3042 | -109.99999999999363 | 698.0000000000064 | 808 | 10.1 | 90.49480290494802 | 671.6 | 0 | 86.40000000000634 | 60 |  | 9.351851851851851 | 808 | 2021 | 12 | 2021_12_Asomata_english.xlsx
2 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 55 | 0 | 2.0100000000020373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 82 | 2200 | 41.35 | 3042 | -330.00000000001273 | 672.2499999999874 | 1002.25 | 10.55 | 86.95971563981043 | 644 | 0 | 88.24999999998738 | 60 |  | 11.600115740740742 | 1002.25 | 2021 | 12 | 2021_12_Asomata_english.xlsx
3 | 80 | 0 | 80 | 0 | 0 | 6 | 80 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 81.95 | 2090.0000000000064 | 41.26 | 2936.7 | -109.99999999999363 | 750.0000000000064 | 860 | 10.75 | 85.44867130424657 | 664.3 | 0 | 85.70000000000641 | 0 |  | 9.953703703703704 | 860 | 2021 | 12 | 2021_12_Asomata_english.xlsx
4 | 0 | 90 | 90 | 0 | 0 | 5 | 90 | 40 | 0 | 1.9899999999979627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 81.8 | 1759.9999999999936 | 41.25 | 2925 | -330.00000000001273 | 637.4999999999873 | 967.5 | 10.75 | 85.77071403529276 | 609 | 0 | 88.49999999998727 | 60 |  | 11.197916666666666 | 967.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
5 | 75 | 0 | 75 | 0 | 0 | 6 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 81.8 | 1759.9999999999936 | 41.1 | 2749.5 | 0 | 798.75 | 798.75 | 10.65 | 86.57607285252554 | 678.9 | 0 | 119.85 | 0 |  | 9.244791666666666 | 798.75 | 2021 | 12 | 2021_12_Asomata_english.xlsx
6 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 40 | 0 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 81.75 | 1650 | 41 | 2632.5 | -109.99999999999363 | 746.0000000000064 | 856 | 10.7 | 86.27990360312702 | 658 | 0 | 148.00000000000637 | 60 |  | 9.907407407407407 | 856 | 2021 | 12 | 2021_12_Asomata_english.xlsx
7 | 120 | 0 | 120 | 0 | 0 | 6 | 120 | 54 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 82.4 | 3080.0000000000127 | 41.26 | 2936.7 | 1430.0000000000127 | 2642.0000000000127 | 1212 | 10.1 | 89.93481031271443 | 2520 | 0 | 182.00000000001273 | 60 |  | 14.027777777777779 | 1212 | 2021 | 12 | 2021_12_Asomata_english.xlsx
8 | 0 | 150 | 150 | 0 | 0 | 6 | 150 | 54 | 0 | 3.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 82 | 2200 | 41.63 | 3369.6 | -880.0000000000127 | 702.4999999999873 | 1582.5 | 10.55 | 86.95971563981043 | 642.4 | 0 | 60.09999999998729 | 0 |  | 18.31597222222222 | 1582.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
9 | 255 | 0 | 255 | 0 | 0 | 6 | 255 | 50 | 5.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 9 | 82.05 | 2309.9999999999936 | 41.7 | 3451.5 | 109.99999999999363 | 2749.2499999999936 | 2639.25 | 10.35 | 88.52943482482645 | 2645.2 | 0 | 164.04999999999382 | 60 |  | 30.546875 | 2639.25 | 2021 | 12 | 2021_12_Asomata_english.xlsx
10 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 81.9 | 1980.0000000000125 | 41.45 | 3159 | -329.9999999999811 | 476.2500000000189 | 806.25 | 10.75 | 85.55574983971556 | 476 | 0 | 60.25000000001887 | 60 |  | 9.331597222222221 | 806.25 | 2021 | 12 | 2021_12_Asomata_english.xlsx
11 | 400 | 265 | 665 | 0 | 0 | 6 | 665 | 108 | 8.5 | 5.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.1 | 7039.999999999993 | 41.9 | 3685.5 | 5059.99999999998 | 12845.648936170193 | 6716.5 | 10.1 | 86.3032383998495 | 12814.8 | 1069.1489361702127 | 90.84893617019407 | 60 |  | 77.73726851851852 | 6716.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
12 | 0 | 215 | 215 | 0 | 0 | 5 | 215 | 50 | 0 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 83.3 | 5120 | 41.53 | 3252.6 | -1919.9999999999927 | 4310.010638297879 | 2171.5 | 10.1 | 87.97497183132359 | 4235 | 4058.5106382978724 | 175.01063829787927 | 100 |  | 25.13310185185185 | 2171.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
13 | 390 | 0 | 390 | 0 | 0 | 5 | 390 | 54 | 7.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 0 | ΒΛΑΒΗ ΜΕ ΤΟ ΟΡΙΟ ΦΟΡΤΙΟΥ & ΟΡΙΟ ΙΣΧΥΟΣ | 13 | 84.3 | 7520 | 41.38 | 3077.1 | 2400 | 8679.425531914894 | 3939 | 10.1 | 85.89518526320718 | 8615.1 | 2340.425531914894 | 124.32553191489387 | 60 |  | 45.59027777777778 | 3939 | 2021 | 12 | 2021_12_Asomata_english.xlsx
14 | 730 | 560 | 1290 | 0 | 0 | 7 | 1290 | 110 | 15.650000000001455 | 12.470000000001164 | 0 | 0 | 0.8 | 0 | 0 | 0 | 11.5 | 0 | 1 | 1 | ΒΛ. ΜΕ ΤΟ ΟΡΙΟ Φ. & Ι. NoII - ΒΛ. ΡΥΘΜ. ΣΤΡ. ΝοΙ | 14 | 84.25 | 7400.000000000007 | 41.9 | 3685.5 | -119.99999999999272 | 12909 | 13029 | 10.1 | 85.99683637002754 | 12884.5 | 0 | 84.50000000000728 | 60 |  | 150.79861111111111 | 13029 | 2021 | 12 | 2021_12_Asomata_english.xlsx
15 | 290 | 225 | 515 | 0 | 0 | 6 | 515 | 108 | 5.900000000001455 | 4.129999999997381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 85.05 | 9320 | 41.78 | 3545.1 | 1919.9999999999927 | 9861.878172588826 | 5150 | 10 | 85.24274099883856 | 9616.32 | 2791.8781725888325 | 245.55817258882598 | 0 |  | 59.60648148148148 | 5150 | 2021 | 12 | 2021_12_Asomata_english.xlsx
16 | 105 | 530 | 635 | 0 | 0 | 5 | 635 | 80 | 2.6999999999970896 | 12.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.5 | 8000.000000000007 | 41.7 | 3451.5 | -1319.9999999999927 | 5093.500000000007 | 6413.5 | 10.1 | 85.49097262667443 | 4971.3 | 0 | 182.2000000000071 | 60 |  | 74.23032407407408 | 6413.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
17 | 85 | 0 | 85 | 0 | 0 | 5 | 85 | 42 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.5 | 8000.000000000007 | 41.48 | 3194.1 | 0 | 858.5 | 858.5 | 10.1 | 85.49097262667443 | 678.9 | 0 | 239.6 | 60 |  | 9.936342592592593 | 858.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
18 | 0 | 90 | 90 | 0 | 0 | 6 | 90 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.9 | 6560.00000000002 | 41.5 | 3217.5 | -1439.9999999999873 | 1200.5851063829914 | 922.5 | 10.25 | 85.44618429477849 | 1035 | 1718.0851063829787 | 165.5851063829914 | 0 |  | 10.677083333333334 | 922.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
19 | 105 | 0 | 105 | 0 | 0 | 6 | 105 | 40 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.8 | 6320 | 41.63 | 3369.6 | -240.00000000002 | 3102.4148936170013 | 1060.5 | 10.1 | 86.9226396323843 | 2933 | 2281.9148936170213 | 229.41489361700133 | 60 |  | 12.274305555555555 | 1060.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
20 | 250 | 265 | 515 | 0 | 0 | 6 | 515 | 80 | 5.30000000000291 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 85.25 | 9800.000000000007 | 41.75 | 3510 | 3480.0000000000073 | 10712.112244897966 | 5201.5 | 10.1 | 84.00847021118297 | 10554.6 | 2030.612244897959 | 157.51224489796732 | 0 |  | 60.2025462962963 | 5201.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
21 | 540 | 400 | 940 | 0 | 0 | 5 | 940 | 108 | 12.779999999998836 | 9.439999999995052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85 | 9200.000000000007 | 41.77 | 3533.4 | -600 | 11761.021276595744 | 9494 | 10.1 | 84.49689154962007 | 11636.2 | 2867.021276595745 | 184.82127659574326 | 60 |  | 109.88425925925925 | 9494 | 2021 | 12 | 2021_12_Asomata_english.xlsx
22 | 420 | 500 | 920 | 0 | 0 | 6 | 920 | 90 | 9.489999999997963 | 11.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 83.5 | 5600.000000000007 | 41.6 | 3334.5 | -3600 | 8053.702127659575 | 9292 | 10.1 | 87.55099606346177 | 7971.6 | 2361.7021276595747 | 142.10212765957476 | 60 |  | 107.54629629629629 | 9292 | 2021 | 12 | 2021_12_Asomata_english.xlsx
23 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.8 | 6320 | 41.46 | 3170.7 | 719.9999999999927 | 1511.2499999999927 | 791.25 | 10.55 | 83.21503888977074 | 1124.2 | 0 | 387.0499999999927 | 0 |  | 9.15798611111111 | 791.25 | 2021 | 12 | 2021_12_Asomata_english.xlsx
24 | 0 | 85 | 85 | 0 | 0 | 6 | 85 | 40 | 0 | 2.1300000000046566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.9 | 6560.00000000002 | 41.43 | 3135.6 | 240.00000000002 | 2161.00000000002 | 858.5 | 10.1 | 86.71518703182966 | 2044 | 1062.5 | 177.00000000002 | 60 |  | 9.936342592592593 | 858.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 5 | 70 | 35 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.8 | 6320 | 41.33 | 3018.6 | -240.00000000002 | 2715.458333333313 | 731.5 | 10.45 | 84.01135505139536 | 2620.7 | 2223.958333333333 | 94.7583333333132 | 0 |  | 8.466435185185185 | 731.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
26 | 0 | 90 | 90 | 0 | 0 | 6 | 90 | 50 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.85 | 6439.999999999993 | 41.32 | 3006.9 | 119.99999999999272 | 2794.9574468085034 | 909 | 10.1 | 86.81878940582232 | 2591.5 | 1765.9574468085107 | 203.4574468085034 | 0 |  | 10.520833333333334 | 909 | 2021 | 12 | 2021_12_Asomata_english.xlsx
27 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.1 | 7039.999999999993 | 41.3 | 2983.5 | 600 | 6039.578947368421 | 808 | 10.1 | 86.3032383998495 | 6041.95 | 4631.578947368421 | 57.628947368420086 | 60 |  | 9.351851851851851 | 808 | 2021 | 12 | 2021_12_Asomata_english.xlsx
28 | 0 | 95 | 95 | 0 | 0 | 6 | 95 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.9 | 6560.00000000002 | 41.33 | 3018.6 | -479.9999999999727 | 7319.9255319149215 | 959.5 | 10.1 | 86.71518703182966 | 7236 | 6840.425531914894 | 143.92553191492152 | 60 |  | 11.105324074074074 | 959.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
29 | 390 | 45 | 435 | 0 | 0 | 6 | 435 | 95 | 9.05000000000291 | 0.930000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.2 | 7280.000000000014 | 41.65 | 3393 | 719.9999999999936 | 6966.457446808505 | 4480.5 | 10.3 | 84.42690838816543 | 6940.8 | 1765.9574468085107 | 85.65744680850457 | 60 |  | 51.8576388888889 | 4480.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
30 | 0 | 605 | 605 | 0 | 0 | 6 | 605 | 54 | 0 | 14.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.3 | 9920 | 41.29 | 2971.8 | 2639.9999999999864 | 9290.372340425518 | 6352.5 | 10.5 | 80.7148355878148 | 9241.8 | 297.8723404255319 | 108.57234042551863 | 60 |  | 73.52430555555556 | 6352.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
31 | 705 | 90 | 795 | 0 | 0 | 0 | 795 | 108 | 13.650000000001455 | 2.0200000000040745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 83.3 | 5120 | 41.49 | 3205.8 | -4800 | 3793.602564102564 | 8029.5 | 10.1 | 87.97497183132359 | 3633 | 564.1025641025641 | 220.60256410256397 | 60 |  | 92.93402777777777 | 8029.5 | 2021 | 12 | 2021_12_Asomata_english.xlsx
1 | 655 | 610 | 1265 | 0 | 0 | 10 | 1265 | 110 | 15 | 14.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 82.45 | 3190.0000000000064 | 41.58 | 3311.1 | -1929.9999999999936 | 11947.094594594602 | 13282.5 | 10.5 | 86.40178939313672 | 11871.05 | 594.5945945945946 | 136.04459459460304 | 60 |  | 153.73263888888889 | 13282.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
2 | 260 | 645 | 905 | 0 | 0 | 5 | 905 | 88 | 6.099999999998545 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.4 | 5360.00000000002 | 41.59 | 3322.8 | 2170.0000000000136 | 11672.5 | 9502.5 | 10.5 | 84.41913963653093 | 11622.7 | 0 | 109.80000000001564 | 60 |  | 109.98263888888889 | 9502.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
3 | 645 | 640 | 1285 | 0 | 0 | 5 | 1285 | 110 | 12.099999999998545 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 82.55 | 3409.9999999999936 | 41.82 | 3591.9 | -1950.0000000000264 | 12056.5 | 14006.5 | 10.9 | 83.02582608400547 | 12078.99 | 0 | 37.50999999997657 | 60 |  | 162.1122685185185 | 14006.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
4 | 100 | 645 | 745 | 0 | 0 | 5 | 745 | 110 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 83.85 | 6439.999999999993 | 41.75 | 3510 | 3030 | 10778 | 7748 | 10.4 | 84.31440124988514 | 10661 | 0 | 117 | 0 |  | 89.67592592592592 | 7748 | 2022 | 1 | 2022_01_Asomata_english.xlsx
5 | 655 | 635 | 1290 | 0 | 0 | 5 | 1290 | 110 | 12.30000000000291 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 83.8 | 6320 | 41.75 | 3510 | -119.99999999999272 | 13296 | 13416 | 10.4 | 84.41525579683476 | 13260 | 0 | 66.00000000000728 | 30 |  | 155.27777777777777 | 13416 | 2022 | 1 | 2022_01_Asomata_english.xlsx
6 | 650 | 660 | 1310 | 0 | 0 | 6 | 1310 | 108 | 12.319999999999709 | 12.430000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 6 | 84.9 | 8960.00000000002 | 41.95 | 3744 | 2640.00000000002 | 15609 | 12969 | 9.9 | 86.40484095029548 | 15429 | 0 | 180.00000000002 | 0 |  | 150.10416666666666 | 12969 | 2022 | 1 | 2022_01_Asomata_english.xlsx
7 | 715 | 675 | 1390 | 0 | 0 | 4 | 1390 | 110 | 13.680000000000291 | 12.790000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 7 | 83.05 | 4520 | 41.82 | 3591.9 | -4440.00000000002 | 11925.053475935809 | 14595 | 10.5 | 85.13891305608723 | 11739 | 1770.0534759358288 | 186.05347593580882 | 0 |  | 168.92361111111111 | 14595 | 2022 | 1 | 2022_01_Asomata_english.xlsx
8 | 625 | 620 | 1245 | 0 | 0 | 5 | 1245 | 108 | 12.260000000002037 | 11.980000000003201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 82.6 | 3519.9999999999873 | 42 | 3802.5 | -1000.0000000000127 | 12570.5 | 13570.5 | 10.9 | 82.92357752971483 | 12656 | 0 | 64.49999999998727 | 150 |  | 157.06597222222223 | 13570.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
9 | 640 | 625 | 1265 | 0 | 0 | 5 | 1265 | 108 | 12.109999999993306 | 12.010000000002037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 83.7 | 6080.000000000014 | 42 | 3802.5 | 2560.0000000000264 | 15969 | 13409 | 10.6 | 83.02113026559883 | 16023 | 0 | 96.00000000002547 | 150 |  | 155.19675925925927 | 13409 | 2022 | 1 | 2022_01_Asomata_english.xlsx
10 | 655 | 655 | 1310 | 0 | 0 | 4 | 1310 | 108 | 12.230000000003201 | 12.189999999995052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 10 | 84.75 | 8600.000000000007 | 42 | 3802.5 | 2519.9999999999936 | 15751 | 13231 | 10.1 | 84.9910254183313 | 15236.65 | 0 | 514.3499999999931 | 0 |  | 153.13657407407408 | 13231 | 2022 | 1 | 2022_01_Asomata_english.xlsx
11 | 850 | 915 | 1765 | 0 | 0 | 5 | 1765 | 110 | 16.25 | 16.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 83.7 | 6080.000000000014 | 41.87 | 3650.4 | -2519.9999999999936 | 15306.5 | 17826.5 | 10.1 | 87.13108720944037 | 13986.3 | 0 | 138.20000000001 | 60 |  | 206.3252314814815 | 17826.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
12 | 110 | 775 | 885 | 0 | 0 | 4 | 885 | 110 | 2.0500000000029104 | 15.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 83.4 | 5360.00000000002 | 41.8 | 3568.5 | -719.9999999999936 | 8572.500000000007 | 9292.5 | 10.5 | 84.41913963653093 | 7955.7 | 0 | 676.8000000000065 | 60 |  | 107.55208333333333 | 9292.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
13 | 260 | 110 | 370 | 0 | 0 | 5 | 370 | 55 | 5.769999999996799 | 2.1199999999953434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 85.3 | 9920 | 41.3 | 2983.5 | 4559.99999999998 | 8222.99999999998 | 3663 | 9.9 | 85.60664380525813 | 7760.3 | 0 | 462.6999999999807 | 0 |  | 42.395833333333336 | 3663 | 2022 | 1 | 2022_01_Asomata_english.xlsx
14 | 805 | 160 | 965 | 0 | 0 | 5 | 965 | 110 | 14.480000000003201 | 2.9800000000032014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.5 | 5600.000000000007 | 41.75 | 3510 | -4319.999999999993 | 5426.500000000007 | 9746.5 | 10.1 | 87.55099606346177 | 5393.25 | 0 | 93.25000000000728 | 60 |  | 112.80671296296296 | 9746.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
15 | 540 | 425 | 965 | 0 | 0 | 5 | 965 | 108 | 10.349999999998545 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 82.4 | 3080.0000000000127 | 41.78 | 3545.1 | -2519.9999999999945 | 7805.5000000000055 | 10325.5 | 10.7 | 84.89173683723511 | 7809 | 0 | 56.50000000000546 | 60 |  | 119.50810185185185 | 10325.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
16 | 165 | 695 | 860 | 0 | 0 | 4 | 860 | 109 | 2.970000000001164 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 82.7 | 3740.0000000000064 | 41.72 | 3474.9 | 659.9999999999936 | 9818.999999999993 | 9159 | 10.65 | 84.66161423907901 | 9842 | 0 | 36.999999999992724 | 60 |  | 106.00694444444444 | 9159 | 2022 | 1 | 2022_01_Asomata_english.xlsx
17 | 360 | 0 | 360 | 0 | 0 | 5 | 360 | 54 | 6.9799999999959255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.85 | 8839.999999999993 | 41.6 | 3334.5 | 5099.999999999986 | 8699.999999999985 | 3600 | 10 | 85.64060676779464 | 8523.27 | 0 | 176.729999999985 | 0 |  | 41.666666666666664 | 3600 | 2022 | 1 | 2022_01_Asomata_english.xlsx
18 | 225 | 440 | 665 | 0 | 0 | 4 | 665 | 108 | 4.55000000000291 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.45 | 7880.000000000014 | 40.99 | 2620.8 | -959.9999999999791 | 5756.500000000021 | 6716.5 | 10.1 | 85.5916687075068 | 5672.1 | 0 | 144.40000000002146 | 60 |  | 77.73726851851852 | 6716.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
19 | 235 | 220 | 455 | 0 | 0 | 5 | 455 | 108 | 5.099999999998545 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 84.65 | 8360.00000000002 | 40.96 | 2585.7 | 480.00000000000637 | 7964.973684210532 | 4595.5 | 10.1 | 85.19030097617029 | 7825.6 | 2889.4736842105262 | 139.3736842105327 | 0 |  | 53.188657407407405 | 4595.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
20 | 270 | 380 | 650 | 0 | 0 | 5 | 650 | 108 | 4.94999999999709 | 6.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.2 | 7280.000000000014 | 41.04 | 2679.3 | -1080.0000000000064 | 7177.307692307686 | 6565 | 10.1 | 86.09872835624795 | 7159.45 | 1692.3076923076922 | 77.85769230768528 | 60 |  | 75.98379629629629 | 6565 | 2022 | 1 | 2022_01_Asomata_english.xlsx
21 | 305 | 275 | 580 | 0 | 0 | 4 | 580 | 108 | 6.150000000001455 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.75 | 8600.000000000007 | 41.84 | 3615.3 | 1319.9999999999936 | 9446.041237113395 | 5858 | 10.1 | 84.9910254183313 | 9380.5 | 2268.041237113402 | 125.54123711339525 | 60 |  | 67.80092592592592 | 5858 | 2022 | 1 | 2022_01_Asomata_english.xlsx
22 | 220 | 385 | 605 | 0 | 0 | 5 | 605 | 110 | 4 | 7.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.15 | 7160.00000000002 | 41.9 | 3685.5 | -1439.9999999999873 | 4670.500000000013 | 6110.5 | 10.1 | 86.20086207909047 | 4533.3 | 0 | 197.20000000001255 | 60 |  | 70.72337962962963 | 6110.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
23 | 265 | 245 | 510 | 0 | 0 | 5 | 510 | 110 | 5 | 4.44999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.2 | 7280.000000000014 | 41.85 | 3627 | 119.99999999999363 | 5270.999999999994 | 5151 | 10.1 | 86.09872835624795 | 5283.6 | 0 | 47.39999999999327 | 60 |  | 59.61805555555556 | 5151 | 2022 | 1 | 2022_01_Asomata_english.xlsx
24 | 275 | 295 | 570 | 0 | 0 | 4 | 570 | 110 | 6 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 85.05 | 9320 | 41.8 | 3568.5 | 2039.9999999999864 | 7739.999999999986 | 5700 | 10 | 85.24274099883856 | 7584.8 | 0 | 155.19999999998709 | 0 |  | 65.97222222222223 | 5700 | 2022 | 1 | 2022_01_Asomata_english.xlsx
25 | 680 | 625 | 1305 | 0 | 0 | 5 | 1305 | 108 | 13.5 | 12.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 83.15 | 4760.00000000002 | 41.75 | 3510 | -4559.99999999998 | 10147.836956521758 | 13506.75 | 10.35 | 86.1629128732515 | 10042.1 | 1201.086956521739 | 165.73695652175957 | 60 |  | 156.328125 | 13506.75 | 2022 | 1 | 2022_01_Asomata_english.xlsx
26 | 155 | 420 | 575 | 0 | 0 | 5 | 575 | 109 | 3 | 8.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 82.9 | 4180.000000000013 | 41.83 | 3603.6 | -580.0000000000073 | 5457.499999999993 | 6037.5 | 10.5 | 85.45115845849341 | 5459.45 | 0 | 58.049999999992906 | 60 |  | 69.87847222222223 | 6037.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
27 | 315 | 245 | 560 | 0 | 0 | 5 | 560 | 108 | 6.400000000001455 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84 | 6800.000000000007 | 41.58 | 3311.1 | 2619.9999999999945 | 9446.212765957442 | 5656 | 10.1 | 86.50872230080151 | 9298.72 | 1170.212765957447 | 207.49276595744232 | 60 |  | 65.46296296296296 | 5656 | 2022 | 1 | 2022_01_Asomata_english.xlsx
28 | 145 | 365 | 510 | 0 | 0 | 4 | 510 | 108 | 2.8000000000029104 | 7.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 83.6 | 5839.999999999993 | 41.83 | 3603.6 | -960.0000000000146 | 5153.765957446794 | 5151 | 10.1 | 87.34053693830923 | 5112 | 962.7659574468086 | 101.76595744679435 | 60 |  | 59.61805555555556 | 5151 | 2022 | 1 | 2022_01_Asomata_english.xlsx
29 | 200 | 210 | 410 | 0 | 0 | 5 | 410 | 108 | 4.099999999998545 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 83.15 | 4760.00000000002 | 41.85 | 3627 | -1079.9999999999727 | 5468.210526315816 | 4264 | 10.4 | 85.7486680998224 | 5495 | 2284.210526315789 | 33.21052631581642 | 60 |  | 49.351851851851855 | 4264 | 2022 | 1 | 2022_01_Asomata_english.xlsx
30 | 160 | 265 | 425 | 0 | 0 | 5 | 425 | 108 | 3.0499999999956344 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 82.85 | 4069.9999999999873 | 41.8 | 3568.5 | -690.0000000000327 | 5395.978260869532 | 4292.5 | 10.1 | 88.94409636802115 | 5413.56 | 1793.4782608695652 | 42.41826086953279 | 60 |  | 49.68171296296296 | 4292.5 | 2022 | 1 | 2022_01_Asomata_english.xlsx
31 | 255 | 185 | 440 | 0 | 0 | 4 | 440 | 108 | 5.150000000001455 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 82.65 | 3630.0000000000127 | 41.91 | 3697.2 | -439.99999999997453 | 5759.319148936196 | 4444 | 10.1 | 89.38170569824509 | 5779.02 | 1755.3191489361702 | 40.29914893619571 | 60 |  | 51.43518518518518 | 4444 | 2022 | 1 | 2022_01_Asomata_english.xlsx
1 | 330 | 150 | 480 | 0 | 0 | 5 | 480 | 110 | 6.099999999998545 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 82.6 | 3519.9999999999873 | 42.05 | 3861 | -110.00000000002547 | 6500.162162162136 | 4848 | 10.1 | 89.49178169048433 | 6513.6 | 1762.162162162162 | 46.56216216213579 | 60 |  | 56.111111111111114 | 4848 | 2022 | 2 | 2022_02_Asomata_english.xlsx
2 | 100 | 240 | 340 | 0 | 0 | 4 | 340 | 110 | 2.7000000000043656 | 5.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.45 | 7880.000000000014 | 41.85 | 3627 | 4360.000000000026 | 9512.085106383005 | 3434 | 10.1 | 85.5916687075068 | 9396 | 1718.0851063829787 | 176.08510638300504 | 60 |  | 39.745370370370374 | 3434 | 2022 | 2 | 2022_02_Asomata_english.xlsx
3 | 265 | 215 | 480 | 0 | 0 | 5 | 480 | 110 | 5 | 4.059999999997672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 85 | 9200.000000000007 | 41.93 | 3720.6 | 1319.9999999999936 | 8569.04166666666 | 4848 | 10.1 | 84.49689154962007 | 8387.7 | 2401.0416666666665 | 181.34166666665988 | 0 |  | 56.111111111111114 | 4848 | 2022 | 2 | 2022_02_Asomata_english.xlsx
4 | 300 | 325 | 625 | 0 | 0 | 4 | 625 | 110 | 6.080000000001746 | 5.790000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.3 | 7520 | 41.92 | 3708.9 | -1680.0000000000073 | 5254.0997409326355 | 6281.25 | 10.05 | 86.32252449337238 | 5112.38 | 652.8497409326425 | 141.71974093263543 | 0 |  | 72.69965277777777 | 6281.25 | 2022 | 2 | 2022_02_Asomata_english.xlsx
5 | 275 | 110 | 385 | 0 | 0 | 5 | 385 | 98 | 6.019999999996799 | 2.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 83.75 | 6200.000000000007 | 41.74 | 3498.3 | -1319.9999999999927 | 4908.9255319149015 | 3888.5 | 10.1 | 87.02673860200392 | 4898.04 | 2340.425531914894 | 70.88553191490155 | 60 |  | 45.00578703703704 | 3888.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
6 | 180 | 145 | 325 | 0 | 0 | 5 | 325 | 88 | 4.099999999998545 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 83.55 | 5720 | 41.8 | 3568.5 | -480.0000000000073 | 2802.4999999999927 | 3282.5 | 10.1 | 87.44563987084629 | 2817.8 | 0 | 44.699999999993 | 60 |  | 37.991898148148145 | 3282.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
7 | 165 | 100 | 265 | 0 | 0 | 5 | 265 | 86 | 3.7000000000043656 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 83.2 | 4880.000000000014 | 41.69 | 3439.8 | -839.9999999999864 | 3591.819148936184 | 2676.5 | 10.1 | 88.18850331635105 | 3540.5 | 1755.3191489361702 | 111.31914893618386 | 60 |  | 30.97800925925926 | 2676.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
8 | 0 | 200 | 200 | 0 | 0 | 5 | 200 | 54 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.05 | 4520 | 41.85 | 3627 | -360.00000000001364 | 4120.42553191488 | 2140 | 10.7 | 83.54753150363702 | 4139.75 | 2340.425531914894 | 40.675531914879684 | 60 |  | 24.76851851851852 | 2140 | 2022 | 2 | 2022_02_Asomata_english.xlsx
9 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 54 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 82.9 | 4180.000000000013 | 41.83 | 3603.6 | -339.99999999998727 | 3389.2691489361832 | 1973.95 | 10.67 | 84.08970607443119 | 3306.9 | 1755.3191489361702 | 142.3691489361836 | 60 |  | 22.84664351851852 | 1973.95 | 2022 | 2 | 2022_02_Asomata_english.xlsx
10 | 0 | 190 | 190 | 0 | 0 | 5 | 190 | 50 | 0 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.4 | 5360.00000000002 | 41.75 | 3510 | 1180.0000000000073 | 4269.212765957454 | 1919 | 10.1 | 87.76247189936385 | 4292.4 | 1170.212765957447 | 36.81276595745476 | 60 |  | 22.21064814814815 | 1919 | 2022 | 2 | 2022_02_Asomata_english.xlsx
11 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 40 | 2.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.6 | 8239.999999999993 | 41.74 | 3498.3 | 2879.9999999999727 | 5397.844559585465 | 808 | 10.1 | 85.29028959233953 | 5238.52 | 1709.844559585492 | 159.32455958546416 | 0 |  | 9.351851851851851 | 808 | 2022 | 2 | 2022_02_Asomata_english.xlsx
12 | 0 | 115 | 115 | 0 | 0 | 5 | 115 | 45 | 0 | 2.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.4 | 10160 | 41.95 | 3744 | 1920.0000000000273 | 4220.675257731986 | 1161.5 | 10.1 | 83.71811835561435 | 4160.05 | 1139.1752577319587 | 60.625257731986494 | 0 |  | 13.443287037037036 | 1161.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
13 | 180 | 0 | 180 | 0 | 0 | 5 | 180 | 50 | 4.0200000000040745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 85.2 | 9680.000000000015 | 41.87 | 3650.4 | -480.00000000000546 | 3678.4255319148883 | 1818 | 10.1 | 84.10570223689035 | 3642.7 | 2340.425531914894 | 95.7255319148885 | 60 |  | 21.041666666666668 | 1818 | 2022 | 2 | 2022_02_Asomata_english.xlsx
14 | 100 | 215 | 315 | 0 | 0 | 4 | 315 | 80 | 2.5499999999956344 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.65 | 8360.00000000002 | 41.81 | 3580.2 | -1319.9999999999945 | 4201.9255319149 | 3181.5 | 10.1 | 85.19030097617029 | 4197.5 | 2340.425531914894 | 64.4255319148997 | 60 |  | 36.822916666666664 | 3181.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
15 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 84.6 | 8239.999999999993 | 41.76 | 3521.7 | -120.00000000002728 | 3477.9893617021003 | 656.5 | 10.1 | 85.29028959233953 | 3493 | 2941.4893617021276 | 44.98936170210027 | 60 |  | 7.59837962962963 | 656.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
16 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.0800000000017462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 84.5 | 8000.000000000007 | 41.37 | 3065.4 | -239.99999999998545 | 2227.638297872355 | 707 | 10.1 | 85.49097262667443 | 2197.3 | 1760.6382978723404 | 90.33829787235527 | 60 |  | 8.18287037037037 | 707 | 2022 | 2 | 2022_02_Asomata_english.xlsx
17 | 0 | 110 | 110 | 0 | 0 | 5 | 110 | 54 | 0 | 2.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 17 | 84.55 | 8120 | 41.5 | 3217.5 | 119.99999999999272 | 1208.9999999999927 | 1089 | 9.9 | 87.11557407209581 | 1011.7 | 0 | 197.2999999999928 | 0 |  | 12.604166666666666 | 1089 | 2022 | 2 | 2022_02_Asomata_english.xlsx
18 | 40 | 95 | 135 | 0 | 0 | 5 | 135 | 80 | 1 | 2.279999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 83.95 | 6680.000000000014 | 41.65 | 3393 | -1439.9999999999864 | 2646.904255319163 | 1363.5 | 10.1 | 86.61183162416361 | 2550.45 | 2723.4042553191493 | 96.45425531916317 | 0 |  | 15.78125 | 1363.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.45 | 5480.000000000014 | 41.56 | 3287.7 | -1200 | 2469.7659574468084 | 707 | 10.1 | 87.65660643265774 | 2469.6 | 2962.7659574468084 | 60.165957446808534 | 60 |  | 8.18287037037037 | 707 | 2022 | 2 | 2022_02_Asomata_english.xlsx
20 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 40 | 0 | 2.0200000000040745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.05 | 4520 | 41.53 | 3252.6 | -960.0000000000136 | 2560.6578947368284 | 757.5 | 10.1 | 88.51075119692239 | 2426.4 | 2763.157894736842 | 134.25789473682835 | 0 |  | 8.76736111111111 | 757.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
21 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 82.95 | 4290.000000000006 | 41.5 | 3217.5 | -229.99999999999363 | 515.5000000000064 | 745.5 | 10.65 | 84.14475456728977 | 574 | 0 | 21.500000000006366 | 80 |  | 8.628472222222221 | 745.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
22 | 0 | 70 | 70 | 0 | 0 | 5 | 70 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.85 | 6439.999999999993 | 41.34 | 3030.3 | 2149.9999999999864 | 4540.6734693877415 | 707 | 10.1 | 86.81878940582232 | 4456.8 | 1683.673469387755 | 83.87346938774135 | 0 |  | 8.18287037037037 | 707 | 2022 | 2 | 2022_02_Asomata_english.xlsx
23 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.7 | 6080.000000000014 | 41.18 | 2843.1 | -359.9999999999791 | 3550.2706185567217 | 776.25 | 10.35 | 85.0264715763621 | 3540.5 | 3134.020618556701 | 69.77061855672173 | 60 |  | 8.984375 | 776.25 | 2022 | 2 | 2022_02_Asomata_english.xlsx
24 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 36 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.3 | 5120 | 41.34 | 3030.3 | -960.0000000000136 | 3106.0106382978583 | 757.5 | 10.1 | 87.97497183132359 | 2807 | 3308.510638297872 | 299.01063829785835 | 0 |  | 8.76736111111111 | 757.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
25 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 49 | 2.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.6 | 5839.999999999993 | 41.51 | 3229.2 | 719.9999999999927 | 3459.069892473111 | 959.5 | 10.1 | 87.34053693830923 | 3450 | 1779.5698924731182 | 69.06989247311094 | 60 |  | 11.105324074074074 | 959.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
26 | 0 | 120 | 120 | 0 | 0 | 5 | 120 | 55 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.5 | 5600.000000000007 | 41.55 | 3276 | -239.99999999998545 | 960.0000000000146 | 1200 | 10 | 88.42650602409638 | 720.3 | 0 | 239.7000000000146 | 0 |  | 13.88888888888889 | 1200 | 2022 | 2 | 2022_02_Asomata_english.xlsx
27 | 15 | 0 | 15 | 0 | 0 | 3 | 15 | 15 | 0.1500000000014552 | 0 | 0 | 0 | 0 | 5.67 | 0 | 0 | 0 | 5.67 | 1 | 0 | ΒΛΑΒΗ Κ.Γ. ΔΕΔΔΗΕ 20KV | 27 | 83.5 | 5600.000000000007 | 41.1 | 2749.5 | 0 | 1188.342105263158 | 151.5 | 10.1 | 87.55099606346177 | 644 | 1036.842105263158 | 544.3421052631579 | 0 |  | 1.7534722222222223 | 151.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
28 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 50 | 0 | 5.400000000001455 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 7.5 | 0 | 3 | ΒΛΑΒΗ Κ.Γ. ΔΕΔΔΗΕ 20KV | 28 | 83.45 | 5480.000000000014 | 41.85 | 3627 | -119.99999999999363 | 4174.776595744687 | 2523.5 | 10.3 | 85.95453640483913 | 4060 | 1771.276595744681 | 174.77659574468726 | 60 |  | 29.207175925925927 | 2523.5 | 2022 | 2 | 2022_02_Asomata_english.xlsx
1 | 355 | 265 | 620 | 0 | 0 | 4 | 620 | 80 | 8.779999999998836 | 7.2299999999959255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 83.25 | 5000.000000000007 | 41.87 | 3650.4 | -480.00000000000637 | 5781.999999999994 | 6262 | 10.1 | 88.08160816081609 | 5778.25 | 0 | 63.74999999999363 | 60 |  | 72.47685185185185 | 6262 | 2022 | 3 | 2022_03_Asomata_english.xlsx
2 | 0 | 210 | 210 | 0.5 | 0.0021999999999999993 | 5 | 210 | 55 | 0 | 4.059999999997672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.95 | 9080.000000000015 | 41.79 | 3556.8 | 4080.0000000000073 | 6148.500000000007 | 2068.5 | 9.85 | 86.74234589860717 | 5722.9 | 0 | 425.60000000000764 | 0 |  | 23.94097222222222 | 2068.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
3 | 310 | 205 | 515 | 0 | 0 | 5 | 515 | 110 | 6.120000000002619 | 4.110000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.25 | 7400.000000000007 | 41.56 | 3287.7 | -1680.0000000000073 | 3418.4999999999927 | 5098.5 | 9.9 | 87.73414619568464 | 3281.85 | 0 | 136.64999999999236 | 0 |  | 59.010416666666664 | 5098.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
4 | 35 | 560 | 595 | 0 | 0 | 5 | 595 | 100 | 0.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 83.35 | 5239.999999999993 | 41.86 | 3638.7 | -2160.0000000000146 | 5037.672043010738 | 6009.5 | 10.1 | 87.86859338896406 | 4907 | 1188.1720430107528 | 190.67204301073798 | 60 |  | 69.55439814814815 | 6009.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
5 | 340 | 280 | 620 | 0 | 0 | 4 | 620 | 108 | 7.75 | 18.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 83.65 | 5960.00000000002 | 41.63 | 3369.6 | 720.0000000000273 | 6982.000000000027 | 6262 | 10.1 | 87.23568635374941 | 6921.2 | 0 | 120.80000000002656 | 60 |  | 72.47685185185185 | 6262 | 2022 | 3 | 2022_03_Asomata_english.xlsx
6 | 95 | 490 | 585 | 0 | 0 | 5 | 585 | 70 | 2.599999999998545 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 6 | 82.3 | 2859.9999999999936 | 41.84 | 3615.3 | -3100.0000000000264 | 3100.9999999999736 | 6201 | 10.6 | 85.90523900931693 | 2883.85 | 0 | 277.1499999999737 | 60 |  | 71.77083333333333 | 6201 | 2022 | 3 | 2022_03_Asomata_english.xlsx
7 | 140 | 0 | 140 | 0 | 0 | 5 | 140 | 54 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 82 | 2200 | 41.46 | 3170.7 | -659.9999999999936 | 817.0000000000064 | 1477 | 10.55 | 86.95971563981043 | 672 | 0 | 205.00000000000637 | 60 |  | 17.09490740740741 | 1477 | 2022 | 3 | 2022_03_Asomata_english.xlsx
8 | 0 | 90 | 90 | 0 | 0 | 5 | 90 | 55 | 0 | 2.069999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.25 | 5000.000000000007 | 41.26 | 2936.7 | 2800.0000000000073 | 3709.0000000000073 | 909 | 10.1 | 88.08160816081609 | 3244.7 | 0 | 464.30000000000746 | 0 |  | 10.520833333333334 | 909 | 2022 | 3 | 2022_03_Asomata_english.xlsx
9 | 305 | 455 | 760 | 0 | 0 | 5 | 760 | 105 | 8 | 10.930000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 9 | 83.75 | 6200.000000000007 | 41.84 | 3615.3 | 1200 | 8876 | 7676 | 10.1 | 87.02673860200392 | 8551.4 | 0 | 384.59999999999854 | 60 |  | 88.8425925925926 | 7676 | 2022 | 3 | 2022_03_Asomata_english.xlsx
10 | 240 | 330 | 570 | 0 | 0 | 5 | 570 | 108 | 4.950000000004366 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 82 | 2200 | 41.6 | 3334.5 | -4000.0000000000073 | 2155.9999999999927 | 6156 | 10.8 | 84.94675925925925 | 2159.7 | 0 | 56.299999999992906 | 60 |  | 71.25 | 6156 | 2022 | 3 | 2022_03_Asomata_english.xlsx
11 | 105 | 0 | 105 | 0 | 0 | 5 | 105 | 49 | 2.8300000000017462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 82.95 | 4290.000000000006 | 41.22 | 2889.9 | 2090.0000000000064 | 3234.5000000000064 | 1144.5 | 10.9 | 82.21482900381983 | 3158.4 | 0 | 76.10000000000628 | 0 |  | 13.246527777777779 | 1144.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
12 | 55 | 315 | 370 | 0 | 0 | 5 | 370 | 75 | 1.4699999999938882 | 6.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 82.85 | 4069.9999999999873 | 41.74 | 3498.3 | -220.0000000000191 | 5857.425531914874 | 3737 | 10.1 | 88.94409636802115 | 5788.9 | 2340.425531914894 | 128.5255319148746 | 60 |  | 43.25231481481482 | 3737 | 2022 | 3 | 2022_03_Asomata_english.xlsx
13 | 270 | 55 | 325 | 0 | 0 | 4 | 325 | 55 | 6 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.55 | 8120 | 41.66 | 3404.7 | 4050.0000000000127 | 7332.500000000013 | 3282.5 | 10.1 | 85.39051319938106 | 7178 | 0 | 154.50000000001273 | 0 |  | 37.991898148148145 | 3282.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
14 | 240 | 350 | 590 | 0 | 0 | 5 | 590 | 110 | 5.200000000004366 | 7.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 14 | 83.65 | 5960.00000000002 | 41.65 | 3393 | -2159.99999999998 | 5564.95744680853 | 5959 | 10.1 | 87.23568635374941 | 5599.1 | 1765.9574468085107 | 25.857446808530767 | 60 |  | 68.9699074074074 | 5959 | 2022 | 3 | 2022_03_Asomata_english.xlsx
15 | 305 | 110 | 415 | 0 | 0 | 4 | 415 | 80 | 7.599999999998545 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 83.9 | 6560.00000000002 | 41.77 | 3533.4 | 600 | 4791.5 | 4191.5 | 10.1 | 86.71518703182966 | 4526.2 | 0 | 265.3 | 0 |  | 48.51273148148148 | 4191.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
16 | 170 | 275 | 445 | 0 | 0 | 4 | 445 | 100 | 4 | 6.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.5 | 8000.000000000007 | 41.81 | 3580.2 | 1439.9999999999873 | 5934.499999999987 | 4494.5 | 10.1 | 85.49097262667443 | 5759.7 | 0 | 234.79999999998745 | 60 |  | 52.019675925925924 | 4494.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
17 | 155 | 25 | 180 | 0 | 0 | 5 | 180 | 100 | 3.599999999998545 | 0.41999999999825377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 85.15 | 9560.00000000002 | 41.63 | 3369.6 | 1560.0000000000127 | 5104.818181818195 | 1863 | 10.35 | 82.16926685363381 | 4832 | 1681.8181818181818 | 272.8181818181947 | 0 |  | 21.5625 | 1863 | 2022 | 3 | 2022_03_Asomata_english.xlsx
18 | 260 | 445 | 705 | 0 | 0 | 5 | 705 | 110 | 6.099999999998545 | 10.12999999999738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.05 | 6920 | 41.86 | 3638.7 | -2640.00000000002 | 7356.775641025621 | 7155.75 | 10.15 | 85.98021356232024 | 7377.8 | 2841.025641025641 | 38.97564102561955 | 60 |  | 82.82118055555556 | 7155.75 | 2022 | 3 | 2022_03_Asomata_english.xlsx
19 | 220 | 0 | 220 | 0 | 0 | 5 | 220 | 45 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.95 | 9080.000000000015 | 41.79 | 3556.8 | 2160.0000000000146 | 6075.877551020423 | 2222 | 10.1 | 84.59525812883966 | 5943.2 | 1693.8775510204082 | 132.6775510204243 | 0 |  | 25.71759259259259 | 2222 | 2022 | 3 | 2022_03_Asomata_english.xlsx
20 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 40 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.15 | 9560.00000000002 | 40.94 | 2562.3 | 480.00000000000546 | 2886.717171717177 | 735 | 9.8 | 86.78080734031734 | 2776.8 | 1671.7171717171716 | 109.9171717171771 | 0 |  | 8.506944444444445 | 735 | 2022 | 3 | 2022_03_Asomata_english.xlsx
21 | 100 | 0 | 100 | 0 | 0 | 6 | 100 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.05 | 9320 | 41.05 | 2691 | -240.00000000002 | 3026.4102564102363 | 1010 | 10.1 | 84.3987534641966 | 2977.5 | 2256.4102564102564 | 108.91025641023634 | 60 |  | 11.689814814814815 | 1010 | 2022 | 3 | 2022_03_Asomata_english.xlsx
22 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 40 | 0 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85.15 | 9560.00000000002 | 41.04 | 2679.3 | 240.00000000002 | 5623.9162303665125 | 808 | 10.1 | 84.20315959753565 | 5350.9 | 4575.9162303664925 | 273.0162303665129 | 0 |  | 9.351851851851851 | 808 | 2022 | 3 | 2022_03_Asomata_english.xlsx
23 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 40 | 2.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.55 | 8120 | 41.34 | 3030.3 | -1440.00000000002 | 4166.415343915323 | 1262.5 | 10.1 | 85.39051319938106 | 4119.85 | 4343.915343915343 | 106.56534391532296 | 60 |  | 14.612268518518519 | 1262.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
24 | 40 | 145 | 185 | 0 | 0 | 4 | 185 | 94 | 0.6500000000014552 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.1 | 7039.999999999993 | 41.87 | 3650.4 | -1080.0000000000073 | 3640.466321243516 | 1850 | 10 | 87.16627078384799 | 3291.8 | 2870.4663212435235 | 348.66632124351645 | 0 |  | 21.412037037037038 | 1850 | 2022 | 3 | 2022_03_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.75 | 8600.000000000007 | 41.34 | 3030.3 | 1560.0000000000146 | 4831.102564102579 | 707 | 10.1 | 84.9910254183313 | 4824.45 | 2564.102564102564 | 16.652564102579163 | 10 |  | 8.18287037037037 | 707 | 2022 | 3 | 2022_03_Asomata_english.xlsx
26 | 0 | 70 | 70 | 0 | 0 | 5 | 70 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.4 | 7760.00000000002 | 41.27 | 2948.4 | -839.9999999999873 | 3845.723404255332 | 707 | 10.1 | 85.69260227909582 | 3686.5 | 3978.723404255319 | 179.22340425533184 | 20 |  | 8.18287037037037 | 707 | 2022 | 3 | 2022_03_Asomata_english.xlsx
27 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.9700000000011642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.6 | 8239.999999999993 | 41.21 | 2878.2 | 479.9999999999727 | 3440.8071065989575 | 707 | 10.1 | 85.29028959233953 | 3419.55 | 2253.807106598985 | 81.25710659895731 | 60 |  | 8.18287037037037 | 707 | 2022 | 3 | 2022_03_Asomata_english.xlsx
28 | 60 | 155 | 215 | 0 | 0 | 4 | 215 | 100 | 1.1999999999970896 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 85 | 9200.000000000007 | 41.83 | 3603.6 | 960.0000000000146 | 5963.132653061239 | 2171.5 | 10.1 | 84.49689154962007 | 5872.5 | 2831.632653061224 | 90.63265306123867 | 0 |  | 25.13310185185185 | 2171.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
29 | 220 | 140 | 360 | 0 | 0 | 5 | 360 | 55 | 5.30000000000291 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.4 | 7760.00000000002 | 42.07 | 3884.4 | -1439.9999999999873 | 4467.794871794884 | 3636 | 10.1 | 85.69260227909582 | 4294 | 2271.7948717948716 | 233.79487179488387 | 60 |  | 42.083333333333336 | 3636 | 2022 | 3 | 2022_03_Asomata_english.xlsx
30 | 175 | 380 | 555 | 0 | 0 | 4 | 555 | 110 | 3.599999999998545 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 30 | 84.25 | 7400.000000000007 | 41.84 | 3615.3 | -360.00000000001273 | 7901.749999999987 | 5605.5 | 10.1 | 85.99683637002754 | 7829.95 | 2656.25 | 131.79999999998654 | 60 |  | 64.87847222222223 | 5605.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
31 | 100 | 45 | 145 | 0 | 0 | 4 | 145 | 90 | 2.099999999998545 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.05 | 6920 | 41.81 | 3580.2 | -480.0000000000073 | 984.4999999999927 | 1464.5 | 10.1 | 86.4058581839159 | 722.7 | 0 | 321.7999999999928 | 60 |  | 16.95023148148148 | 1464.5 | 2022 | 3 | 2022_03_Asomata_english.xlsx
1 | 35 | 0 | 35 | 0 | 0 | 4 | 35 | 40 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85 | 9200.000000000007 | 41.19 | 2854.8 | 2280.0000000000073 | 7289.750000000007 | 353.5 | 10.1 | 84.49689154962007 | 7148.4 | 4656.25 | 201.35000000000764 | 60 |  | 4.091435185185185 | 353.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
2 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 50 | 0 | 3.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.1 | 9439.999999999993 | 41.33 | 3018.6 | 239.99999999998545 | 6074.3404255319 | 1212 | 10.1 | 84.30084307734718 | 5788.9 | 4622.340425531915 | 285.4404255319005 | 0 |  | 14.027777777777779 | 1212 | 2022 | 4 | 2022_04_Asomata_english.xlsx
3 | 165 | 0 | 165 | 0 | 0 | 5 | 165 | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.15 | 7160.00000000002 | 41.91 | 3697.2 | -2279.9999999999727 | 6097.026315789501 | 1666.5 | 10.1 | 86.20086207909047 | 5986 | 6710.526315789473 | 171.0263157895006 | 60 |  | 19.288194444444443 | 1666.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
4 | 370 | 630 | 1000 | 0 | 0 | 4 | 1000 | 110 | 7.030000000006112 | 11.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84.8 | 8720 | 41.93 | 3720.6 | 1559.99999999998 | 11660 | 10100 | 10.1 | 84.89173683723513 | 11711.7 | 0 | 8.299999999979264 | 60 |  | 116.89814814814815 | 10100 | 2022 | 4 | 2022_04_Asomata_english.xlsx
5 | 245 | 85 | 330 | 0 | 0 | 4 | 330 | 100 | 5.069999999999709 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.8 | 8720 | 41.97 | 3767.4 | 0 | 5441.808290155441 | 3333 | 10.1 | 84.89173683723513 | 5140.5 | 2108.8082901554403 | 301.3082901554408 | 0 |  | 38.576388888888886 | 3333 | 2022 | 4 | 2022_04_Asomata_english.xlsx
6 | 35 | 165 | 200 | 0 | 0 | 5 | 200 | 85 | 1 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.4 | 7760.00000000002 | 41.1 | 2749.5 | -959.99999999998 | 3879.1489361702324 | 2020 | 10.1 | 85.69260227909582 | 3730.3 | 2819.1489361702124 | 208.84893617023226 | 60 |  | 23.37962962962963 | 2020 | 2022 | 4 | 2022_04_Asomata_english.xlsx
7 | 55 | 130 | 185 | 0 | 0 | 4 | 185 | 104 | 1 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 7 | 83.6 | 5839.999999999993 | 41.44 | 3147.3 | -1920.0000000000273 | 4347.436170212739 | 1868.5 | 10.1 | 87.34053693830923 | 4089.6 | 4398.936170212766 | 257.83617021273903 | 0 |  | 21.62615740740741 | 1868.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
8 | 0 | 155 | 155 | 0 | 0 | 4 | 155 | 55 | 0 | 3.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.85 | 8839.999999999993 | 41.36 | 3053.7 | 3000 | 10283.58510638298 | 1565.5 | 10.1 | 84.79267996811352 | 10209.6 | 5718.085106382979 | 133.9851063829792 | 60 |  | 18.119212962962962 | 1565.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
9 | 180 | 140 | 320 | 0 | 0 | 4 | 320 | 54 | 3.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.6 | 8239.999999999993 | 41.76 | 3521.7 | -600 | 7092.732984293194 | 3232 | 10.1 | 85.29028959233953 | 6870.5 | 4460.732984293194 | 222.23298429319402 | 0 |  | 37.407407407407405 | 3232 | 2022 | 4 | 2022_04_Asomata_english.xlsx
10 | 80 | 185 | 265 | 0 | 0 | 4 | 265 | 108 | 1.5999999999985448 | 3.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.6 | 8239.999999999993 | 41.6 | 3334.5 | 0 | 6570.117021276596 | 2676.5 | 10.1 | 85.29028959233953 | 6439.7 | 3893.617021276596 | 190.41702127659664 | 60 |  | 30.97800925925926 | 2676.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
11 | 310 | 255 | 565 | 0 | 0 | 4 | 565 | 108 | 6.549999999995634 | 5.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 85 | 9200.000000000007 | 41.9 | 3685.5 | 960.0000000000146 | 10806.284946236574 | 5706.5 | 10.1 | 84.49689154962007 | 10728 | 4139.784946236559 | 138.2849462365739 | 60 |  | 66.04745370370371 | 5706.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
12 | 210 | 405 | 615 | 0 | 0 | 4 | 615 | 110 | 4.0200000000040745 | 7.960000000006403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 12 | 84.3 | 7520 | 41.84 | 3615.3 | -1680.0000000000073 | 5629.574468085099 | 6150 | 10 | 86.75413711583924 | 5204.9 | 1159.5744680851064 | 424.67446808509976 | 0 |  | 71.18055555555556 | 6150 | 2022 | 4 | 2022_04_Asomata_english.xlsx
13 | 150 | 65 | 215 | 0 | 0 | 5 | 215 | 108 | 3.150000000001455 | 1.3399999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.85 | 8839.999999999993 | 41.88 | 3662.1 | 1319.9999999999927 | 7002.138297872333 | 2171.5 | 10.1 | 84.79267996811352 | 6767.1 | 3510.6382978723404 | 295.0382978723328 | 60 |  | 25.13310185185185 | 2171.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
14 | 70 | 180 | 250 | 0 | 0 | 4 | 250 | 110 | 1.3799999999973807 | 4.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 83.9 | 6560.00000000002 | 41.6 | 3334.5 | -2279.9999999999727 | 4723.723404255346 | 2525 | 10.1 | 86.71518703182966 | 4636.3 | 4478.723404255319 | 147.4234042553462 | 60 |  | 29.224537037037038 | 2525 | 2022 | 4 | 2022_04_Asomata_english.xlsx
15 | 110 | 85 | 195 | 0 | 0 | 4 | 195 | 110 | 2.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.8 | 8720 | 41.71 | 3463.2 | 2159.99999999998 | 6340.840206185547 | 1969.5 | 10.1 | 84.89173683723513 | 6181.35 | 2211.340206185567 | 159.4902061855464 | 0 |  | 22.79513888888889 | 1969.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
16 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 50 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85.2 | 9680.000000000015 | 41.96 | 3755.7 | 960.0000000000146 | 2626.5000000000146 | 1666.5 | 10.1 | 84.10570223689035 | 2350.6 | 0 | 335.90000000001464 | 60 |  | 19.288194444444443 | 1666.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
17 | 205 | 70 | 275 | 0 | 0 | 5 | 275 | 110 | 4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.95 | 9080.000000000015 | 42.07 | 3884.4 | -600 | 8884.946808510638 | 2777.5 | 10.1 | 84.59525812883966 | 8745.4 | 6707.446808510638 | 199.54680851063858 | 60 |  | 32.14699074074074 | 2777.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
18 | 55 | 190 | 245 | 0 | 0 | 4 | 245 | 90 | 1.3000000000029104 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 85.1 | 9439.999999999993 | 42.07 | 3884.4 | 359.9999999999782 | 3994.074468085085 | 2474.5 | 10.1 | 84.30084307734718 | 3730.3 | 1159.5744680851064 | 323.77446808508466 | 60 |  | 28.640046296296298 | 2474.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
19 | 395 | 105 | 500 | 0 | 0 | 5 | 500 | 90 | 8.94999999999709 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 84.5 | 8000.000000000007 | 41.59 | 3322.8 | -1439.9999999999854 | 5961.063829787248 | 5050 | 10.1 | 85.49097262667443 | 5914.95 | 2351.063829787234 | 106.1138297872485 | 60 |  | 58.449074074074076 | 5050 | 2022 | 4 | 2022_04_Asomata_english.xlsx
20 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 50 | 0 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.75 | 8600.000000000007 | 41.95 | 3744 | 600 | 4407.413043478261 | 3383.5 | 10.1 | 84.9910254183313 | 3791.34 | 423.9130434782609 | 616.0730434782613 | 0 |  | 39.160879629629626 | 3383.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
21 | 305 | 0 | 305 | 0 | 0 | 4 | 305 | 55 | 6.129999999997381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.7 | 8480.000000000015 | 41.87 | 3650.4 | -119.99999999999272 | 5210.500000000007 | 3080.5 | 10.1 | 85.09054652537853 | 4909.8 | 2250 | 300.7000000000071 | 0 |  | 35.65393518518518 | 3080.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
22 | 0 | 145 | 145 | 0 | 0 | 5 | 145 | 45 | 0 | 3.9800000000032014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.7 | 8480.000000000015 | 41.48 | 3194.1 | 0 | 3746.4148936170213 | 1464.5 | 10.1 | 85.09054652537853 | 3540.5 | 2281.9148936170213 | 265.91489361702133 | 60 |  | 16.95023148148148 | 1464.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
23 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 55 | 3.3500000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.25 | 9800.000000000007 | 41.64 | 3381.3 | 1319.9999999999927 | 6903.196891191703 | 1749 | 10.6 | 80.04580652197623 | 6975.15 | 3834.1968911917097 | 28.046891191703253 | 100 |  | 20.243055555555557 | 1749 | 2022 | 4 | 2022_04_Asomata_english.xlsx
24 | 220 | 250 | 470 | 0 | 0 | 4 | 470 | 110 | 4.029999999998836 | 4.819999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.7 | 8480.000000000015 | 42.02 | 3825.9 | -1319.9999999999927 | 4378.612903225814 | 4747 | 10.1 | 85.09054652537853 | 4172 | 951.6129032258065 | 266.6129032258141 | 60 |  | 54.942129629629626 | 4747 | 2022 | 4 | 2022_04_Asomata_english.xlsx
25 | 125 | 60 | 185 | 0 | 0 | 4 | 185 | 90 | 3.1199999999953434 | 1.4899999999979627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.6 | 8239.999999999993 | 41.93 | 3720.6 | -240.00000000002183 | 4434.6224489795695 | 1868.5 | 10.1 | 85.29028959233953 | 4086.6 | 2806.122448979592 | 408.0224489795696 | 60 |  | 21.62615740740741 | 1868.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
26 | 0 | 145 | 145 | 0 | 0 | 3 | 145 | 54 | 0 | 3.110000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85.2 | 9680.000000000015 | 41.68 | 3428.1 | 1440.0000000000218 | 3877.9042553191707 | 1464.5 | 10.1 | 84.10570223689035 | 3664.6 | 973.4042553191489 | 213.30425531917035 | 0 |  | 16.95023148148148 | 1464.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
27 | 235 | 145 | 380 | 0 | 0 | 4 | 380 | 109 | 4.42000000000553 | 2.7999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.75 | 8600.000000000007 | 41.9 | 3685.5 | -1080.0000000000073 | 4417.574468085099 | 3838 | 10.1 | 84.9910254183313 | 4073.4 | 1659.5744680851064 | 404.17446808509976 | 60 |  | 44.4212962962963 | 3838 | 2022 | 4 | 2022_04_Asomata_english.xlsx
28 | 125 | 225 | 350 | 0 | 0 | 3 | 350 | 108 | 2.6499999999941792 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 85.4 | 10160 | 41.71 | 3463.2 | 1560.0000000000127 | 7712.021276595758 | 3535 | 10.1 | 83.71811835561435 | 7519 | 2617.021276595745 | 253.02127659575763 | 60 |  | 40.914351851851855 | 3535 | 2022 | 4 | 2022_04_Asomata_english.xlsx
29 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 54 | 3.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.15 | 9560.00000000002 | 41.72 | 3474.9 | -600 | 7067.829787234043 | 1854 | 10.3 | 82.5681467898165 | 6905.8 | 5813.829787234043 | 222.0297872340434 | 60 |  | 21.458333333333336 | 1854 | 2022 | 4 | 2022_04_Asomata_english.xlsx
30 | 50 | 205 | 255 | 0 | 0 | 4 | 255 | 100 | 1.0500000000029104 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.75 | 8600.000000000007 | 42 | 3802.5 | -960.0000000000127 | 5932.704301075256 | 2575.5 | 10.1 | 84.9910254183313 | 5733 | 4317.204301075269 | 259.7043010752559 | 60 |  | 29.80902777777778 | 2575.5 | 2022 | 4 | 2022_04_Asomata_english.xlsx
1 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 55 | 3.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85.3 | 9920 | 41.87 | 3650.4 | 1319.9999999999927 | 4773.563451776642 | 1616 | 10.1 | 83.91146273980748 | 4426.59 | 1837.5634517766496 | 346.9734517766419 | 0 |  | 18.703703703703702 | 1616 | 2022 | 5 | 2022_05_Asomata_english.xlsx
2 | 100 | 400 | 500 | 0 | 0 | 5 | 500 | 100 | 2.970000000001164 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 85.25 | 9800.000000000007 | 41.97 | 3767.4 | -119.99999999999272 | 7265.106382978731 | 5050 | 10.1 | 84.00847021118297 | 7219.7 | 2335.1063829787236 | 105.40638297873102 | 60 |  | 58.449074074074076 | 5050 | 2022 | 5 | 2022_05_Asomata_english.xlsx
3 | 310 | 170 | 480 | 0 | 0 | 4 | 480 | 100 | 6.779999999998836 | 3.8700000000026193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 85 | 9200.000000000007 | 42.02 | 3825.9 | -600 | 6561.829787234043 | 4848 | 10.1 | 84.49689154962007 | 6518.9 | 2313.8297872340427 | 102.92978723404303 | 60 |  | 56.111111111111114 | 4848 | 2022 | 5 | 2022_05_Asomata_english.xlsx
4 | 330 | 660 | 990 | 0 | 0 | 4 | 990 | 110 | 6.919999999998254 | 14.779999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 85.24 | 9775.999999999995 | 41.85 | 3627 | 575.9999999999873 | 11739.893617021264 | 9999 | 10.1 | 84.0278986270505 | 11636.2 | 1164.8936170212767 | 103.6936170212648 | 0 |  | 115.72916666666667 | 9999 | 2022 | 5 | 2022_05_Asomata_english.xlsx
5 | 355 | 295 | 650 | 0 | 0 | 3 | 650 | 109 | 7.200000000004366 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.6 | 8239.999999999993 | 41.98 | 3779.1 | -1536 | 5599.680628272249 | 6565 | 10.1 | 85.29028959233953 | 5277.3 | 570.6806282722513 | 322.38062827224985 | 0 |  | 75.98379629629629 | 6565 | 2022 | 5 | 2022_05_Asomata_english.xlsx
6 | 110 | 385 | 495 | 0 | 0 | 4 | 495 | 90 | 2.6999999999970896 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 |  | 6 | 84.4 | 7760.00000000002 | 41.89 | 3673.8 | -479.9999999999727 | 4519.500000000027 | 4999.5 | 10.1 | 85.69260227909582 | 4365.4 | 0 | 214.10000000002765 | 60 |  | 57.864583333333336 | 4999.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
7 | 310 | 0 | 310 | 0 | 0 | 4 | 310 | 50 | 6.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 83.55 | 5720 | 42 | 3802.5 | -2040.00000000002 | 3935.0860215053563 | 3131 | 10.1 | 87.44563987084629 | 3955 | 2844.0860215053763 | 40.08602150535626 | 60 |  | 36.238425925925924 | 3131 | 2022 | 5 | 2022_05_Asomata_english.xlsx
8 | 125 | 340 | 465 | 0 | 0 | 4 | 465 | 100 | 3.1999999999970896 | 7.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 83.9 | 6560.00000000002 | 41.87 | 3650.4 | 840.00000000002 | 6111.768817204321 | 4696.5 | 10.1 | 86.71518703182966 | 5964 | 575.2688172043011 | 207.76881720432084 | 60 |  | 54.357638888888886 | 4696.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
9 | 240 | 0 | 240 | 0 | 0 | 3 | 240 | 54 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 83.8 | 6320 | 41.8 | 3568.5 | -240.00000000002 | 2585.0416666666465 | 2424 | 10.1 | 86.9226396323843 | 2369.1 | 401.0416666666667 | 215.9416666666466 | 0 |  | 28.055555555555557 | 2424 | 2022 | 5 | 2022_05_Asomata_english.xlsx
10 | 170 | 325 | 495 | 0 | 0 | 4 | 495 | 110 | 3.4500000000043656 | 6.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.25 | 5000.000000000007 | 41.82 | 3591.9 | -1319.9999999999927 | 6050.561827956996 | 5123.25 | 10.35 | 85.95403308446787 | 5999 | 2247.311827956989 | 111.56182795699624 | 60 |  | 59.296875 | 5123.25 | 2022 | 5 | 2022_05_Asomata_english.xlsx
11 | 310 | 0 | 310 | 0 | 0 | 4 | 310 | 54 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.15 | 7160.00000000002 | 42 | 3802.5 | 2160.0000000000127 | 10072.914893617035 | 3131 | 10.1 | 86.20086207909047 | 9939.75 | 4781.914893617021 | 193.16489361703498 | 60 |  | 36.238425925925924 | 3131 | 2022 | 5 | 2022_05_Asomata_english.xlsx
12 | 115 | 290 | 405 | 0 | 0 | 3 | 405 | 110 | 2.680000000000291 | 6.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.8 | 8720 | 41.98 | 3779.1 | 1559.99999999998 | 9198.372340425512 | 4090.5 | 10.1 | 84.89173683723513 | 9113.25 | 3547.872340425532 | 115.12234042551245 | 30 |  | 47.34375 | 4090.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
13 | 360 | 160 | 520 | 0 | 0 | 4 | 520 | 110 | 7.619999999995343 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.2 | 7280.000000000014 | 41.95 | 3744 | -1439.9999999999864 | 4407.744680851078 | 5252 | 10.1 | 86.09872835624795 | 4197.5 | 595.7446808510638 | 270.24468085107765 | 60 |  | 60.78703703703704 | 5252 | 2022 | 5 | 2022_05_Asomata_english.xlsx
14 | 0 | 335 | 335 | 0 | 0 | 3 | 335 | 50 | 0 | 7.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.85 | 6439.999999999993 | 41.88 | 3662.1 | -840.0000000000209 | 5327.283783783763 | 3383.5 | 10.1 | 86.81878940582232 | 5155.15 | 2783.7837837837837 | 232.13378378376274 | 60 |  | 39.160879629629626 | 3383.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
15 | 345 | 0 | 345 | 0 | 0 | 3 | 345 | 55 | 6.450000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.7 | 6080.000000000014 | 41.86 | 3638.7 | -359.9999999999791 | 6730.882978723425 | 3484.5 | 10.1 | 87.13108720944037 | 6730.6 | 3606.3829787234044 | 60.282978723425 | 60 |  | 40.329861111111114 | 3484.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
16 | 225 | 350 | 575 | 0 | 0 | 4 | 575 | 110 | 5.299999999995634 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 16 | 84.6 | 8239.999999999993 | 41.93 | 3720.6 | 2159.999999999979 | 9371.755319148915 | 5807.5 | 10.1 | 85.29028959233953 | 9316.8 | 1404.2553191489362 | 114.9553191489158 | 60 |  | 67.21643518518519 | 5807.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
17 | 360 | 165 | 525 | 0 | 0 | 3 | 525 | 108 | 8.099999999998545 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.45 | 7880.000000000014 | 41.84 | 3615.3 | -359.9999999999791 | 7584.300518134736 | 5250 | 10 | 86.44758539458186 | 7540.6 | 2694.300518134715 | 43.70051813473583 | 0 |  | 60.763888888888886 | 5250 | 2022 | 5 | 2022_05_Asomata_english.xlsx
18 | 65 | 395 | 460 | 0 | 0 | 3 | 460 | 100 | 1.8000000000029104 | 8.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 83.9 | 6560.00000000002 | 42.08 | 3896.1 | -1319.9999999999936 | 5187.702127659581 | 4646 | 10.1 | 86.71518703182966 | 5197.6 | 1861.7021276595744 | 50.10212765958022 | 60 |  | 53.773148148148145 | 4646 | 2022 | 5 | 2022_05_Asomata_english.xlsx
19 | 370 | 115 | 485 | 0 | 0 | 3 | 485 | 100 | 8.150000000001455 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 83.7 | 6080.000000000014 | 41.6 | 3334.5 | -480.00000000000637 | 9991.247354497347 | 5116.75 | 10.55 | 83.41459533794765 | 10027 | 5354.4973544973545 | 24.24735449734726 | 60 |  | 59.22164351851852 | 5116.75 | 2022 | 5 | 2022_05_Asomata_english.xlsx
20 | 0 | 340 | 340 | 0 | 0 | 4 | 340 | 54 | 0 | 6.580000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.1 | 7039.999999999993 | 41.16 | 2819.7 | 959.9999999999791 | 5718.468085106362 | 3434 | 10.1 | 86.3032383998495 | 5599.1 | 1324.4680851063831 | 179.36808510636274 | 60 |  | 39.745370370370374 | 3434 | 2022 | 5 | 2022_05_Asomata_english.xlsx
21 | 425 | 0 | 425 | 0 | 0 | 3 | 425 | 54 | 8.089999999996508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.29 | 2971.8 | 480.0000000000073 | 7128.882978723412 | 4292.5 | 10.1 | 85.89518526320718 | 7119.5 | 2356.3829787234044 | 69.38297872341172 | 60 |  | 49.68171296296296 | 4292.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
22 | 0 | 475 | 475 | 0 | 0 | 3 | 475 | 55 | 0 | 9.019999999996799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.3 | 7520 | 41.55 | 3276 | 0 | 7412.083333333334 | 4797.5 | 10.1 | 85.89518526320718 | 7457.1 | 2614.5833333333335 | 14.983333333333576 | 60 |  | 55.526620370370374 | 4797.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
23 | 400 | 210 | 610 | 0 | 0 | 4 | 610 | 108 | 9.55000000000291 | 5.0900000000037835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.3 | 7520 | 41.81 | 3580.2 | 0 | 7291.8900523560205 | 6161 | 10.1 | 85.89518526320718 | 7067 | 1130.890052356021 | 224.89005235602053 | 0 |  | 71.30787037037037 | 6161 | 2022 | 5 | 2022_05_Asomata_english.xlsx
24 | 0 | 450 | 450 | 0 | 0 | 3 | 450 | 50 | 0 | 9.009999999994761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 83.8 | 6320 | 41.54 | 3264.3 | -1200 | 5681.78756476684 | 4545 | 10.1 | 86.9226396323843 | 5483.2 | 2336.7875647668398 | 198.58756476683993 | 0 |  | 52.604166666666664 | 4545 | 2022 | 5 | 2022_05_Asomata_english.xlsx
25 | 500 | 30 | 530 | 0 | 0 | 3 | 530 | 100 | 10.010000000002037 | 0.7000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 83.9 | 6560.00000000002 | 41.79 | 3556.8 | 240.00000000002 | 5540.00000000002 | 5300 | 10 | 87.58233890214795 | 5241.4 | 0 | 298.6000000000204 | 0 |  | 61.342592592592595 | 5300 | 2022 | 5 | 2022_05_Asomata_english.xlsx
26 | 45 | 500 | 545 | 0 | 0 | 3 | 545 | 90 | 1.0499999999956344 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.1 | 7039.999999999993 | 42.08 | 3896.1 | 479.9999999999727 | 7094.102564102537 | 5450 | 10 | 87.16627078384799 | 7007.2 | 1164.102564102564 | 86.90256410253733 | 0 |  | 63.0787037037037 | 5450 | 2022 | 5 | 2022_05_Asomata_english.xlsx
27 | 500 | 0 | 500 | 0 | 0 | 3 | 500 | 55 | 10.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.4 | 7760.00000000002 | 41.82 | 3591.9 | 720.0000000000273 | 5720.000000000027 | 5000 | 10 | 86.54952830188678 | 5637.45 | 0 | 142.55000000002747 | 60 |  | 57.870370370370374 | 5000 | 2022 | 5 | 2022_05_Asomata_english.xlsx
28 | 0 | 540 | 540 | 0 | 0 | 3 | 540 | 50 | 0 | 11.119999999995343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 83.75 | 6200.000000000007 | 41.85 | 3627 | -1560.0000000000127 | 6511.021276595732 | 5454 | 10.1 | 87.02673860200392 | 6453.2 | 2617.021276595745 | 117.82127659573234 | 60 |  | 63.125 | 5454 | 2022 | 5 | 2022_05_Asomata_english.xlsx
29 | 550 | 20 | 570 | 0 | 0 | 3 | 570 | 70 | 11.060000000004948 | 0.6100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 82.75 | 3850 | 42.05 | 3861 | -2350.0000000000073 | 6371.037634408594 | 6070.5 | 10.65 | 84.55773495780409 | 6380.2 | 2650.537634408602 | 50.83763440859457 | 60 |  | 70.26041666666667 | 6070.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
30 | 50 | 565 | 615 | 0 | 0 | 3 | 615 | 104 | 1.0599999999976717 | 11.17000000000553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.3 | 7520 | 41.97 | 3767.4 | 3670 | 9881.5 | 6211.5 | 10.1 | 85.89518526320718 | 9926.1 | 0 | 15.399999999999636 | 60 |  | 71.89236111111111 | 6211.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
31 | 480 | 55 | 535 | 0 | 0 | 3 | 535 | 74 | 9.529999999998836 | 1.4899999999979627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 84.8 | 8720 | 41.96 | 3755.7 | 1200 | 7759.75 | 5403.5 | 10.1 | 84.89173683723513 | 7803 | 1156.25 | 16.75 | 60 |  | 62.54050925925926 | 5403.5 | 2022 | 5 | 2022_05_Asomata_english.xlsx
1 | 420 | 195 | 615 | 0 | 0 | 3 | 615 | 100 | 9.200000000004366 | 4.669999999998254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 1 | 84.9 | 8960.00000000002 | 41.72 | 3474.9 | 240.00000000002 | 8185.54255319151 | 6211.5 | 10.1 | 84.6938540007847 | 7964.96 | 1734.0425531914893 | 220.58255319151067 | 0 |  | 71.89236111111111 | 6211.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
2 | 240 | 450 | 690 | 0 | 0 | 3 | 690 | 100 | 5.5 | 9.440000000002328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 2 | 85.1 | 9439.999999999993 | 42.02 | 3825.9 | 479.9999999999727 | 9188.361702127633 | 6969 | 10.1 | 84.30084307734718 | 9255 | 1739.3617021276596 | 13.36170212763318 | 80 |  | 80.65972222222223 | 6969 | 2022 | 6 | 2022_06_Asomata_english.xlsx
3 | 460 | 100 | 560 | 0 | 0 | 3 | 560 | 100 | 9.099999999998545 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.9 | 8960.00000000002 | 41.85 | 3627 | -479.9999999999727 | 7748.164948453636 | 5656 | 10.1 | 84.6938540007847 | 7552.5 | 2572.1649484536083 | 255.6649484536356 | 60 |  | 65.46296296296296 | 5656 | 2022 | 6 | 2022_06_Asomata_english.xlsx
4 | 80 | 460 | 540 | 0 | 0 | 3 | 540 | 90 | 1.7999999999956344 | 8.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 85.1 | 9439.999999999993 | 41.53 | 3252.6 | 479.9999999999727 | 7540.217616580283 | 5454 | 10.1 | 84.30084307734718 | 7189.6 | 1606.2176165803107 | 350.61761658028354 | 0 |  | 63.125 | 5454 | 2022 | 6 | 2022_06_Asomata_english.xlsx
5 | 330 | 195 | 525 | 0 | 0 | 3 | 525 | 100 | 6.400000000001455 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.8 | 8720 | 41.26 | 2936.7 | -719.9999999999927 | 7322.420634920643 | 5407.5 | 10.3 | 83.24335359767714 | 7360.6 | 2634.9206349206347 | 21.820634920642988 | 60 |  | 62.586805555555564 | 5407.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
6 | 125 | 450 | 575 | 0 | 0 | 3 | 575 | 100 | 2.8000000000029104 | 8.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 85.35 | 10040 | 41.17 | 2831.4 | 1319.9999999999927 | 7127.499999999993 | 5807.5 | 10.1 | 83.81467904575926 | 6705 | 0 | 422.4999999999927 | 0 |  | 67.21643518518519 | 5807.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
7 | 475 | 220 | 695 | 0 | 0 | 3 | 695 | 105 | 9.94999999999709 | 5.0899999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 7 | 84.85 | 8839.999999999993 | 41.94 | 3732.3 | -1200 | 7534.525906735751 | 7019.5 | 10.1 | 84.79267996811352 | 7250.4 | 1715.0259067357513 | 284.1259067357514 | 0 |  | 81.24421296296296 | 7019.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
8 | 70 | 425 | 495 | 0 | 0 | 3 | 495 | 70 | 1.9100000000034925 | 9.160000000003492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.8 | 8720 | 41.53 | 3252.6 | -119.99999999999272 | 4904.250000000007 | 5024.25 | 10.15 | 84.4735509414852 | 4952.8 | 0 | 11.450000000007094 | 60 |  | 58.151041666666664 | 5024.25 | 2022 | 6 | 2022_06_Asomata_english.xlsx
9 | 365 | 210 | 575 | 0 | 0 | 4 | 575 | 108 | 7.25 | 4.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.5 | 8000.000000000007 | 41.86 | 3638.7 | -719.9999999999927 | 6944.4468085106455 | 5957 | 10.36 | 83.34544628662276 | 6997.2 | 1707.4468085106382 | 7.246808510646588 | 60 |  | 68.94675925925925 | 5957 | 2022 | 6 | 2022_06_Asomata_english.xlsx
10 | 135 | 460 | 595 | 0 | 0 | 3 | 595 | 108 | 2.680000000000291 | 8.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.65 | 8360.00000000002 | 42.02 | 3825.9 | 360.00000000001273 | 8642.695876288672 | 6009.5 | 10.1 | 85.19030097617029 | 8205.2 | 2273.1958762886597 | 437.49587628867084 | 0 |  | 69.55439814814815 | 6009.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
11 | 360 | 0 | 360 | 0 | 0 | 3 | 360 | 54 | 7.110000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.9 | 8960.00000000002 | 41.59 | 3322.8 | 600 | 6919.937823834197 | 3636 | 10.1 | 84.6938540007847 | 6891.25 | 2683.937823834197 | 88.68782383419693 | 60 |  | 42.083333333333336 | 3636 | 2022 | 6 | 2022_06_Asomata_english.xlsx
12 | 0 | 365 | 365 | 0 | 0 | 2 | 365 | 54 | 0 | 7.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.75 | 8600.000000000007 | 41.24 | 2913.3 | -360.00000000001273 | 6651.107329842919 | 3686.5 | 10.1 | 84.9910254183313 | 6313.65 | 3324.607329842932 | 337.45732984291953 | 0 |  | 42.667824074074076 | 3686.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
13 | 385 | 50 | 435 | 0 | 0 | 3 | 435 | 100 | 7.599999999998545 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 1 | ΥΨΗΛΗ ΘΕΡΜΟΚΡΑΣΙΑ ΩΣΤΙΚΟΥ - ΟΔΗΓΟΥ ΕΔΡΑΝΟΥ Μον. ΝοΙΙ | 13 | 84.55 | 8120 | 41.9 | 3685.5 | -480.0000000000073 | 6253.925531914887 | 4393.5 | 10.1 | 85.39051319938106 | 6029.8 | 2340.425531914894 | 284.1255319148877 | 60 |  | 50.85069444444444 | 4393.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
14 | 175 | 170 | 345 | 0 | 0 | 3 | 345 | 90 | 3.5 | 3.349999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 18.2 | 0 | 2 | 2 | ΥΨΗΛΗ ΘΕΡΜΟΚΡΑΣΙΑ ΩΣΤΙΚΟΥ - ΟΔΗΓΟΥ ΕΔΡΑΝΟΥ Μον. ΝοΙΙ | 14 | 84.4 | 7760.00000000002 | 41.71 | 3463.2 | -359.99999999998 | 5346.410256410276 | 3450 | 10 | 86.54952830188678 | 5190 | 2256.4102564102564 | 156.4102564102759 | 0 |  | 39.93055555555556 | 3450 | 2022 | 6 | 2022_06_Asomata_english.xlsx
15 | 350 | 0 | 350 | 0 | 0 | 3 | 350 | 54 | 7.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.4 | 7760.00000000002 | 41.64 | 3381.3 | 0 | 7681.973684210527 | 3692.5 | 10.55 | 82.0374675847268 | 7716.1 | 3989.4736842105262 | 25.873684210527244 | 60 |  | 42.737268518518526 | 3692.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
16 | 55 | 325 | 380 | 0 | 0 | 3 | 380 | 90 | 1.4000000000014552 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.7 | 8480.000000000015 | 41.71 | 3463.2 | 719.9999999999945 | 6301.455497382193 | 3838 | 10.1 | 85.09054652537853 | 5956.8 | 1743.455497382199 | 344.65549738219306 | 0 |  | 44.4212962962963 | 3838 | 2022 | 6 | 2022_06_Asomata_english.xlsx
17 | 345 | 35 | 380 | 0 | 0 | 3 | 380 | 70 | 7.25 | 1.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 85.05 | 9320 | 41.62 | 3357.9 | 839.9999999999854 | 7029.063829787219 | 3838 | 10.1 | 84.3987534641966 | 6942.3 | 2351.063829787234 | 146.76382978721904 | 60 |  | 44.4212962962963 | 3838 | 2022 | 6 | 2022_06_Asomata_english.xlsx
18 | 0 | 375 | 375 | 0 | 0 | 3 | 375 | 54 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 85.45 | 10280 | 41.8 | 3568.5 | 960.0000000000146 | 10449.627659574482 | 3787.5 | 10.1 | 83.62177989950894 | 10360.8 | 5702.127659574468 | 148.82765957448282 | 60 |  | 43.83680555555556 | 3787.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
19 | 70 | 305 | 375 | 0 | 0 | 3 | 375 | 110 | 0.9599999999991269 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.6 | 8239.999999999993 | 42 | 3802.5 | -2040.0000000000218 | 9118.467741935463 | 3787.5 | 10.1 | 85.29028959233953 | 9144.8 | 7370.967741935484 | 33.66774193546371 | 60 |  | 43.83680555555556 | 3787.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
20 | 480 | 285 | 765 | 0 | 0 | 3 | 765 | 110 | 9.790000000000873 | 5.489999999997963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 20 | 84.3 | 7520 | 42 | 3802.5 | -719.9999999999927 | 7006.500000000007 | 7726.5 | 10.1 | 85.89518526320718 | 6592.95 | 0 | 413.55000000000746 | 0 |  | 89.42708333333333 | 7726.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
21 | 455 | 135 | 590 | 0 | 0 | 2 | 590 | 80 | 10.55000000000291 | 3.5100000000020373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85.2 | 9680.000000000015 | 41.78 | 3545.1 | 2160.0000000000146 | 8119.000000000015 | 5959 | 10.1 | 84.10570223689035 | 7965.1 | 0 | 213.9000000000142 | 60 |  | 68.9699074074074 | 5959 | 2022 | 6 | 2022_06_Asomata_english.xlsx
22 | 185 | 470 | 655 | 0 | 0 | 3 | 655 | 108 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 85 | 9200.000000000007 | 41.97 | 3767.4 | -480.0000000000073 | 7795.074468085099 | 6615.5 | 10.1 | 84.49689154962007 | 7540.9 | 1659.5744680851064 | 314.17446808509976 | 60 |  | 76.56828703703704 | 6615.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
23 | 305 | 205 | 510 | 0 | 0 | 4 | 510 | 108 | 6.19999999999709 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 23 | 84.9 | 8960.00000000002 | 41.68 | 3428.1 | -239.99999999998727 | 6070.574468085119 | 5151 | 10.1 | 84.6938540007847 | 5878.8 | 1159.5744680851064 | 191.77446808512013 | 0 |  | 59.61805555555556 | 5151 | 2022 | 6 | 2022_06_Asomata_english.xlsx
24 | 0 | 445 | 445 | 0 | 0 | 3 | 445 | 54 | 0 | 8.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.9 | 8960.00000000002 | 41.23 | 2901.6 | 0 | 7978.54255319149 | 4494.5 | 10.1 | 84.6938540007847 | 7740.9 | 3484.0425531914893 | 267.64255319149015 | 30 |  | 52.019675925925924 | 4494.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
25 | 475 | 180 | 655 | 0 | 0 | 3 | 655 | 100 | 10.099999999998545 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.7 | 8480.000000000015 | 42 | 3802.5 | -480.00000000000546 | 6135.4999999999945 | 6615.5 | 10.1 | 85.09054652537853 | 6012 | 0 | 153.49999999999454 | 30 |  | 76.56828703703704 | 6615.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
26 | 0 | 500 | 500 | 0 | 0 | 3 | 500 | 50 | 0 | 10.080000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.75 | 8600.000000000007 | 41.61 | 3346.2 | 119.99999999999272 | 6340.21276595744 | 5050 | 10.1 | 84.9910254183313 | 6132 | 1170.212765957447 | 208.21276595743984 | 0 |  | 58.449074074074076 | 5050 | 2022 | 6 | 2022_06_Asomata_english.xlsx
27 | 530 | 365 | 895 | 0 | 0 | 3 | 895 | 108 | 12.139999999999418 | 8.690000000002328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 27 | 84.25 | 7400.000000000007 | 41.91 | 3697.2 | -1200 | 7839.5 | 9039.5 | 10.1 | 85.99683637002754 | 7797.3 | 0 | 72.20000000000073 | 30 |  | 104.6238425925926 | 9039.5 | 2022 | 6 | 2022_06_Asomata_english.xlsx
28 | 305 | 570 | 875 | 0 | 0 | 3 | 875 | 110 | 6.540000000000873 | 12.259999999994761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 28 | 85 | 9200.000000000007 | 41.8 | 3568.5 | 1800 | 10768.75 | 8968.75 | 10.25 | 83.26035167328418 | 10752.9 | 0 | 75.85000000000036 | 60 |  | 103.80497685185185 | 8968.75 | 2022 | 6 | 2022_06_Asomata_english.xlsx
29 | 565 | 225 | 790 | 0 | 0 | 3 | 790 | 80 | 12.55000000000291 | 5.930000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.9 | 8960.00000000002 | 41.95 | 3744 | -239.99999999998727 | 7660.000000000013 | 7900 | 10 | 85.54079254079252 | 7321.9 | 0 | 338.1000000000131 | 0 |  | 91.43518518518519 | 7900 | 2022 | 6 | 2022_06_Asomata_english.xlsx
30 | 265 | 640 | 905 | 0 | 0 | 3 | 905 | 108 | 6.069999999999709 | 13.190000000002328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.55 | 8120 | 41.98 | 3779.1 | -840.00000000002 | 10173.469148936152 | 9258.15 | 10.23 | 84.30539426331852 | 10168.9 | 1755.3191489361702 | 64.56914893615249 | 60 |  | 107.15451388888891 | 9258.15 | 2022 | 6 | 2022_06_Asomata_english.xlsx
1 | 490 | 580 | 1070 | 0 | 0 | 3 | 1070 | 108 | 11.489999999997963 | 13.470000000001164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 1 | 85.15 | 9560.00000000002 | 41.95 | 3744 | 1440.00000000002 | 12247 | 10807 | 10.1 | 84.20315959753565 | 12130.83 | 0 | 176.17000000001826 | 60 |  | 125.08101851851852 | 10807 | 2022 | 7 | 2022_07_Asomata_english.xlsx
2 | 165 | 620 | 785 | 0 | 0 | 3 | 785 | 108 | 4.209999999999127 | 13.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.95 | 9080.000000000015 | 42 | 3802.5 | -480.00000000000546 | 9186.719895287952 | 7928.5 | 10.1 | 84.59525812883966 | 8932.5 | 1738.219895287958 | 314.21989528795166 | 60 |  | 91.76504629629629 | 7928.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
3 | 365 | 330 | 695 | 0 | 0 | 3 | 695 | 100 | 7.510000000002037 | 6.930000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 83.75 | 6200.000000000007 | 41.98 | 3779.1 | -2880.0000000000073 | 7192.131578947361 | 7019.5 | 10.1 | 87.02673860200392 | 7234.71 | 3052.6315789473683 | 17.421578947361922 | 60 |  | 81.24421296296296 | 7019.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
4 | 325 | 365 | 690 | 0 | 0 | 3 | 690 | 108 | 7.05000000000291 | 7.690000000002328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 83.9 | 6560.00000000002 | 42.08 | 3896.1 | 360.00000000001273 | 7329.000000000013 | 6969 | 10.1 | 86.71518703182966 | 7341.96 | 0 | 47.0400000000127 | 60 |  | 80.65972222222223 | 6969 | 2022 | 7 | 2022_07_Asomata_english.xlsx
5 | 410 | 305 | 715 | 0 | 0 | 3 | 715 | 108 | 8.089999999996508 | 6.0899999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 84.1 | 7039.999999999993 | 41.92 | 3708.9 | 479.9999999999727 | 9426.888601036242 | 7221.5 | 10.1 | 86.3032383998495 | 9435 | 1725.3886010362694 | 51.88860103624211 | 60 |  | 83.58217592592592 | 7221.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
6 | 290 | 400 | 690 | 0 | 0 | 3 | 690 | 100 | 6.150000000001455 | 8.020000000004075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 6 | 84.4 | 7760.00000000002 | 42.02 | 3825.9 | 720.0000000000273 | 7620.000000000027 | 6900 | 10 | 86.54952830188678 | 7394.9 | 0 | 225.10000000002765 | 0 |  | 79.86111111111111 | 6900 | 2022 | 7 | 2022_07_Asomata_english.xlsx
7 | 400 | 290 | 690 | 0 | 0 | 3 | 690 | 100 | 8.19999999999709 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 7 | 84.65 | 8360.00000000002 | 42 | 3802.5 | 600 | 7569 | 6969 | 10.1 | 85.19030097617029 | 7219.7 | 0 | 349.3 | 0 |  | 80.65972222222223 | 6969 | 2022 | 7 | 2022_07_Asomata_english.xlsx
8 | 405 | 400 | 805 | 0 | 0 | 3 | 805 | 100 | 8.200000000004366 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 85.1 | 9439.999999999993 | 41.79 | 3556.8 | 1079.9999999999727 | 9210.499999999973 | 8130.5 | 10.1 | 84.30084307734718 | 8584.8 | 0 | 625.6999999999734 | 0 |  | 94.10300925925925 | 8130.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
9 | 390 | 315 | 705 | 0 | 0 | 3 | 705 | 100 | 8.19999999999709 | 6.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 9 | 85.25 | 9800.000000000007 | 41.89 | 3673.8 | 360.00000000001455 | 7480.500000000015 | 7120.5 | 10.1 | 84.00847021118297 | 7288.4 | 0 | 252.10000000001492 | 60 |  | 82.41319444444444 | 7120.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
10 | 220 | 310 | 530 | 0 | 0 | 3 | 530 | 100 | 4.599999999998545 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.35 | 7639.999999999993 | 41.98 | 3779.1 | -2160.0000000000146 | 10588.833333333318 | 5353 | 10.1 | 85.79377418261309 | 10585 | 7395.833333333333 | 63.83333333331757 | 60 |  | 61.95601851851852 | 5353 | 2022 | 7 | 2022_07_Asomata_english.xlsx
11 | 415 | 420 | 835 | 0 | 0 | 3 | 835 | 108 | 8.200000000004366 | 8.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 84.95 | 9080.000000000015 | 42.08 | 3896.1 | 1440.0000000000218 | 9873.500000000022 | 8433.5 | 10.1 | 84.59525812883966 | 9636.8 | 0 | 236.70000000002256 | 0 |  | 97.60995370370371 | 8433.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
12 | 145 | 360 | 505 | 0 | 0 | 3 | 505 | 100 | 2.7999999999956344 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 85 | 9200.000000000007 | 42.11 | 3931.2 | 119.99999999999272 | 5220.499999999993 | 5100.5 | 10.1 | 84.49689154962007 | 4876.4 | 0 | 344.0999999999931 | 0 |  | 59.03356481481482 | 5100.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
13 | 315 | 105 | 420 | 0 | 0 | 3 | 420 | 110 | 6.5 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.5 | 8000.000000000007 | 41.6 | 3334.5 | -1200 | 5403.702127659575 | 4242 | 10.1 | 85.49097262667443 | 5365.5 | 2361.7021276595747 | 98.20212765957513 | 60 |  | 49.09722222222222 | 4242 | 2022 | 7 | 2022_07_Asomata_english.xlsx
14 | 0 | 445 | 445 | 0 | 0 | 3 | 445 | 54 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.5 | 8000.000000000007 | 41.52 | 3240.9 | 0 | 5029.787234042553 | 4450 | 10 | 86.34588235294117 | 4620 | 579.7872340425532 | 409.7872340425529 | 0 |  | 51.504629629629626 | 4450 | 2022 | 7 | 2022_07_Asomata_english.xlsx
15 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 55 | 8.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.05 | 9320 | 41.31 | 2995.2 | 1319.9999999999927 | 8220.312834224591 | 4595.5 | 10.1 | 84.3987534641966 | 7999.2 | 2304.812834224599 | 281.1128342245902 | 60 |  | 53.188657407407405 | 4595.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
16 | 230 | 390 | 620 | 0 | 0 | 2 | 620 | 110 | 4.80000000000291 | 7.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 16 | 84.4 | 7760.00000000002 | 41.98 | 3779.1 | -1559.99999999998 | 5851.732620320876 | 6262 | 10.1 | 85.69260227909582 | 5738.4 | 1149.7326203208556 | 173.33262032087532 | 60 |  | 72.47685185185185 | 6262 | 2022 | 7 | 2022_07_Asomata_english.xlsx
17 | 345 | 160 | 505 | 0 | 0 | 3 | 505 | 100 | 7.099999999998545 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.1 | 7039.999999999993 | 41.77 | 3533.4 | -720.0000000000273 | 5641.074468085079 | 5201.5 | 10.3 | 84.6274473629592 | 5628.3 | 1159.5744680851064 | 72.77446808508012 | 60 |  | 60.2025462962963 | 5201.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
18 | 395 | 90 | 485 | 0 | 0 | 3 | 485 | 100 | 7.799999999995634 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 1 | ΒΛΑΒΗ Α/Σ Δ/Κ (Ρ25) Μον. ΝοΙΙ | 18 | 85.3 | 9920 | 41.02 | 2655.9 | 2880.0000000000073 | 10730.627659574475 | 4898.5 | 10.1 | 83.91146273980748 | 10752.9 | 2952.1276595744685 | 37.727659574477 | 60 |  | 56.695601851851855 | 4898.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
19 | 690 | 0 | 690 | 0 | 0 | 4 | 690 | 55 | 13.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 2 | 0 | ΒΛΑΒΗ Α/Σ Δ/Κ (Ρ25) Μον. ΝοΙΙ | 19 | 84.5 | 8000.000000000007 | 41.34 | 3030.3 | -1919.9999999999927 | 8000.871657754018 | 6969 | 10.1 | 85.49097262667443 | 7948.8 | 2951.871657754011 | 112.071657754017 | 60 |  | 80.65972222222223 | 6969 | 2022 | 7 | 2022_07_Asomata_english.xlsx
20 | 745 | 0 | 745 | 0 | 0 | 3 | 745 | 54 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 2 | 0 | ΒΛΑΒΗ Α/Σ Δ/Κ (Ρ25) Μον. ΝοΙΙ | 20 | 83.6 | 5839.999999999993 | 42 | 3802.5 | -2160.0000000000146 | 7449.734042553177 | 7822.5 | 10.5 | 84.0132783882784 | 7458.9 | 1787.2340425531916 | 50.834042553176914 | 60 |  | 90.53819444444444 | 7822.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
21 | 565 | 235 | 800 | 0 | 0 | 3 | 800 | 50 | 12.05000000000291 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 84.8 | 8720 | 41.98 | 3779.1 | 2880.0000000000073 | 12814.042553191497 | 8200 | 10.25 | 83.64941873717802 | 12854.25 | 1734.0425531914893 | 19.792553191497063 | 60 |  | 94.9074074074074 | 8200 | 2022 | 7 | 2022_07_Asomata_english.xlsx
22 | 590 | 765 | 1355 | 0 | 0 | 2 | 1355 | 110 | 11.349999999998545 | 15.220000000001164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 22 | 85.25 | 9800.000000000007 | 42 | 3802.5 | 1080.0000000000073 | 14765.5 | 13685.5 | 10.1 | 84.00847021118297 | 14755.6 | 0 | 69.90000000000691 | 60 |  | 158.39699074074073 | 13685.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
23 | 720 | 495 | 1215 | 0 | 0 | 4 | 1215 | 110 | 14.5 | 9.87999999999738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 23 | 83.8 | 6320 | 42 | 3802.5 | -3480.0000000000073 | 9155.999999999993 | 12636 | 10.4 | 84.41525579683476 | 9176.1 | 0 | 39.89999999999418 | 60 |  | 146.25 | 12636 | 2022 | 7 | 2022_07_Asomata_english.xlsx
24 | 240 | 625 | 865 | 0 | 0 | 3 | 865 | 108 | 4.30000000000291 | 12.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84 | 6800.000000000007 | 42 | 3802.5 | 480.0000000000073 | 9216.500000000007 | 8736.5 | 10.1 | 86.50872230080151 | 9117.7 | 0 | 158.80000000000655 | 60 |  | 101.11689814814815 | 8736.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
25 | 820 | 415 | 1235 | 0 | 0 | 3 | 1235 | 108 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 25 | 84.1 | 7039.999999999993 | 41.95 | 3744 | 239.99999999998545 | 12812.3 | 12572.3 | 10.18 | 85.62502041635364 | 12859.2 | 0 | 13.099999999983993 | 60 |  | 145.5127314814815 | 12572.3 | 2022 | 7 | 2022_07_Asomata_english.xlsx
26 | 250 | 710 | 960 | 0 | 0 | 3 | 960 | 108 | 3.75 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 26 | 84.3 | 7520 | 41.95 | 3744 | 480.0000000000073 | 10176 | 9696 | 10.1 | 85.89518526320718 | 10015.6 | 0 | 190.40000000000873 | 30 |  | 112.22222222222223 | 9696 | 2022 | 7 | 2022_07_Asomata_english.xlsx
27 | 575 | 170 | 745 | 0 | 0 | 3 | 745 | 110 | 28.81999999999971 | 2.0199999999967986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.35 | 7639.999999999993 | 41.98 | 3779.1 | 119.99999999999272 | 7644.499999999993 | 7524.5 | 10.1 | 85.79377418261309 | 7509.6 | 0 | 164.89999999999327 | 30 |  | 87.08912037037037 | 7524.5 | 2022 | 7 | 2022_07_Asomata_english.xlsx
28 | 155 | 795 | 950 | 0 | 0 | 4 | 950 | 110 | 3.099999999998545 | 14.980000000003201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 28 | 85.1 | 9439.999999999993 | 42 | 3802.5 | 1800 | 12559.893617021276 | 9595 | 10.1 | 84.30084307734718 | 12488.9 | 1164.8936170212767 | 130.99361702127862 | 60 |  | 111.05324074074075 | 9595 | 2022 | 7 | 2022_07_Asomata_english.xlsx
29 | 750 | 235 | 985 | 0 | 0 | 3 | 985 | 108 | 14.029999999998836 | 4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 85.05 | 9320 | 42 | 3802.5 | -119.99999999999272 | 10859.533678756485 | 9850 | 10 | 85.24274099883856 | 10599.6 | 1129.5336787564765 | 259.9336787564862 | 0 |  | 114.00462962962963 | 9850 | 2022 | 7 | 2022_07_Asomata_english.xlsx
30 | 275 | 690 | 965 | 0 | 0 | 3 | 965 | 110 | 5.220000000001164 | 12.819999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 83.9 | 6560.00000000002 | 41.94 | 3732.3 | -2759.99999999998 | 8260.41935483873 | 9843 | 10.2 | 85.86503813936075 | 8246 | 1177.4193548387098 | 74.41935483873021 | 60 |  | 113.92361111111111 | 9843 | 2022 | 7 | 2022_07_Asomata_english.xlsx
31 | 700 | 0 | 700 | 0 | 0 | 3 | 700 | 55 | 13.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.1 | 7039.999999999993 | 41.93 | 3720.6 | 479.9999999999727 | 9284.042553191463 | 7070 | 10.1 | 86.3032383998495 | 9093 | 1734.0425531914893 | 191.0425531914625 | 0 |  | 81.82870370370371 | 7070 | 2022 | 7 | 2022_07_Asomata_english.xlsx
1 | 660 | 210 | 870 | 0 | 0 | 3 | 870 | 108 | 13.009999999994761 | 4.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 83.95 | 6680.000000000014 | 42 | 3802.5 | -359.9999999999791 | 9616.189189189212 | 8787 | 10.1 | 86.61183162416361 | 9473.7 | 1189.1891891891892 | 202.48918918921117 | 60 |  | 101.70138888888889 | 8787 | 2022 | 8 | 2022_08_Asomata_english.xlsx
2 | 295 | 630 | 925 | 0 | 0 | 3 | 925 | 108 | 7.0200000000040745 | 13.269999999996799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.2 | 7280.000000000014 | 42 | 3802.5 | 600 | 11316.68918918919 | 9527.5 | 10.3 | 84.42690838816544 | 11277 | 1189.1891891891892 | 99.68918918919007 | 60 |  | 110.27199074074075 | 9527.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
3 | 635 | 165 | 800 | 0 | 0 | 3 | 800 | 90 | 12.510000000002037 | 3.709999999999127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.35 | 7639.999999999993 | 42 | 3802.5 | 359.9999999999791 | 8439.999999999978 | 8080 | 10.1 | 85.79377418261309 | 8358.5 | 0 | 141.49999999997817 | 60 |  | 93.51851851851852 | 8080 | 2022 | 8 | 2022_08_Asomata_english.xlsx
4 | 0 | 700 | 700 | 0 | 0 | 3 | 700 | 55 | 0 | 13.069999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85 | 9200.000000000007 | 41.8 | 3568.5 | 1560.0000000000146 | 9821.489361702143 | 7070 | 10.1 | 84.49689154962007 | 9628.7 | 1191.4893617021276 | 252.78936170214365 | 60 |  | 81.82870370370371 | 7070 | 2022 | 8 | 2022_08_Asomata_english.xlsx
5 | 675 | 160 | 835 | 0 | 0 | 3 | 835 | 108 | 13.099999999998545 | 3.4800000000032014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.3 | 7520 | 42 | 3802.5 | -1680.0000000000073 | 7923.71276595744 | 8433.5 | 10.1 | 85.89518526320718 | 7944.9 | 1170.212765957447 | 38.812765957440206 | 60 |  | 97.60995370370371 | 8433.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
6 | 0 | 670 | 670 | 0 | 0 | 3 | 670 | 54 | 0 | 13.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 83.9 | 6560.00000000002 | 41.9 | 3685.5 | -959.99999999998 | 7562.319148936191 | 6767 | 10.1 | 86.71518703182966 | 7447.9 | 1755.3191489361702 | 174.41914893619105 | 60 |  | 78.32175925925925 | 6767 | 2022 | 8 | 2022_08_Asomata_english.xlsx
7 | 635 | 0 | 635 | 0 | 0 | 3 | 635 | 54 | 13.12999999999738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 83.65 | 5960.00000000002 | 41.65 | 3393 | -600 | 8754.989361702128 | 6413.5 | 10.1 | 87.23568635374941 | 8763.15 | 2941.4893617021276 | 51.83936170212837 | 60 |  | 74.23032407407408 | 6413.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
8 | 95 | 630 | 725 | 0 | 0 | 3 | 725 | 75 | 2.650000000001455 | 13.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.5 | 8000.000000000007 | 41.99 | 3790.8 | 2039.9999999999873 | 12421.323529411751 | 7322.5 | 10.1 | 85.49097262667443 | 12398.8 | 3058.823529411765 | 82.52352941175013 | 60 |  | 84.7511574074074 | 7322.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
9 | 325 | 575 | 900 | 0 | 0 | 3 | 900 | 90 | 7.930000000000291 | 12.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 9 | 83.95 | 6680.000000000014 | 42.05 | 3861 | -1319.9999999999936 | 10241.720430107533 | 9180 | 10.2 | 85.76269602000514 | 10290 | 2381.7204301075267 | 11.720430107532593 | 60 |  | 106.25 | 9180 | 2022 | 8 | 2022_08_Asomata_english.xlsx
10 | 65 | 615 | 680 | 0 | 0 | 3 | 680 | 85 | 1.6299999999973807 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 83.8 | 6320 | 41.86 | 3638.7 | -360.00000000001364 | 7799.1891891891755 | 6970 | 10.25 | 85.6506010036177 | 7770 | 1189.1891891891892 | 89.18918918917552 | 60 |  | 80.67129629629629 | 6970 | 2022 | 8 | 2022_08_Asomata_english.xlsx
11 | 645 | 85 | 730 | 0 | 0 | 3 | 730 | 70 | 13.05000000000291 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.8 | 8720 | 41.97 | 3767.4 | 2400 | 12113.425531914894 | 7373 | 10.1 | 84.89173683723513 | 11949.3 | 2340.425531914894 | 164.12553191489496 | 0 |  | 85.33564814814815 | 7373 | 2022 | 8 | 2022_08_Asomata_english.xlsx
12 | 170 | 595 | 765 | 0 | 0 | 3 | 765 | 90 | 4.299999999995634 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 12 | 84.2 | 7280.000000000014 | 41.73 | 3486.6 | -1439.9999999999864 | 8648.202127659588 | 7726.5 | 10.1 | 86.09872835624795 | 8562.6 | 2361.7021276595747 | 145.6021276595875 | 60 |  | 89.42708333333333 | 7726.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
13 | 665 | 30 | 695 | 0 | 0 | 3 | 695 | 104 | 13.10000000000582 | 0.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.1 | 7039.999999999993 | 42.02 | 3825.9 | -240.00000000002092 | 6779.499999999979 | 7019.5 | 10.1 | 86.3032383998495 | 6776 | 0 | 63.49999999997908 | 60 |  | 81.24421296296296 | 7019.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
14 | 0 | 615 | 615 | 0 | 0 | 3 | 615 | 53 | 0 | 12.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.7 | 6080.000000000014 | 42.07 | 3884.4 | -959.9999999999791 | 7001.500000000021 | 6211.5 | 10.1 | 87.13108720944037 | 6901.2 | 1750 | 160.3000000000211 | 60 |  | 71.89236111111111 | 6211.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
15 | 590 | 0 | 590 | 0 | 0 | 3 | 590 | 55 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.15 | 7160.00000000002 | 41.9 | 3685.5 | 1080.0000000000064 | 8853.306451612909 | 6047.5 | 10.25 | 84.93938604866474 | 8827 | 1725.8064516129032 | 86.30645161290886 | 60 |  | 69.99421296296296 | 6047.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
16 | 50 | 665 | 715 | 0 | 0 | 2 | 715 | 80 | 1.0999999999985448 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.65 | 8360.00000000002 | 41.91 | 3697.2 | 1200 | 8421.5 | 7221.5 | 10.1 | 85.19030097617029 | 8088.4 | 0 | 393.1 | 60 |  | 83.58217592592592 | 7221.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
17 | 530 | 110 | 640 | 0 | 0 | 3 | 640 | 80 | 10.5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.1 | 7039.999999999993 | 42 | 3802.5 | -1320.0000000000273 | 8633.361702127633 | 6464 | 10.1 | 86.3032383998495 | 8611.2 | 3489.3617021276596 | 82.16170212763245 | 60 |  | 74.81481481481481 | 6464 | 2022 | 8 | 2022_08_Asomata_english.xlsx
18 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 55 | 0 | 10.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 83.8 | 6320 | 42.05 | 3861 | -719.9999999999927 | 7521.344086021512 | 5865 | 10.2 | 86.07045689089034 | 7521 | 2376.3440860215055 | 60.34408602151234 | 60 |  | 67.88194444444444 | 5865 | 2022 | 8 | 2022_08_Asomata_english.xlsx
19 | 565 | 370 | 935 | 0 | 0 | 3 | 935 | 100 | 11.599999999998545 | 8.39999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 84 | 6800.000000000007 | 42.05 | 3861 | 480.0000000000073 | 9923.500000000007 | 9443.5 | 10.1 | 86.50872230080151 | 9968.4 | 0 | 15.10000000000764 | 60 |  | 109.29976851851852 | 9443.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
20 | 85 | 555 | 640 | 0 | 0 | 3 | 640 | 84 | 1.75 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 83.6 | 5839.999999999993 | 42 | 3802.5 | -960.0000000000146 | 7264.361290322566 | 6579.2 | 10.28 | 85.81122792577075 | 7235.2 | 1645.1612903225807 | 89.16129032256595 | 60 |  | 76.14814814814815 | 6579.2 | 2022 | 8 | 2022_08_Asomata_english.xlsx
21 | 495 | 205 | 700 | 0 | 0 | 3 | 700 | 110 | 11.110000000000582 | 4.620000000002619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 83.85 | 6439.999999999993 | 42 | 3802.5 | 600 | 9444.193548387097 | 7070 | 10.1 | 86.81878940582232 | 9345 | 1774.1935483870968 | 159.1935483870966 | 60 |  | 81.82870370370371 | 7070 | 2022 | 8 | 2022_08_Asomata_english.xlsx
22 | 540 | 805 | 1345 | 0 | 0 | 3 | 1345 | 110 | 11.139999999999418 | 15.980000000003201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 22 | 84.6 | 8239.999999999993 | 42 | 3802.5 | 1800 | 15384.5 | 13584.5 | 10.1 | 85.29028959233953 | 15273.6 | 0 | 110.89999999999782 | 0 |  | 157.22800925925927 | 13584.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
23 | 500 | 175 | 675 | 0 | 0 | 3 | 675 | 55 | 10 | 4.180000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.25 | 9800.000000000007 | 42.06 | 3872.7 | 1560.0000000000146 | 8175.000000000015 | 6615 | 9.8 | 86.5801580747906 | 7950 | 0 | 225.00000000001455 | 0 |  | 76.5625 | 6615 | 2022 | 8 | 2022_08_Asomata_english.xlsx
24 | 155 | 505 | 660 | 0 | 0 | 3 | 660 | 108 | 3 | 10.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 84.8 | 8720 | 42.1 | 3919.5 | -1080.0000000000073 | 5519.999999999993 | 6600 | 10 | 85.74065420560747 | 5156.65 | 0 | 363.3499999999931 | 0 |  | 76.38888888888889 | 6600 | 2022 | 8 | 2022_08_Asomata_english.xlsx
25 | 410 | 25 | 435 | 0 | 0 | 3 | 435 | 89 | 8.55000000000291 | 0.47000000000116415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.8 | 8720 | 41.9 | 3685.5 | 0 | 6148.819148936171 | 4393.5 | 10.1 | 84.89173683723513 | 5752.8 | 1755.3191489361702 | 456.0191489361705 | 60 |  | 50.85069444444444 | 4393.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
26 | 210 | 215 | 425 | 0 | 0 | 3 | 425 | 104 | 3.4499999999970896 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 26 | 84.7 | 8480.000000000015 | 42 | 3802.5 | -239.99999999998545 | 5807.819148936185 | 4292.5 | 10.1 | 85.09054652537853 | 5577.2 | 1755.3191489361702 | 290.6191489361854 | 60 |  | 49.68171296296296 | 4292.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
27 | 445 | 170 | 615 | 0 | 0 | 2 | 615 | 108 | 9.5 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 0 | 3 | 2 | ΒΛΑΒΗ ΒΑΘΜΙΔΩΝ ΕΚΚΙΝΗΣΗΣ ΜΟΝΑΔΟΣ | 27 | 84.2 | 7280.000000000014 | 42 | 3802.5 | -1200 | 6181.712765957446 | 6211.5 | 10.1 | 86.09872835624795 | 5964 | 1170.212765957447 | 277.7127659574462 | 60 |  | 71.89236111111111 | 6211.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
28 | 0 | 390 | 390 | 0 | 0 | 3 | 390 | 55 | 0 | 7.299999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.05 | 6920 | 41.65 | 3393 | -360.00000000001364 | 5437.138297872327 | 4036.5 | 10.35 | 84.31876016014982 | 5299.8 | 1760.6382978723404 | 197.33829787232662 | 60 |  | 46.71875 | 4036.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
29 | 615 | 265 | 880 | 0 | 0 | 3 | 880 | 100 | 12 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 83.9 | 6560.00000000002 | 42 | 3802.5 | -359.99999999998 | 8704.00000000002 | 9064 | 10.3 | 85.03139699237666 | 8554 | 0 | 210.00000000002 | 60 |  | 104.9074074074074 | 9064 | 2022 | 8 | 2022_08_Asomata_english.xlsx
30 | 240 | 495 | 735 | 0 | 0 | 3 | 735 | 108 | 5 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 83.95 | 6680.000000000014 | 42 | 3802.5 | 119.99999999999363 | 7543.499999999994 | 7423.5 | 10.1 | 86.61183162416361 | 7497 | 0 | 106.49999999999363 | 60 |  | 85.92013888888889 | 7423.5 | 2022 | 8 | 2022_08_Asomata_english.xlsx
31 | 155 | 215 | 370 | 0 | 0 | 3 | 370 | 55 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 83.95 | 6680.000000000014 | 41.7 | 3451.5 | 0 | 3737 | 3737 | 10.1 | 86.61183162416361 | 3628.1 | 0 | 168.9 | 60 |  | 43.25231481481482 | 3737 | 2022 | 8 | 2022_08_Asomata_english.xlsx
1 | 195 | 145 | 340 | 0 | 0 | 3 | 340 | 51 | 4.19999999999709 | 3.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 83.7 | 6080.000000000014 | 41.66 | 3404.7 | -600 | 3538.1063829787236 | 3553 | 10.45 | 84.21282113065529 | 3516.25 | 585.1063829787234 | 81.85638297872356 | 60 |  | 41.12268518518518 | 3553 | 2022 | 9 | 2022_09_Asomata_english.xlsx
2 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 55 | 0 | 11.569999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.1 | 7039.999999999993 | 42.04 | 3849.3 | 959.9999999999791 | 6767.499999999979 | 5807.5 | 10.1 | 86.3032383998495 | 6734 | 0 | 93.49999999997908 | 60 |  | 67.21643518518519 | 5807.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
3 | 370 | 0 | 370 | 0 | 0 | 3 | 370 | 55 | 7.220000000001164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.95 | 9080.000000000015 | 41.8 | 3568.5 | 2040.0000000000218 | 7095.212765957469 | 3885 | 10.5 | 81.37258162869338 | 6717.6 | 1170.212765957447 | 377.6127659574686 | 0 |  | 44.96527777777778 | 3885 | 2022 | 9 | 2022_09_Asomata_english.xlsx
4 | 150 | 350 | 500 | 0 | 0 | 3 | 500 | 108 | 2.9900000000052387 | 7.180000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 85.1 | 9439.999999999993 | 41.98 | 3779.1 | 359.9999999999782 | 5409.999999999978 | 5050 | 10.1 | 84.30084307734718 | 5128.2 | 0 | 281.79999999997835 | 0 |  | 58.449074074074076 | 5050 | 2022 | 9 | 2022_09_Asomata_english.xlsx
5 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 54 | 8.489999999997963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.6 | 8239.999999999993 | 41.84 | 3615.3 | -1200 | 4911.904255319148 | 3888.5 | 10.1 | 85.29028959233953 | 4686.6 | 2223.404255319149 | 285.30425531914807 | 60 |  | 45.00578703703704 | 3888.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
6 | 0 | 425 | 425 | 0 | 0 | 3 | 425 | 54 | 0 | 8.639999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.35 | 7639.999999999993 | 41.9 | 3685.5 | -600 | 3692.5 | 4292.5 | 10.1 | 85.79377418261309 | 3605 | 0 | 147.5 | 60 |  | 49.68171296296296 | 4292.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
7 | 350 | 150 | 500 | 0 | 0 | 2 | 500 | 100 | 7.19999999999709 | 3.1599999999962165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.25 | 7400.000000000007 | 41.72 | 3474.9 | -239.99999999998545 | 4836.595744680865 | 5050 | 10.1 | 85.99683637002754 | 4593.7 | 26.595744680851062 | 242.8957446808654 | 0 |  | 58.449074074074076 | 5050 | 2022 | 9 | 2022_09_Asomata_english.xlsx
8 | 0 | 340 | 340 | 0 | 0 | 3 | 340 | 55 | 0 | 7.17000000000553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.75 | 8600.000000000007 | 41.2 | 2866.5 | 1200 | 6368.04255319149 | 3434 | 10.1 | 84.9910254183313 | 6322 | 1734.0425531914893 | 106.04255319148979 | 60 |  | 39.745370370370374 | 3434 | 2022 | 9 | 2022_09_Asomata_english.xlsx
9 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 50 | 8.380000000004657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.6 | 8239.999999999993 | 42.05 | 3861 | -360.00000000001455 | 3528.4999999999854 | 3888.5 | 10.1 | 85.29028959233953 | 3372.6 | 0 | 215.89999999998554 | 60 |  | 45.00578703703704 | 3888.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
10 | 105 | 325 | 430 | 0 | 0 | 3 | 430 | 100 | 2.3799999999973807 | 7.489999999997963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 10 | 84.85 | 8839.999999999993 | 41.98 | 3779.1 | 600 | 4900 | 4300 | 10 | 85.64060676779464 | 4664.7 | 0 | 235.3 | 0 |  | 49.76851851851852 | 4300 | 2022 | 9 | 2022_09_Asomata_english.xlsx
11 | 220 | 135 | 355 | 0 | 0 | 3 | 355 | 90 | 5.190000000002328 | 3.040000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.5 | 8000.000000000007 | 41.98 | 3779.1 | -839.9999999999854 | 3341.2446808510786 | 3585.5 | 10.1 | 85.49097262667443 | 3190.1 | 595.7446808510638 | 211.14468085107865 | 60 |  | 41.498842592592595 | 3585.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
12 | 70 | 210 | 280 | 0 | 0 | 3 | 280 | 70 | 1.9899999999979627 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 85.15 | 9560.00000000002 | 41.85 | 3627 | 1560.0000000000127 | 4388.000000000013 | 2828 | 10.1 | 84.20315959753565 | 4292.4 | 0 | 95.6000000000131 | 0 |  | 32.73148148148148 | 2828 | 2022 | 9 | 2022_09_Asomata_english.xlsx
13 | 295 | 90 | 385 | 0 | 0 | 3 | 385 | 80 | 7.049999999995634 | 2.3799999999973807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.95 | 9080.000000000015 | 41.9 | 3685.5 | -480.00000000000546 | 3408.4999999999945 | 3888.5 | 10.1 | 84.59525812883966 | 3385.75 | 0 | 82.74999999999454 | 60 |  | 45.00578703703704 | 3888.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
14 | 210 | 305 | 515 | 0 | 0 | 3 | 515 | 88 | 5.260000000002037 | 7.5200000000040745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 14 | 85.1 | 9439.999999999993 | 41.9 | 3685.5 | 359.9999999999782 | 6141.287234042531 | 5201.5 | 10.1 | 84.30084307734718 | 6134.7 | 579.7872340425532 | 66.58723404253033 | 60 |  | 60.2025462962963 | 5201.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
15 | 385 | 190 | 575 | 0 | 0 | 2 | 575 | 110 | 8.150000000001455 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 84.95 | 9080.000000000015 | 41.78 | 3545.1 | -359.9999999999782 | 5390.000000000022 | 5750 | 10 | 85.44121071012806 | 5277.9 | 0 | 172.1000000000222 | 60 |  | 66.55092592592592 | 5750 | 2022 | 9 | 2022_09_Asomata_english.xlsx
16 | 120 | 395 | 515 | 0 | 0 | 3 | 515 | 90 | 2.8000000000029104 | 8.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.7 | 8480.000000000015 | 41.84 | 3615.3 | -600 | 4601.5 | 5201.5 | 10.1 | 85.09054652537853 | 4590.3 | 0 | 71.19999999999982 | 60 |  | 60.2025462962963 | 5201.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
17 | 415 | 145 | 560 | 0 | 0 | 3 | 560 | 108 | 8.299999999995634 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 84.95 | 9080.000000000015 | 42.06 | 3872.7 | 600 | 7697.489361702128 | 5656 | 10.1 | 84.59525812883966 | 7670.5 | 1441.4893617021276 | 86.98936170212801 | 60 |  | 65.46296296296296 | 5656 | 2022 | 9 | 2022_09_Asomata_english.xlsx
18 | 15 | 255 | 270 | 0 | 0 | 2 | 270 | 100 | 0.4000000000014552 | 5.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.05 | 9320 | 41.85 | 3627 | 239.99999999998545 | 7365.936170212752 | 2727 | 10.1 | 84.3987534641966 | 7307.3 | 4398.936170212766 | 58.636170212752404 | 0 |  | 31.5625 | 2727 | 2022 | 9 | 2022_09_Asomata_english.xlsx
19 | 475 | 50 | 525 | 0 | 0 | 3 | 525 | 90 | 10 | 1.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 85.3 | 9920 | 41.99 | 3790.8 | 600 | 5902.5 | 5302.5 | 10.1 | 83.91146273980748 | 5730.5 | 0 | 232 | 60 |  | 61.37152777777778 | 5302.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
20 | 0 | 415 | 415 | 0 | 0 | 3 | 415 | 55 | 0 | 8.60000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 20 | 84.25 | 7400.000000000007 | 42.06 | 3872.7 | -2519.9999999999927 | 5687.629032258072 | 4191.5 | 10.1 | 85.99683637002754 | 5659.2 | 4016.1290322580644 | 88.42903225807095 | 60 |  | 48.51273148148148 | 4191.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
21 | 275 | 0 | 275 | 0 | 0 | 3 | 275 | 54 | 5.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 83.95 | 6680.000000000014 | 41.19 | 2854.8 | -719.9999999999936 | 4919.202127659581 | 2777.5 | 10.1 | 86.61183162416361 | 4869.1 | 2861.7021276595747 | 110.10212765958022 | 60 |  | 32.14699074074074 | 2777.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
22 | 0 | 245 | 245 | 0 | 0 | 2 | 245 | 54 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.65 | 5960.00000000002 | 41.47 | 3182.4 | -719.9999999999936 | 5461.44251336899 | 2609.25 | 10.65 | 82.730557011537 | 5424.4 | 3572.192513368984 | 97.04251336899051 | 60 |  | 30.19965277777778 | 2609.25 | 2022 | 9 | 2022_09_Asomata_english.xlsx
23 | 280 | 0 | 280 | 0 | 0 | 3 | 280 | 54 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.5 | 8000.000000000007 | 41.46 | 3170.7 | 2039.9999999999873 | 8437.446808510625 | 2940 | 10.5 | 82.2341736694678 | 8312.85 | 3457.446808510638 | 124.59680851062512 | 0 |  | 34.02777777777778 | 2940 | 2022 | 9 | 2022_09_Asomata_english.xlsx
24 | 0 | 235 | 235 | 0 | 0 | 3 | 235 | 50 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.6 | 8239.999999999993 | 41.39 | 3088.8 | 239.99999999998545 | 2675.0699999999856 | 2435.07 | 10.362 | 83.13375071247145 | 2520 | 0 | 215.0699999999856 | 60 |  | 28.183680555555554 | 2435.07 | 2022 | 9 | 2022_09_Asomata_english.xlsx
25 | 245 | 0 | 245 | 0 | 0 | 3 | 245 | 50 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.7 | 8480.000000000015 | 41.46 | 3170.7 | 240.00000000002183 | 4633.8775510204305 | 2450 | 10 | 85.94145199063232 | 4462.55 | 1943.8775510204082 | 171.3275510204303 | 0 |  | 28.35648148148148 | 2450 | 2022 | 9 | 2022_09_Asomata_english.xlsx
26 | 0 | 275 | 275 | 0 | 0 | 3 | 275 | 50 | 0 | 6.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.6 | 8239.999999999993 | 41.56 | 3287.7 | -240.00000000002183 | 2556.749999999978 | 2796.75 | 10.17 | 84.70323745158596 | 2470.2 | 0 | 146.5499999999779 | 60 |  | 32.369791666666664 | 2796.75 | 2022 | 9 | 2022_09_Asomata_english.xlsx
27 | 245 | 0 | 245 | 0 | 0 | 2 | 245 | 40 | 6.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.5 | 8000.000000000007 | 41.9 | 3685.5 | -239.99999999998545 | 2320.2500000000146 | 2560.25 | 10.45 | 82.62763861525472 | 2284.9 | 0 | 95.35000000001446 | 60 |  | 29.63252314814815 | 2560.25 | 2022 | 9 | 2022_09_Asomata_english.xlsx
28 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 40 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.55 | 8120 | 42 | 3802.5 | 119.99999999999272 | 4820.510638297865 | 2392 | 10.4 | 82.92732531862967 | 4763.25 | 2308.5106382978724 | 117.26063829786472 | 60 |  | 27.685185185185187 | 2392 | 2022 | 9 | 2022_09_Asomata_english.xlsx
29 | 300 | 125 | 425 | 0 | 0 | 3 | 425 | 104 | 6.19999999999709 | 2.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.7 | 8480.000000000015 | 41.84 | 3615.3 | 360.00000000001455 | 4652.500000000015 | 4292.5 | 10.1 | 85.09054652537853 | 4674.6 | 0 | 37.90000000001419 | 60 |  | 49.68171296296296 | 4292.5 | 2022 | 9 | 2022_09_Asomata_english.xlsx
30 | 0 | 230 | 230 | 0 | 0 | 2 | 230 | 55 | 0 | 5.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.65 | 8360.00000000002 | 41.61 | 3346.2 | -119.99999999999454 | 2318.0000000000055 | 2438 | 10.6 | 81.17189055276603 | 2173.6 | 0 | 144.40000000000555 | 0 |  | 28.21759259259259 | 2438 | 2022 | 9 | 2022_09_Asomata_english.xlsx
1 | 250 | 0 | 250 | 0 | 0 | 3 | 250 | 54 | 5.460000000006403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.35 | 10040 | 41.6 | 3334.5 | 1679.9999999999727 | 5720.957446808483 | 2525 | 10.1 | 83.81467904575926 | 5445.8 | 1515.9574468085107 | 275.15744680848366 | 0 |  | 29.224537037037038 | 2525 | 2022 | 10 | 2022_10_Asomata_english.xlsx
2 | 0 | 220 | 220 | 0 | 0 | 3 | 220 | 50 | 0 | 4.519999999996799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.35 | 7639.999999999993 | 41.58 | 3311.1 | -2400 | 4322 | 2222 | 10.1 | 85.79377418261309 | 4267.1 | 4500 | 114.90000000000055 | 60 |  | 25.71759259259259 | 2222 | 2022 | 10 | 2022_10_Asomata_english.xlsx
3 | 490 | 0 | 490 | 0 | 0 | 3 | 490 | 54 | 11.039999999993597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.75 | 8600.000000000007 | 41.8 | 3568.5 | 960.0000000000146 | 5909.000000000015 | 4949 | 10.1 | 84.9910254183313 | 5765.2 | 0 | 203.80000000001473 | 60 |  | 57.280092592592595 | 4949 | 2022 | 10 | 2022_10_Asomata_english.xlsx
4 | 0 | 255 | 255 | 0 | 0 | 2 | 255 | 50 | 0 | 5.639999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.65 | 8360.00000000002 | 40.46 | 2000.7 | -239.99999999998727 | 2335.5000000000127 | 2575.5 | 10.1 | 85.19030097617029 | 2095.1 | 0 | 240.40000000001282 | 0 |  | 29.80902777777778 | 2575.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
5 | 265 | 25 | 290 | 0 | 0 | 3 | 290 | 70 | 6.319999999999709 | 0.8499999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 5 | 84.45 | 7880.000000000014 | 40.67 | 2246.4 | -480.00000000000637 | 5566.0212765957385 | 2929 | 10.1 | 85.5916687075068 | 5526.95 | 3117.021276595745 | 99.0712765957378 | 60 |  | 33.90046296296296 | 2929 | 2022 | 10 | 2022_10_Asomata_english.xlsx
6 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 45 | 0 | 5.060000000004948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.15 | 7160.00000000002 | 40.95 | 2574 | -719.9999999999936 | 6722.776595744687 | 2171.5 | 10.1 | 86.20086207909047 | 6599.2 | 5271.276595744681 | 183.57659574468744 | 60 |  | 25.13310185185185 | 2171.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
7 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 50 | 4.980000000003201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.25 | 7400.000000000007 | 41.03 | 2667.6 | 239.99999999998727 | 4151.322580645148 | 2121 | 10.1 | 85.99683637002754 | 4157.22 | 1790.3225806451612 | 54.10258064514892 | 60 |  | 24.54861111111111 | 2121 | 2022 | 10 | 2022_10_Asomata_english.xlsx
8 | 0 | 165 | 165 | 0 | 0 | 2 | 165 | 45 | 0 | 4.129999999997381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.2 | 7280.000000000014 | 40.74 | 2328.3 | -119.99999999999363 | 4850.6965240641775 | 1740.75 | 10.55 | 82.42627074863547 | 4766.4 | 3229.946524064171 | 144.2965240641779 | 60 |  | 20.147569444444446 | 1740.75 | 2022 | 10 | 2022_10_Asomata_english.xlsx
9 | 170 | 0 | 170 | 0 | 0 | 3 | 170 | 50 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 40.5 | 2047.5 | 239.99999999998636 | 5361.255319148922 | 1717 | 10.1 | 85.89518526320718 | 5212.2 | 3404.255319148936 | 209.05531914892254 | 60 |  | 19.872685185185187 | 1717 | 2022 | 10 | 2022_10_Asomata_english.xlsx
10 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 40 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.2 | 7280.000000000014 | 40.08 | 1556.1 | -239.99999999998636 | 3335.946808510652 | 1868.5 | 10.1 | 86.09872835624795 | 3266 | 1707.4468085106382 | 129.94680851065186 | 60 |  | 21.62615740740741 | 1868.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
11 | 260 | 50 | 310 | 0 | 0 | 2 | 310 | 80 | 5.799999999995634 | 1.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 11 | 84.25 | 7400.000000000007 | 40 | 1462.5 | 119.99999999999363 | 4304.763440860209 | 3131 | 10.1 | 85.99683637002754 | 4222.8 | 1053.763440860215 | 141.96344086020872 | 60 |  | 36.238425925925924 | 3131 | 2022 | 10 | 2022_10_Asomata_english.xlsx
12 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 45 | 0 | 4.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.55 | 8120 | 40.5 | 2047.5 | 719.9999999999927 | 2588.4999999999927 | 1868.5 | 10.1 | 85.39051319938106 | 2453.75 | 0 | 134.74999999999272 | 0 |  | 21.62615740740741 | 1868.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
13 | 285 | 0 | 285 | 0 | 0 | 3 | 285 | 40 | 6.880000000004657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.9 | 8960.00000000002 | 41.46 | 3170.7 | 840.00000000002 | 3718.50000000002 | 2878.5 | 10.1 | 84.6938540007847 | 3562.4 | 0 | 156.10000000001992 | 0 |  | 33.31597222222222 | 2878.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
14 | 130 | 220 | 350 | 0 | 0 | 2 | 350 | 108 | 2.6199999999953434 | 4.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 14 | 85.1 | 9439.999999999993 | 41.81 | 3580.2 | 479.9999999999727 | 4014.9999999999727 | 3535 | 10.1 | 84.30084307734718 | 3859.1 | 0 | 215.89999999997235 | 60 |  | 40.914351851851855 | 3535 | 2022 | 10 | 2022_10_Asomata_english.xlsx
15 | 90 | 70 | 160 | 0 | 0 | 3 | 160 | 80 | 2.599999999998545 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 85.15 | 9560.00000000002 | 41.77 | 3533.4 | 120.00000000002728 | 6520.638297872368 | 1640 | 10.25 | 82.9709182375717 | 6452.5 | 4760.63829787234 | 128.13829787236773 | 60 |  | 18.98148148148148 | 1640 | 2022 | 10 | 2022_10_Asomata_english.xlsx
16 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.8 | 8720 | 41.39 | 3088.8 | -840.00000000002 | 6574.319148936151 | 909 | 10.1 | 84.89173683723513 | 6424 | 6505.319148936171 | 150.31914893615158 | 0 |  | 10.520833333333334 | 909 | 2022 | 10 | 2022_10_Asomata_english.xlsx
17 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 40 | 3.139999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.25 | 9800.000000000007 | 41.27 | 2948.4 | 1080.0000000000073 | 10302.638297872349 | 1212 | 10.1 | 84.00847021118297 | 10166.71 | 8010.638297872341 | 135.9282978723495 | 0 |  | 14.027777777777779 | 1212 | 2022 | 10 | 2022_10_Asomata_english.xlsx
18 | 0 | 125 | 125 | 0 | 0 | 2 | 125 | 40 | 0 | 3.040000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85.35 | 10040 | 41.23 | 2901.6 | 239.99999999998545 | 5635.478723404241 | 1262.5 | 10.1 | 83.81467904575926 | 5652.15 | 4132.978723404255 | 43.32872340424092 | 60 |  | 14.612268518518519 | 1262.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
19 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 45 | 3.110000000000582 | 0 | 0 | 5.83 | 0 | 0 | 0 | 5.83 | 0 | 0 | 1 | 0 | ΣΥΝΤΗΡΗΣΗ Κ.Γ. ΜΕΤΑΦΟΡΑΣ 150KV (ΑΣΩΜΑΤΩΝ - Υ/Σ ΡΑΧΙΑΣ) | 19 | 85.2 | 9680.000000000015 | 41.24 | 2913.3 | -359.9999999999782 | 6761.510638297894 | 1313 | 10.1 | 84.10570223689035 | 6578.25 | 5808.510638297872 | 183.26063829789382 | 0 |  | 15.19675925925926 | 1313 | 2022 | 10 | 2022_10_Asomata_english.xlsx
20 | 0 | 130 | 130 | 0 | 0 | 3 | 130 | 50 | 0 | 3.110000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84 | 6800.000000000007 | 41.41 | 3112.2 | -2880.0000000000073 | 5379.797872340418 | 1371.5 | 10.55 | 82.81877679981945 | 5314.25 | 6888.297872340425 | 125.5478723404176 | 60 |  | 15.873842592592593 | 1371.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
21 | 145 | 0 | 145 | 0 | 0 | 2 | 145 | 54 | 3.5500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.25 | 7400.000000000007 | 41.64 | 3381.3 | 600 | 2086.25 | 1486.25 | 10.25 | 84.73834608168566 | 1912.6 | 0 | 173.65 | 0 |  | 17.20196759259259 | 1486.25 | 2022 | 10 | 2022_10_Asomata_english.xlsx
22 | 0 | 115 | 115 | 0 | 0 | 3 | 115 | 40 | 0 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.2 | 7280.000000000014 | 41.62 | 3357.9 | -119.99999999999363 | 1955.8521505376407 | 1167.25 | 10.15 | 85.67459668946839 | 1830.4 | 908.6021505376344 | 125.45215053764059 | 0 |  | 13.509837962962964 | 1167.25 | 2022 | 10 | 2022_10_Asomata_english.xlsx
23 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 40 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.3 | 7520 | 41.86 | 3638.7 | 239.99999999998636 | 4807.9787234042415 | 1435 | 10.25 | 84.63818255203829 | 4785 | 3132.978723404255 | 82.97872340424146 | 60 |  | 16.608796296296298 | 1435 | 2022 | 10 | 2022_10_Asomata_english.xlsx
24 | 0 | 215 | 215 | 0 | 0 | 2 | 215 | 55 | 0 | 4.330000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.9 | 6560.00000000002 | 41.97 | 3767.4 | -959.99999999998 | 3355.8031088083103 | 2150 | 10 | 87.58233890214795 | 3175.5 | 2165.8031088082903 | 240.3031088083103 | 60 |  | 24.88425925925926 | 2150 | 2022 | 10 | 2022_10_Asomata_english.xlsx
25 | 200 | 100 | 300 | 0 | 0 | 3 | 300 | 108 | 4.44999999999709 | 2.4199999999982538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.75 | 8600.000000000007 | 42.05 | 3861 | 2039.9999999999873 | 5069.999999999987 | 3030 | 10.1 | 84.9910254183313 | 4972.8 | 0 | 97.19999999998709 | 0 |  | 35.06944444444444 | 3030 | 2022 | 10 | 2022_10_Asomata_english.xlsx
26 | 0 | 260 | 260 | 0 | 0 | 3 | 260 | 54 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85 | 9200.000000000007 | 41.62 | 3357.9 | 600 | 5464.248704663212 | 2600 | 10 | 85.34186046511628 | 5146.5 | 2264.2487046632123 | 317.74870466321227 | 0 |  | 30.09259259259259 | 2600 | 2022 | 10 | 2022_10_Asomata_english.xlsx
27 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 45 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.9 | 8960.00000000002 | 41.45 | 3159 | -239.99999999998727 | 2182.0744680851194 | 1262.5 | 10.1 | 84.6938540007847 | 2051.3 | 1159.5744680851064 | 130.77446808511922 | 0 |  | 14.612268518518519 | 1262.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
28 | 90 | 200 | 290 | 0 | 0 | 2 | 290 | 90 | 2.25 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 85.25 | 9800.000000000007 | 41.83 | 3603.6 | 839.9999999999873 | 3739.9999999999873 | 2900 | 10 | 84.84855491329479 | 3586.8 | 0 | 153.19999999998754 | 0 |  | 33.56481481481482 | 2900 | 2022 | 10 | 2022_10_Asomata_english.xlsx
29 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.35 | 10040 | 41.48 | 3194.1 | 239.99999999998545 | 5196.999999999985 | 707 | 10.1 | 83.81467904575926 | 5146.5 | 4250 | 110.49999999998545 | 60 |  | 8.18287037037037 | 707 | 2022 | 10 | 2022_10_Asomata_english.xlsx
30 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.25 | 7400.000000000007 | 41.41 | 3112.2 | -2639.9999999999854 | 2191.9680851063977 | 757.5 | 10.1 | 85.99683637002754 | 2073.2 | 4074.468085106383 | 178.76808510639785 | 60 |  | 8.76736111111111 | 757.5 | 2022 | 10 | 2022_10_Asomata_english.xlsx
31 | 160 | 0 | 160 | 0 | 0 | 2 | 160 | 50 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.65 | 8360.00000000002 | 42.05 | 3861 | 960.0000000000127 | 4404.125000000013 | 1616 | 10.1 | 85.19030097617029 | 4419.22 | 1828.125 | 44.90500000001339 | 60 |  | 18.703703703703702 | 1616 | 2022 | 10 | 2022_10_Asomata_english.xlsx
1 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 84.5 | 8000.000000000007 | 41.82 | 3591.9 | -360.00000000001273 | 2144.8723404255193 | 707 | 10.1 | 85.49097262667443 | 2109.7 | 1797.872340425532 | 95.17234042551945 | 60 |  | 8.18287037037037 | 707 | 2022 | 11 | 2022_11_Asomata_english.xlsx
2 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.6 | 8239.999999999993 | 41.6 | 3334.5 | 239.99999999998545 | 932.9999999999854 | 693 | 9.9 | 87.01332574572012 | 667.5 | 0 | 265.49999999998545 | 0 |  | 8.020833333333334 | 693 | 2022 | 11 | 2022_11_Asomata_english.xlsx
3 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 55 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.65 | 8360.00000000002 | 41.85 | 3627 | 120.00000000002728 | 4485.897959183701 | 2121 | 10.1 | 85.19030097617029 | 4506.6 | 2244.8979591836733 | 9.297959183700186 | 30 |  | 24.54861111111111 | 2121 | 2022 | 11 | 2022_11_Asomata_english.xlsx
4 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.65 | 8360.00000000002 | 41.32 | 3006.9 | 0 | 791.25 | 791.25 | 10.55 | 81.5565914558597 | 686 | 0 | 165.25 | 60 |  | 9.15798611111111 | 791.25 | 2022 | 11 | 2022_11_Asomata_english.xlsx
5 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.2 | 9680.000000000015 | 40.85 | 2457 | 1319.9999999999945 | 3969.494949494944 | 700 | 10 | 84.94675925925925 | 3820.3 | 1949.4949494949494 | 149.194949494944 | 0 |  | 8.101851851851851 | 700 | 2022 | 11 | 2022_11_Asomata_english.xlsx
6 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 35 | 0 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 85.1 | 9439.999999999993 | 40.92 | 2538.9 | -240.00000000002183 | 4851.842105263137 | 1155 | 10.5 | 81.08938238868635 | 4737.7 | 3936.842105263158 | 114.14210526313673 | 0 |  | 13.368055555555555 | 1155 | 2022 | 11 | 2022_11_Asomata_english.xlsx
7 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 40 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.2 | 7280.000000000014 | 40.92 | 2538.9 | -2159.999999999979 | 1037.0416666666874 | 858.5 | 10.1 | 86.09872835624795 | 678.9 | 2338.5416666666665 | 358.14166666668746 | 0 |  | 9.936342592592593 | 858.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
8 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 55 | 0 | 3.7699999999967986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 83.95 | 6680.000000000014 | 41.53 | 3252.6 | -600 | 1997.351063829787 | 1666.5 | 10.1 | 86.61183162416361 | 1966.25 | 930.8510638297872 | 91.10106382978711 | 60 |  | 19.288194444444443 | 1666.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
9 | 265 | 0 | 265 | 0 | 0 | 2 | 265 | 45 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 84.1 | 7039.999999999993 | 41.94 | 3732.3 | 359.9999999999791 | 3036.499999999979 | 2676.5 | 10.1 | 86.3032383998495 | 2940 | 0 | 156.49999999997908 | 60 |  | 30.97800925925926 | 2676.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
10 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 54 | 0 | 3.639999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.95 | 6680.000000000014 | 41.6 | 3334.5 | -359.9999999999791 | 1315.5750000000207 | 1675.575 | 10.155 | 86.1427375090155 | 1057.9 | 0 | 257.6750000000209 | 0 |  | 19.393229166666664 | 1675.575 | 2022 | 11 | 2022_11_Asomata_english.xlsx
11 | 220 | 0 | 220 | 0 | 0 | 3 | 220 | 45 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85.1 | 9439.999999999993 | 41.84 | 3615.3 | 2759.999999999979 | 4981.999999999979 | 2222 | 10.1 | 84.30084307734718 | 4847 | 0 | 134.99999999997908 | 0 |  | 25.71759259259259 | 2222 | 2022 | 11 | 2022_11_Asomata_english.xlsx
12 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 40 | 1.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 85.25 | 9800.000000000007 | 41.64 | 3381.3 | 360.00000000001455 | 2793.0319148936314 | 757.5 | 10.1 | 84.00847021118297 | 2764.8 | 1675.531914893617 | 88.23191489363126 | 60 |  | 8.76736111111111 | 757.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
13 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 55 | 4.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.5 | 8000.000000000007 | 41.75 | 3510 | -1800 | 3126.946808510638 | 1969.5 | 10.1 | 85.49097262667443 | 3080.6 | 2957.446808510638 | 106.34680851063831 | 60 |  | 22.79513888888889 | 1969.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
14 | 0 | 155 | 155 | 0 | 0 | 3 | 155 | 50 | 0 | 3.4899999999979627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.2 | 7280.000000000014 | 41.79 | 3556.8 | -719.9999999999936 | 845.5000000000064 | 1565.5 | 10.1 | 86.09872835624795 | 700.8 | 0 | 204.7000000000064 | 60 |  | 18.119212962962962 | 1565.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
15 | 330 | 0 | 330 | 0 | 0 | 3 | 330 | 54 | 7.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.05 | 6920 | 41.84 | 3615.3 | -360.00000000001364 | 2972.9999999999864 | 3333 | 10.1 | 86.4058581839159 | 2869 | 0 | 103.99999999998636 | 0 |  | 38.576388888888886 | 3333 | 2022 | 11 | 2022_11_Asomata_english.xlsx
16 | 0 | 200 | 200 | 0 | 0 | 2 | 200 | 40 | 0 | 5.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 16 | 84.5 | 8000.000000000007 | 41.56 | 3287.7 | 1080.0000000000073 | 3080.0000000000073 | 2000 | 10 | 86.34588235294117 | 2890.8 | 0 | 189.2000000000071 | 0 |  | 23.14814814814815 | 2000 | 2022 | 11 | 2022_11_Asomata_english.xlsx
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 1.9100000000034925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.7 | 6080.000000000014 | 41.29 | 2971.8 | -1919.9999999999936 | 922.8723404255384 | 795 | 10.6 | 83.02113026559883 | 751.9 | 2047.872340425532 | 170.9723404255384 | 0 |  | 9.20138888888889 | 795 | 2022 | 11 | 2022_11_Asomata_english.xlsx
18 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.0899999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.3 | 7520 | 41.28 | 2960.1 | 1439.9999999999864 | 2139.9999999999864 | 700 | 10 | 86.75413711583924 | 2048.75 | 0 | 91.24999999998636 | 0 |  | 8.101851851851851 | 700 | 2022 | 11 | 2022_11_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 40 | 1.9899999999979627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.5 | 8000.000000000007 | 41.25 | 2925 | 480.0000000000073 | 3782.32978723405 | 738.5 | 10.55 | 81.84443824923333 | 3686.5 | 2563.8297872340427 | 95.82978723404995 | 0 |  | 8.547453703703704 | 738.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
20 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 54 | 0 | 4.510000000002037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.15 | 9560.00000000002 | 39.78 | 1205.1 | 1560.0000000000127 | 7604.593264248717 | 2070.5 | 10.1 | 84.20315959753565 | 7482.5 | 3974.0932642487046 | 122.09326424871688 | 0 |  | 23.96412037037037 | 2070.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
21 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 40 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.8 | 8720 | 39.61 | 1006.2 | -840.00000000002 | 2335.75641025639 | 1565.5 | 10.1 | 84.89173683723513 | 2264.8 | 1610.2564102564102 | 130.95641025638997 | 60 |  | 18.119212962962962 | 1565.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
22 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 50 | 0 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85.05 | 9320 | 40.96 | 2585.7 | 600 | 3449.595744680851 | 2323 | 10.1 | 84.3987534641966 | 3181.15 | 526.5957446808511 | 268.445744680851 | 0 |  | 26.886574074074073 | 2323 | 2022 | 11 | 2022_11_Asomata_english.xlsx
23 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 50 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.55 | 8120 | 42.03 | 3837.6 | -1200 | 4660.619170984455 | 2171.5 | 10.1 | 85.39051319938106 | 4547.9 | 3689.1191709844556 | 112.71917098445556 | 0 |  | 25.13310185185185 | 2171.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
24 | 45 | 95 | 140 | 0 | 0 | 2 | 140 | 95 | 0.8499999999985448 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.3 | 7520 | 41.88 | 3662.1 | -600 | 814 | 1414 | 10.1 | 85.89518526320718 | 729.6 | 0 | 84.40000000000009 | 0 |  | 16.36574074074074 | 1414 | 2022 | 11 | 2022_11_Asomata_english.xlsx
25 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.9 | 6560.00000000002 | 41.48 | 3194.1 | -959.99999999998 | 2988.958333333353 | 787.5 | 10.5 | 83.41175133537901 | 2759.4 | 3161.458333333333 | 229.5583333333534 | 0 |  | 9.114583333333334 | 787.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
26 | 170 | 135 | 305 | 0 | 0 | 3 | 305 | 80 | 4.549999999995634 | 3.3000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.65 | 8360.00000000002 | 41.87 | 3650.4 | 1800 | 5486.842105263158 | 3050 | 10 | 86.04220398593199 | 5431.2 | 636.8421052631579 | 55.642105263158555 | 0 |  | 35.300925925925924 | 3050 | 2022 | 11 | 2022_11_Asomata_english.xlsx
27 | 80 | 55 | 135 | 0 | 0 | 3 | 135 | 80 | 2.0500000000029104 | 1.3799999999973807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.8 | 8720 | 41.79 | 3556.8 | 359.99999999998 | 7670.308510638279 | 1363.5 | 10.1 | 84.89173683723513 | 7519 | 5946.808510638299 | 211.30851063827959 | 60 |  | 15.78125 | 1363.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
28 | 0 | 280 | 280 | 0 | 0 | 3 | 280 | 54 | 0 | 5.819999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.15 | 9560.00000000002 | 41.91 | 3697.2 | 840.00000000002 | 6008.425531914914 | 2828 | 10.1 | 84.20315959753565 | 5767 | 2340.425531914894 | 241.42553191491425 | 0 |  | 32.73148148148148 | 2828 | 2022 | 11 | 2022_11_Asomata_english.xlsx
29 | 465 | 550 | 1015 | 0 | 0 | 3 | 1015 | 108 | 9.299999999995634 | 11.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 83.9 | 6560.00000000002 | 41.77 | 3533.4 | -3000 | 10198.308510638297 | 10251.5 | 10.1 | 86.71518703182966 | 10074 | 2946.808510638298 | 184.30851063829687 | 60 |  | 118.65162037037037 | 10251.5 | 2022 | 11 | 2022_11_Asomata_english.xlsx
30 | 145 | 715 | 860 | 0 | 0 | 3 | 860 | 110 | 3 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.8 | 8720 | 41.65 | 3393 | 2159.99999999998 | 13122.041666666646 | 8686 | 10.1 | 84.89173683723513 | 13005 | 2276.0416666666665 | 177.04166666664605 | 60 |  | 100.5324074074074 | 8686 | 2022 | 11 | 2022_11_Asomata_english.xlsx
1 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 45 | 4.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.35 | 7639.999999999993 | 41.63 | 3369.6 | -1080.0000000000073 | 4351.861702127652 | 1942.5 | 10.5 | 82.52543992803734 | 3606.2 | 3489.3617021276596 | 745.6617021276525 | 0 |  | 22.48263888888889 | 1942.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
2 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.75 | 8600.000000000007 | 41.34 | 3030.3 | 960.0000000000146 | 2360.900537634423 | 798.75 | 10.65 | 80.60181753287758 | 2156 | 602.1505376344086 | 264.900537634423 | 60 |  | 9.244791666666666 | 798.75 | 2022 | 12 | 2022_12_Asomata_english.xlsx
3 | 205 | 0 | 205 | 0 | 0 | 2 | 205 | 55 | 4.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.45 | 7880.000000000014 | 42.03 | 3837.6 | -719.9999999999936 | 4176.141025641032 | 2070.5 | 10.1 | 85.5916687075068 | 4164.55 | 2825.6410256410254 | 71.59102564103159 | 60 |  | 23.96412037037037 | 2070.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
4 | 0 | 105 | 105 | 0 | 0 | 3 | 105 | 40 | 0 | 2.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85 | 9200.000000000007 | 42.08 | 3896.1 | 1319.9999999999936 | 4151.7765957446745 | 1060.5 | 10.1 | 84.49689154962007 | 4095.3 | 1771.276595744681 | 116.47659574467434 | 60 |  | 12.274305555555555 | 1060.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
5 | 290 | 210 | 500 | 0 | 0 | 3 | 500 | 100 | 5.900000000001455 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.45 | 7880.000000000014 | 41.77 | 3533.4 | -1319.9999999999936 | 5926.808510638304 | 5050 | 10.1 | 85.5916687075068 | 5613.7 | 2196.808510638298 | 313.1085106383043 | 0 |  | 58.449074074074076 | 5050 | 2022 | 12 | 2022_12_Asomata_english.xlsx
6 | 0 | 315 | 315 | 0 | 0 | 3 | 315 | 40 | 0 | 8.05000000000291 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ Μον. ΝοΙ | 6 | 85.3 | 9920 | 41.51 | 3229.2 | 2039.9999999999864 | 6998.510638297859 | 3150 | 10 | 84.75057736720554 | 6694.1 | 1808.5106382978724 | 304.4106382978598 | 0 |  | 36.458333333333336 | 3150 | 2022 | 12 | 2022_12_Asomata_english.xlsx
7 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 50 | 3.5500000000029104 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ Μον. ΝοΙ | 7 | 85.3 | 9920 | 41.83 | 3603.6 | 0 | 5278.13829787234 | 1767.5 | 10.1 | 83.91146273980748 | 5204.3 | 3510.6382978723404 | 133.83829787234117 | 60 |  | 20.457175925925927 | 1767.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
8 | 155 | 700 | 855 | 0 | 0 | 3 | 855 | 80 | 4.150000000001455 | 15.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.8 | 8720 | 41.71 | 3463.2 | -1200 | 9662.5 | 8550 | 10 | 85.74065420560747 | 9555.7 | 2312.5 | 106.79999999999927 | 0 |  | 98.95833333333333 | 8550 | 2022 | 12 | 2022_12_Asomata_english.xlsx
9 | 0 | 115 | 115 | 0 | 0 | 3 | 115 | 40 | 0 | 3.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.5 | 8000.000000000007 | 41.79 | 3556.8 | -719.9999999999927 | 1042.5638297872413 | 1161.5 | 10.1 | 85.49097262667443 | 686.2 | 601.063829787234 | 416.36382978724134 | 60 |  | 13.443287037037036 | 1161.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
10 | 0 | 80 | 80 | 0 | 0 | 2 | 80 | 40 | 0 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84 | 6800.000000000007 | 41.95 | 3744 | -1200 | 1668.6486486486488 | 820 | 10.25 | 85.24274099883856 | 1638 | 2048.6486486486488 | 90.64864864864876 | 60 |  | 9.49074074074074 | 820 | 2022 | 12 | 2022_12_Asomata_english.xlsx
11 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 40 | 0 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 11 | 84.15 | 7160.00000000002 | 41.55 | 3276 | 360.00000000001273 | 4254.397435897448 | 858.5 | 10.1 | 86.20086207909047 | 3988.6 | 3035.8974358974356 | 265.79743589744794 | 0 |  | 9.936342592592593 | 858.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
12 | 90 | 525 | 615 | 0 | 0 | 3 | 615 | 108 | 1.75 | 9.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 84.55 | 8120 | 41.9 | 3685.5 | 959.99999999998 | 10543.840425531895 | 6211.5 | 10.1 | 85.39051319938106 | 10300.05 | 3372.3404255319147 | 303.7904255318954 | 60 |  | 71.89236111111111 | 6211.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
13 | 150 | 420 | 570 | 0 | 0 | 3 | 570 | 110 | 2.75 | 7.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 13 | 84.6 | 8239.999999999993 | 41.62 | 3357.9 | 119.99999999999272 | 12116.27419354838 | 5899.5 | 10.35 | 83.23013766981926 | 12147.85 | 6096.774193548387 | 28.424193548378753 | 60 |  | 68.28125 | 5899.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
14 | 0 | 160 | 160 | 0 | 0 | 2 | 160 | 40 | 0 | 4.540000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 85 | 9200.000000000007 | 41.5 | 3217.5 | 960.0000000000146 | 2560.0000000000146 | 1600 | 10 | 85.34186046511628 | 2138.85 | 0 | 421.15000000001464 | 0 |  | 18.51851851851852 | 1600 | 2022 | 12 | 2022_12_Asomata_english.xlsx
15 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 1.9599999999991269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 83.7 | 6080.000000000014 | 41.33 | 3018.6 | -3119.9999999999936 | 2632.0945945946014 | 757.5 | 10.1 | 87.13108720944037 | 2591.5 | 4994.594594594595 | 100.5945945946014 | 60 |  | 8.76736111111111 | 757.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
16 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 45 | 0 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.4 | 7760.00000000002 | 41.33 | 3018.6 | 1680.0000000000064 | 4049.138297872347 | 858.5 | 10.1 | 85.69260227909582 | 3892 | 1510.6382978723404 | 217.1382978723468 | 60 |  | 9.936342592592593 | 858.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
17 | 0 | 100 | 100 | 0 | 0 | 3 | 100 | 50 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 17 | 84.8 | 8720 | 41.6 | 3334.5 | 959.99999999998 | 3853.9361702127458 | 995 | 9.95 | 86.17151176442964 | 3723 | 1898.9361702127658 | 160.93617021274576 | 30 |  | 11.516203703703702 | 995 | 2022 | 12 | 2022_12_Asomata_english.xlsx
18 | 0 | 295 | 295 | 0 | 0 | 2 | 295 | 55 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.15 | 7160.00000000002 | 41.8 | 3568.5 | -1559.99999999998 | 2749.287234042573 | 2979.5 | 10.1 | 86.20086207909047 | 2540.4 | 1329.787234042553 | 208.8872340425728 | 0 |  | 34.4849537037037 | 2979.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
19 | 0 | 195 | 195 | 0 | 0 | 3 | 195 | 40 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 85 | 9200.000000000007 | 41.8 | 3568.5 | 2039.9999999999873 | 8479.164507772008 | 1998.75 | 10.25 | 83.26035167328418 | 8227.1 | 4440.41450777202 | 252.06450777200735 | 0 |  | 23.133680555555557 | 1998.75 | 2022 | 12 | 2022_12_Asomata_english.xlsx
20 | 40 | 225 | 265 | 0 | 0 | 3 | 265 | 80 | 0.8999999999941792 | 4.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.85 | 8839.999999999993 | 41.82 | 3591.9 | -360.00000000001455 | 5186.2916666666515 | 2676.5 | 10.1 | 84.79267996811352 | 4978.6 | 2869.7916666666665 | 207.69166666665205 | 0 |  | 30.97800925925926 | 2676.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
21 | 170 | 0 | 170 | 0 | 0 | 3 | 170 | 54 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.8 | 8720 | 41.72 | 3474.9 | -119.99999999999272 | 4762.803108808297 | 1717 | 10.1 | 84.89173683723513 | 4652.55 | 3165.8031088082903 | 170.25310880829784 | 60 |  | 19.872685185185187 | 1717 | 2022 | 12 | 2022_12_Asomata_english.xlsx
22 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.85 | 8839.999999999993 | 41.43 | 3135.6 | 119.99999999999272 | 1412.1063829787163 | 707 | 10.1 | 84.79267996811352 | 1270.2 | 585.1063829787234 | 201.90638297871624 | 60 |  | 8.18287037037037 | 707 | 2022 | 12 | 2022_12_Asomata_english.xlsx
23 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.1 | 9439.999999999993 | 41.47 | 3182.4 | 600 | 4410.6276595744675 | 858.5 | 10.1 | 84.30084307734718 | 4248.6 | 2952.127659574468 | 162.02765957446718 | 0 |  | 9.936342592592593 | 858.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
24 | 0 | 150 | 150 | 0 | 0 | 3 | 150 | 45 | 0 | 3.969999999993888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.7 | 8480.000000000015 | 42.08 | 3896.1 | -959.9999999999782 | 3528.118279569914 | 1515 | 10.1 | 85.09054652537853 | 3457.7 | 2973.1182795698924 | 130.41827956991438 | 60 |  | 17.53472222222222 | 1515 | 2022 | 12 | 2022_12_Asomata_english.xlsx
25 | 165 | 0 | 165 | 0 | 0 | 2 | 165 | 55 | 4.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.2 | 9680.000000000015 | 41.88 | 3662.1 | 1200 | 6329.265957446809 | 1666.5 | 10.1 | 84.10570223689035 | 6175.8 | 3462.7659574468084 | 153.46595744680963 | 0 |  | 19.288194444444443 | 1666.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
26 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 40 | 0 | 2.0900000000037835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.5 | 8000.000000000007 | 41.63 | 3369.6 | -1680.0000000000073 | 3713.1063829787163 | 808 | 10.1 | 85.49097262667443 | 3699.1 | 4585.106382978724 | 74.00638297871683 | 60 |  | 9.351851851851851 | 808 | 2022 | 12 | 2022_12_Asomata_english.xlsx
27 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.75 | 6200.000000000007 | 41.62 | 3357.9 | -1800 | 4891.063829787234 | 840 | 10.5 | 83.71143427430853 | 4822.2 | 5851.063829787234 | 128.86382978723395 | 60 |  | 9.722222222222221 | 840 | 2022 | 12 | 2022_12_Asomata_english.xlsx
28 | 100 | 190 | 290 | 0 | 0 | 3 | 290 | 110 | 2.0500000000029104 | 4.0899999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 85.05 | 9320 | 41.78 | 3545.1 | 3119.9999999999927 | 6019.999999999993 | 2900 | 10 | 85.24274099883856 | 5811 | 0 | 208.99999999999272 | 0 |  | 33.56481481481482 | 2900 | 2022 | 12 | 2022_12_Asomata_english.xlsx
29 | 75 | 195 | 270 | 0 | 0 | 3 | 270 | 55 | 2 | 3.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.25 | 7400.000000000007 | 41.63 | 3369.6 | -1919.9999999999927 | 807.0000000000073 | 2727 | 10.1 | 85.99683637002754 | 675 | 0 | 132.00000000000728 | 0 |  | 31.5625 | 2727 | 2022 | 12 | 2022_12_Asomata_english.xlsx
30 | 0 | 135 | 135 | 0 | 0 | 3 | 135 | 50 | 0 | 3.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.65 | 8360.00000000002 | 41.61 | 3346.2 | 960.0000000000127 | 2323.5000000000127 | 1363.5 | 10.1 | 85.19030097617029 | 2197.3 | 0 | 126.200000000013 | 0 |  | 15.78125 | 1363.5 | 2022 | 12 | 2022_12_Asomata_english.xlsx
31 | 260 | 340 | 600 | 0 | 0 | 2 | 600 | 110 | 5.209999999999127 | 6.970000000001164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 31 | 85 | 9200.000000000007 | 41.71 | 3463.2 | 839.9999999999873 | 6899.999999999987 | 6060 | 10.1 | 84.49689154962007 | 6667.75 | 0 | 232.24999999998727 | 0 |  | 70.13888888888889 | 6060 | 2022 | 12 | 2022_12_Asomata_english.xlsx
1 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.0899999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.7 | 8480.000000000015 | 41.57 | 3299.4 | -719.9999999999854 | 5673.106382978737 | 808 | 10.1 | 85.09054652537853 | 5533.4 | 5585.106382978723 | 199.70638297873757 | 60 |  | 9.351851851851851 | 808 | 2023 | 1 | 2023_01_Asomata_english.xlsx
2 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 50 | 0 | 2.1299999999973807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.65 | 5960.00000000002 | 41.64 | 3381.3 | -2519.9999999999945 | 3725.842105263164 | 909 | 10.1 | 87.23568635374941 | 3569.7 | 5336.842105263158 | 216.142105263164 | 60 |  | 10.520833333333334 | 909.0000000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
3 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 50 | 4.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83.55 | 5720 | 41.74 | 3498.3 | -240.00000000002 | 1628.49999999998 | 1868.5 | 10.1 | 87.44563987084629 | 1620.6 | 0 | 67.89999999998008 | 60 |  | 21.62615740740741 | 1868.5000000000002 | 2023 | 1 | 2023_01_Asomata_english.xlsx
4 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 40 | 0 | 5.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 83.95 | 6680.000000000014 | 41.75 | 3510 | 960.0000000000136 | 3030.5000000000136 | 2070.5 | 10.1 | 86.61183162416361 | 2905.4 | 0 | 185.10000000001355 | 60 |  | 23.96412037037037 | 2070.5 | 2023 | 1 | 2023_01_Asomata_english.xlsx
5 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 55 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.2 | 9680.000000000015 | 42.01 | 3814.2 | 3000.000000000001 | 8296.531914893618 | 2121 | 10.1 | 84.10570223689035 | 8139.5 | 3175.531914893617 | 217.0319148936178 | 60 |  | 24.54861111111111 | 2121 | 2023 | 1 | 2023_01_Asomata_english.xlsx
6 | 0 | 100 | 100 | 0 | 0 | 2 | 100 | 35 | 0 | 2.8000000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 83.6 | 5839.999999999993 | 41.52 | 3240.9 | -3840.000000000022 | 3435.9574468084884 | 1010 | 10.1 | 87.34053693830923 | 3412.8 | 6265.95744680851 | 83.1574468084882 | 60 |  | 11.689814814814815 | 1010.0000000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
7 | 145 | 60 | 205 | 0 | 0 | 3 | 205 | 80 | 3.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 85.25 | 9800.000000000007 | 41.91 | 3697.2 | 3960.0000000000146 | 6010.000000000015 | 2050 | 10 | 84.84855491329479 | 5868.2 | 0 | 141.80000000001473 | 0 |  | 23.72685185185185 | 2050 | 2023 | 1 | 2023_01_Asomata_english.xlsx
8 | 85 | 95 | 180 | 0 | 0 | 3 | 180 | 55 | 1.7000000000043656 | 2.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 85.1 | 9439.999999999993 | 41.91 | 3697.2 | -360.00000000001455 | 4426.421052631564 | 1818 | 10.1 | 84.30084307734718 | 4212.1 | 2968.4210526315787 | 214.32105263156336 | 0 |  | 21.041666666666668 | 1818.0000000000002 | 2023 | 1 | 2023_01_Asomata_english.xlsx
9 | 340 | 255 | 595 | 0 | 0 | 3 | 595 | 110 | 7.099999999998545 | 4.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.65 | 8360.00000000002 | 41.73 | 3486.6 | -1079.9999999999727 | 5995.826530612272 | 6009.5 | 10.1 | 85.19030097617029 | 5989.8 | 1066.3265306122448 | 66.02653061227193 | 60 |  | 69.55439814814815 | 6009.500000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
10 | 0 | 260 | 260 | 0 | 0 | 3 | 260 | 54 | 0 | 6.239999999997963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 |  | 10 | 84.92 | 9008.000000000011 | 41.73 | 3486.6 | 647.9999999999909 | 3221.999999999991 | 2574 | 9.9 | 86.36457774388809 | 3022.5 | 0 | 199.4999999999909 | 0 |  | 29.791666666666668 | 2574.0000000000005 | 2023 | 1 | 2023_01_Asomata_english.xlsx
11 | 95 | 0 | 95 | 0 | 0 | 3 | 95 | 40 | 2.139999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.35 | 7639.999999999993 | 41.48 | 3194.1 | -1368.0000000000182 | 2139.372340425514 | 959.5 | 10.1 | 85.79377418261309 | 1978.3 | 2547.872340425532 | 221.07234042551386 | 60 |  | 11.105324074074074 | 959.5000000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
12 | 105 | 235 | 340 | 0 | 0 | 3 | 340 | 100 | 1.9599999999991269 | 4.459999999999127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.7 | 8480.000000000015 | 41.92 | 3708.9 | 840.0000000000218 | 4274.000000000022 | 3434 | 10.1 | 85.09054652537853 | 4321 | 0 | 3.000000000021828 | 50 |  | 39.745370370370374 | 3434.0000000000005 | 2023 | 1 | 2023_01_Asomata_english.xlsx
13 | 185 | 0 | 185 | 0 | 0 | 2 | 185 | 54 | 4.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.9 | 8960.00000000002 | 41.65 | 3393 | 480.00000000000546 | 2293.0000000000055 | 1813 | 9.8 | 87.2865230008087 | 2197.05 | 0 | 95.95000000000528 | 0 |  | 20.983796296296298 | 1813.0000000000002 | 2023 | 1 | 2023_01_Asomata_english.xlsx
14 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 55 | 0 | 9.400000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.6 | 8239.999999999993 | 41.83 | 3603.6 | -720.0000000000273 | 4127.999999999973 | 4848 | 10.1 | 85.29028959233953 | 3737.25 | 0 | 390.7499999999727 | 0 |  | 56.111111111111114 | 4848.000000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
15 | 75 | 0 | 75 | 0 | 0 | 2 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.35 | 7639.999999999993 | 41.58 | 3311.1 | -600 | 5822.393617021276 | 757.5 | 10.1 | 85.79377418261309 | 5785.5 | 5664.893617021276 | 96.89361702127644 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 1 | 2023_01_Asomata_english.xlsx
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.3 | 7520 | 41.07 | 2714.4 | -119.99999999999272 | 2316.0000000000073 | 686 | 9.8 | 88.52462971004005 | 2052 | 1750 | 264.0000000000073 | 0 |  | 7.939814814814815 | 686 | 2023 | 1 | 2023_01_Asomata_english.xlsx
17 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480.000000000015 | 40.74 | 2328.3 | 960.0000000000146 | 8464.808510638313 | 808 | 10.1 | 85.09054652537853 | 8358.5 | 6696.808510638299 | 106.30851063831324 | 0 |  | 9.351851851851851 | 808 | 2023 | 1 | 2023_01_Asomata_english.xlsx
18 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.9 | 8960.00000000002 | 40.72 | 2304.9 | 480.00000000000546 | 8134.089947089952 | 707 | 10.1 | 84.6938540007847 | 8169.12 | 6947.089947089947 | 24.969947089952257 | 60 |  | 8.18287037037037 | 707 | 2023 | 1 | 2023_01_Asomata_english.xlsx
19 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2.180000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85 | 9200.000000000007 | 40.78 | 2375.1 | 239.99999999998727 | 9092.738095238083 | 757.5 | 10.1 | 84.49689154962007 | 9103.1 | 8095.238095238095 | 49.638095238082315 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 1 | 2023_01_Asomata_english.xlsx
20 | 0 | 235 | 235 | 0 | 0 | 3 | 235 | 55 | 0 | 5.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.3 | 9920 | 41.89 | 3673.8 | 719.9999999999927 | 8270.583333333325 | 2373.5 | 10.1 | 83.91146273980748 | 8015.4 | 5177.083333333333 | 255.1833333333252 | 0 |  | 27.471064814814813 | 2373.5 | 2023 | 1 | 2023_01_Asomata_english.xlsx
21 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 1.9700000000011642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.5 | 8000.000000000007 | 41.79 | 3556.8 | -1919.9999999999927 | 3914.6595744680926 | 707 | 10.1 | 85.49097262667443 | 3859.2 | 5127.659574468085 | 115.4595744680928 | 60 |  | 8.18287037037037 | 707 | 2023 | 1 | 2023_01_Asomata_english.xlsx
22 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 1.9700000000011642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.8 | 6320 | 41.72 | 3474.9 | -1680.0000000000073 | 795.5851063829714 | 757.5 | 10.1 | 86.9226396323843 | 671.6 | 1718.0851063829787 | 123.98510638297137 | 0 |  | 8.76736111111111 | 757.5 | 2023 | 1 | 2023_01_Asomata_english.xlsx
23 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.6 | 5839.999999999993 | 41.75 | 3510 | -480.0000000000073 | 2878.563829787227 | 757.5 | 10.1 | 87.34053693830923 | 2730.2 | 2601.063829787234 | 148.36382978722713 | 0 |  | 8.76736111111111 | 757.5 | 2023 | 1 | 2023_01_Asomata_english.xlsx
24 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.95 | 6680.000000000014 | 41.37 | 3065.4 | 840.0000000000209 | 1578.750000000021 | 738.75 | 9.85 | 88.81010146234034 | 1337.6 | 0 | 241.150000000021 | 0 |  | 8.550347222222221 | 738.75 | 2023 | 1 | 2023_01_Asomata_english.xlsx
25 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.85 | 6439.999999999993 | 40.93 | 2550.6 | -240.00000000002092 | 2219.6858638743247 | 800 | 10 | 87.68697729988054 | 1992.9 | 1659.6858638743456 | 226.7858638743246 | 0 |  | 9.25925925925926 | 800.0000000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
26 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600.000000000007 | 40.94 | 2562.3 | 2160.0000000000146 | 2917.5000000000146 | 757.5 | 10.1 | 84.9910254183313 | 2513.7 | 0 | 463.80000000001473 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 1 | 2023_01_Asomata_english.xlsx
27 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.95 | 9080.000000000015 | 40.88 | 2492.1 | 480.0000000000073 | 2291.712041884824 | 707 | 10.1 | 84.59525812883966 | 2087.8 | 1104.7120418848167 | 203.9120418848238 | 0 |  | 8.18287037037037 | 707 | 2023 | 1 | 2023_01_Asomata_english.xlsx
28 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.8 | 8720 | 40.12 | 1602.8999999999946 | -360.00000000001455 | 2521.892473118265 | 812 | 10.15 | 84.4735509414852 | 2550.65 | 2069.8924731182797 | 31.242473118265025 | 60 |  | 9.398148148148149 | 812.0000000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
29 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.069999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.8 | 8720 | 39.28 | 620.1 | 0 | 2797.425531914894 | 707 | 10.1 | 84.89173683723513 | 2645.92 | 2090.425531914894 | 211.5055319148937 | 60 |  | 8.18287037037037 | 707 | 2023 | 1 | 2023_01_Asomata_english.xlsx
30 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 40 | 0 | 2.0800000000017462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.5 | 8000.000000000007 | 39.67 | 1076.4 | -719.9999999999927 | 2693.263157894744 | 808 | 10.1 | 85.49097262667443 | 2462.4 | 2605.2631578947367 | 230.86315789474384 | 0 |  | 9.351851851851851 | 808 | 2023 | 1 | 2023_01_Asomata_english.xlsx
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.030000000006112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.9 | 8960.00000000002 | 40.04 | 1509.3 | 960.0000000000127 | 3525.595744680864 | 789 | 10.52 | 81.31254043801572 | 3372.6 | 1776.595744680851 | 212.99574468086394 | 60 |  | 9.131944444444445 | 789.0000000000001 | 2023 | 1 | 2023_01_Asomata_english.xlsx
1 | 245 | 0 | 245 | 0 | 0 | 3 | 245 | 55 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85 | 9200.000000000007 | 40.58 | 2141.1 | 239.99999999998727 | 6560.244680851051 | 2474.5 | 10.1 | 84.49689154962007 | 6526.2 | 3845.744680851064 | 34.04468085105145 | 0 |  | 28.640046296296298 | 2474.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
2 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 54 | 0 | 4.419999999998254 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 2 |  | 2 | 84.45 | 7880.000000000014 | 40.49 | 2035.8 | -1319.9999999999936 | 700.0000000000064 | 2020 | 10.1 | 85.5916687075068 | 657 | 0 | 103.00000000000637 | 60 |  | 23.37962962962963 | 2020 | 2023 | 2 | 2023_02_Asomata_english.xlsx
3 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 40 | 3.3999999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.75 | 8600.000000000007 | 40.44 | 1977.3 | 719.9999999999936 | 1982.4999999999936 | 1262.5 | 10.1 | 84.9910254183313 | 1824.7 | 0 | 217.79999999999382 | 60 |  | 14.612268518518519 | 1262.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
4 | 0 | 325 | 325 | 0 | 0 | 2 | 325 | 55 | 0 | 6.600000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.15 | 9560.00000000002 | 40.5 | 2047.5 | 960.0000000000127 | 4242.500000000013 | 3282.5 | 10.1 | 84.20315959753565 | 4175.6 | 0 | 66.90000000001328 | 0 |  | 37.991898148148145 | 3282.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
5 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 50 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.35 | 10040 | 40.48 | 2024.0999999999947 | 479.9999999999727 | 6867.659574468058 | 1010 | 10.1 | 83.81467904575926 | 6730.6 | 5377.659574468085 | 197.0595744680577 | 60 |  | 11.689814814814815 | 1010 | 2023 | 2 | 2023_02_Asomata_english.xlsx
6 | 0 | 185 | 185 | 0 | 0 | 3 | 185 | 55 | 0 | 4.149999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85 | 9200.000000000007 | 40.45 | 1989.0000000000055 | -839.9999999999854 | 1028.5000000000146 | 1868.5 | 10.1 | 84.49689154962007 | 685.4 | 0 | 343.1000000000146 | 0 |  | 21.62615740740741 | 1868.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
7 | 250 | 265 | 515 | 0 | 0 | 3 | 515 | 110 | 4.650000000001455 | 4.850000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.5 | 8000.000000000007 | 40.5 | 2047.5 | -1200 | 7214.265957446809 | 5201.5 | 10.1 | 85.49097262667443 | 7092 | 3212.7659574468084 | 182.2659574468089 | 60 |  | 60.2025462962963 | 5201.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
8 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.75 | 8600.000000000007 | 40.5 | 2047.5 | 600 | 1862.5 | 1262.5 | 10.1 | 84.9910254183313 | 1883.4 | 0 | 39.100000000000136 | 60 |  | 14.612268518518519 | 1262.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
9 | 240 | 160 | 400 | 0 | 0 | 3 | 400 | 110 | 5.399999999994179 | 3.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.8 | 8720 | 40.68 | 2258.1 | 119.99999999999272 | 5605.595854922272 | 4040 | 10.1 | 84.89173683723513 | 5439 | 1445.5958549222798 | 166.59585492227234 | 0 |  | 46.75925925925926 | 4040 | 2023 | 2 | 2023_02_Asomata_english.xlsx
10 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 55 | 0 | 4.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.6 | 8239.999999999993 | 40.43 | 1965.6 | -480.0000000000073 | 3803.5212765957376 | 1666.5 | 10.1 | 85.29028959233953 | 3730.3 | 2617.021276595745 | 133.22127659573744 | 60 |  | 19.288194444444443 | 1666.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
11 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.25 | 7400.000000000007 | 40.38 | 1907.1000000000054 | -839.9999999999854 | 3691.1842105263304 | 757.5 | 10.1 | 85.99683637002754 | 3715.7 | 3773.684210526316 | 35.48421052633057 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
12 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.15 | 7160.00000000002 | 40.48 | 2024.0999999999947 | -239.99999999998727 | 5342.579787234055 | 768.75 | 10.25 | 84.93938604866474 | 5343.25 | 4813.829787234043 | 59.3297872340554 | 60 |  | 8.897569444444445 | 768.75 | 2023 | 2 | 2023_02_Asomata_english.xlsx
13 | 130 | 75 | 205 | 0 | 0 | 3 | 205 | 80 | 3.1999999999970896 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85 | 9200.000000000007 | 40.48 | 2024.0999999999947 | 2039.9999999999873 | 6179.648936170201 | 2070.5 | 10.1 | 84.49689154962007 | 6082.75 | 2069.148936170213 | 96.89893617020061 | 0 |  | 23.96412037037037 | 2070.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
14 | 44 | 179 | 223 | 0 | 0 | 3 | 223 | 85 | 1.069999999999709 | 4.0899999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.3 | 9920 | 40.5 | 2047.5 | 719.9999999999927 | 2949.9999999999927 | 2230 | 10 | 84.75057736720554 | 2708.4 | 0 | 241.59999999999218 | 0 |  | 25.810185185185187 | 2230 | 2023 | 2 | 2023_02_Asomata_english.xlsx
15 | 110 | 0 | 110 | 0 | 0 | 3 | 110 | 55 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 85.1 | 9439.999999999993 | 40.5 | 2047.5 | -480.0000000000073 | 5109.723404255312 | 1111 | 10.1 | 84.30084307734718 | 4964 | 4478.723404255319 | 205.72340425531183 | 60 |  | 12.858796296296296 | 1111 | 2023 | 2 | 2023_02_Asomata_english.xlsx
16 | 206 | 266 | 472 | 0 | 0 | 3 | 472 | 110 | 4.480000000003201 | 5.610000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 85 | 9200.000000000007 | 40.52 | 2070.9000000000055 | -239.99999999998545 | 6316.085106382993 | 4838 | 10.25 | 83.26035167328418 | 6358.25 | 1718.0851063829787 | 17.835106382993217 | 60 |  | 55.995370370370374 | 4838 | 2023 | 2 | 2023_02_Asomata_english.xlsx
17 | 135 | 125 | 260 | 0 | 0 | 3 | 260 | 110 | 3.2999999999956344 | 2.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.3 | 7520 | 40.52 | 2070.9000000000055 | -1680.0000000000073 | 3249.6649214659615 | 2626 | 10.1 | 85.89518526320718 | 3139 | 2303.6649214659687 | 170.66492146596147 | 60 |  | 30.39351851851852 | 2626 | 2023 | 2 | 2023_02_Asomata_english.xlsx
18 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.9 | 6560.00000000002 | 40.54 | 2094.3 | -959.99999999998 | 2192.0945945946146 | 757.5 | 10.1 | 86.71518703182966 | 2219 | 2394.5945945945946 | 33.09459459461459 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
19 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.8 | 8720 | 40.49 | 2035.8 | 2159.99999999998 | 5749.914893617001 | 808 | 10.1 | 84.89173683723513 | 5416.6 | 2781.9148936170213 | 333.31489361700096 | 0 |  | 9.351851851851851 | 808 | 2023 | 2 | 2023_02_Asomata_english.xlsx
20 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 55 | 0 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.1 | 9439.999999999993 | 40.76 | 2351.7 | 719.9999999999927 | 7517.749999999993 | 954 | 10.6 | 80.32438821520817 | 7307.3 | 5843.75 | 210.44999999999345 | 0 |  | 11.041666666666666 | 954 | 2023 | 2 | 2023_02_Asomata_english.xlsx
21 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 54 | 4.370000000002619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.15 | 9560.00000000002 | 40.48 | 2024.0999999999947 | 120.00000000002728 | 2089.5000000000273 | 1969.5 | 10.1 | 84.20315959753565 | 1927.2 | 0 | 162.30000000002724 | 0 |  | 22.79513888888889 | 1969.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
22 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 55 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.6 | 8239.999999999993 | 40.64 | 2211.3 | -1320.0000000000273 | 750.4999999999727 | 2070.5 | 10.1 | 85.29028959233953 | 707 | 0 | 103.49999999997272 | 60 |  | 23.96412037037037 | 2070.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
23 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 55 | 2.0500000000029104 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | ΣΥΝΤΗΡΗΣΗ Υ/Σ 150KV | 23 | 84.9 | 8960.00000000002 | 40.5 | 2047.5 | 720.0000000000273 | 2130.0463917526044 | 858.5 | 10.1 | 84.6938540007847 | 1969.8 | 551.5463917525773 | 160.2463917526045 | 0 |  | 9.936342592592593 | 858.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
24 | 0 | 205 | 205 | 0 | 0 | 2 | 205 | 55 | 0 | 4.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.19 | 9656 | 40.5 | 2047.5 | 695.9999999999818 | 3312.3265306122266 | 2050 | 10 | 84.9664274137532 | 3135 | 566.3265306122448 | 177.32653061222663 | 0 |  | 23.72685185185185 | 2050 | 2023 | 2 | 2023_02_Asomata_english.xlsx
25 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 55 | 2.8799999999973807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.2 | 9680.000000000015 | 40.47 | 2012.4 | 24.000000000012733 | 3291.819148936183 | 1262.5 | 10.1 | 84.10570223689035 | 3131.7 | 2005.3191489361702 | 160.11914893618314 | 0 |  | 14.612268518518519 | 1262.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
26 | 20 | 40 | 60 | 0 | 0 | 3 | 60 | 80 | 0.4000000000014552 | 0.8000000000029104 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 1 | ΑΠΟΚΑΤΑΣΤΑΣΗ ΒΛΑΒΗΣ Η/Κ Απ/Ζ 16 | 26 | 84.3 | 7520 | 40.5 | 2047.5 | -2160.0000000000146 | 5083.526315789459 | 633 | 10.55 | 82.23140958847321 | 4869.1 | 6610.526315789473 | 214.42631578945839 | 0 |  | 7.326388888888889 | 633 | 2023 | 2 | 2023_02_Asomata_english.xlsx
27 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 85.1 | 9439.999999999993 | 40.17 | 1661.4 | 1919.9999999999927 | 4368.989361702121 | 757.5 | 10.1 | 84.30084307734718 | 4234 | 1691.4893617021276 | 194.98936170212073 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 2 | 2023_02_Asomata_english.xlsx
28 | 110 | 380 | 490 | 0 | 0 | 3 | 490 | 55 | 2 | 7.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.7 | 8480.000000000015 | 40.36 | 1883.7 | -959.9999999999782 | 3891.000000000022 | 4851 | 9.9 | 86.80954746528516 | 3809.7 | 0 | 141.30000000002156 | 60 |  | 56.145833333333336 | 4851 | 2023 | 2 | 2023_02_Asomata_english.xlsx
1 | 120 | 50 | 170 | 0 | 0 | 3 | 170 | 80 | 2.900000000001455 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.55 | 8120 | 40.49 | 2035.8 | -360.00000000001455 | 1356.9999999999854 | 1717 | 10.1 | 85.39051319938106 | 1238.2 | 0 | 118.79999999998563 | 0 |  | 19.872685185185187 | 1717 | 2023 | 3 | 2023_03_Asomata_english.xlsx
2 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 55 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.9 | 8960.00000000002 | 40.47 | 2012.4 | 840.00000000002 | 1648.00000000002 | 808 | 10.1 | 84.6938540007847 | 1387 | 0 | 321.00000000002 | 60 |  | 9.351851851851851 | 808 | 2023 | 3 | 2023_03_Asomata_english.xlsx
3 | 220 | 140 | 360 | 0 | 0 | 3 | 360 | 100 | 4.549999999995634 | 2.6000000000058208 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 3 | 84.85 | 8839.999999999993 | 40.5 | 2047.5 | -120.00000000002728 | 3515.9999999999727 | 3636 | 10.1 | 84.79267996811352 | 3337.1 | 0 | 238.8999999999728 | 60 |  | 42.083333333333336 | 3636 | 2023 | 3 | 2023_03_Asomata_english.xlsx
4 | 0 | 95 | 95 | 0 | 0 | 2 | 95 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85.2 | 9680.000000000015 | 39.6 | 994.5 | 840.0000000000218 | 5027.013227513249 | 959.5 | 10.1 | 84.10570223689035 | 4942.1 | 3227.5132275132273 | 144.9132275132497 | 60 |  | 11.105324074074074 | 959.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
5 | 85 | 0 | 85 | 0 | 0 | 3 | 85 | 55 | 1.9100000000034925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85.2 | 9680.000000000015 | 39.88 | 1322.1000000000054 | 0 | 4721.657894736842 | 858.5 | 10.1 | 84.10570223689035 | 4591.7 | 3863.157894736842 | 129.9578947368418 | 0 |  | 9.936342592592593 | 858.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
6 | 35 | 70 | 105 | 0 | 0 | 3 | 105 | 35 | 0.930000000000291 | 2.1299999999973807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84.1 | 7039.999999999993 | 40.48 | 2024.0999999999947 | -2640.000000000022 | 1904.5425531914675 | 1060.5 | 10.1 | 86.3032383998495 | 1843.2 | 3484.0425531914893 | 121.34255319146746 | 60 |  | 12.274305555555555 | 1060.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
7 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.0099999999947613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 83.3 | 5120 | 40.51 | 2059.2 | -1919.9999999999927 | 2142.3128342246064 | 757.5 | 10.1 | 87.97497183132359 | 2190 | 3304.812834224599 | 12.312834224606377 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
8 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2.0199999999967986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.9 | 8960.00000000002 | 40.48 | 2024.0999999999947 | 3840.00000000002 | 6704.642857142877 | 757.5 | 10.1 | 84.6938540007847 | 6600.8 | 2107.142857142857 | 103.84285714287671 | 0 |  | 8.76736111111111 | 757.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
9 | 240 | 130 | 370 | 0 | 0 | 3 | 370 | 110 | 4.600000000005821 | 2.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.7 | 8480.000000000015 | 40.48 | 2024.0999999999947 | -480.00000000000546 | 4331.468085106378 | 3737 | 10.1 | 85.09054652537853 | 4336.2 | 1074.468085106383 | 55.26808510637784 | 60 |  | 43.25231481481482 | 3737 | 2023 | 3 | 2023_03_Asomata_english.xlsx
10 | 0 | 70 | 70 | 0 | 0 | 2 | 70 | 35 | 0 | 1.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 83.2 | 4880.000000000014 | 40.5 | 2047.5 | -3600 | 4132.773195876288 | 707 | 10.1 | 88.18850331635105 | 4124.5 | 7025.773195876289 | 68.2731958762879 | 60 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
11 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.35 | 7639.999999999993 | 40.5 | 2047.5 | 2759.999999999979 | 6661.089743589722 | 757.5 | 10.1 | 85.79377418261309 | 6635.7 | 3143.5897435897436 | 85.38974358972246 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
12 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.35 | 7639.999999999993 | 40.5 | 2047.5 | 0 | 3921.2857142857147 | 707 | 10.1 | 85.79377418261309 | 3806.95 | 3214.2857142857147 | 114.3357142857144 | 0 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
13 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.95 | 9080.000000000015 | 40.5 | 2047.5 | 1440.0000000000218 | 6732.492227979296 | 707 | 10.1 | 84.59525812883966 | 6657.6 | 4585.4922279792745 | 134.89222797929688 | 60 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
14 | 85 | 180 | 265 | 0 | 0 | 3 | 265 | 55 | 2 | 3.930000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.95 | 9080.000000000015 | 40.45 | 1989.0000000000055 | 0 | 5835.474358974359 | 2676.5 | 10.1 | 84.59525812883966 | 5854.6 | 3158.974358974359 | 20.874358974359893 | 40 |  | 30.97800925925926 | 2676.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
15 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.4500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.4 | 7760.00000000002 | 40.5 | 2047.5 | -1319.9999999999945 | 859.5918367346992 | 700 | 10 | 86.54952830188678 | 652.5 | 1479.5918367346937 | 207.0918367346992 | 0 |  | 8.101851851851851 | 700 | 2023 | 3 | 2023_03_Asomata_english.xlsx
16 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2.069999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85.1 | 9439.999999999993 | 40.47 | 2012.4 | 1679.9999999999727 | 2437.4999999999727 | 757.5 | 10.1 | 84.30084307734718 | 2336 | 0 | 101.49999999997272 | 0 |  | 8.76736111111111 | 757.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
17 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.55 | 8120 | 40.45 | 1989.0000000000055 | -1319.9999999999927 | 4046.574468085114 | 707 | 10.1 | 85.39051319938106 | 3920.1 | 4659.574468085107 | 126.4744680851145 | 0 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
18 | 0 | 80 | 80 | 0 | 0 | 2 | 80 | 40 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.9 | 8960.00000000002 | 40.46 | 2000.7 | 840.00000000002 | 2728.808080808101 | 808 | 10.1 | 84.6938540007847 | 2584 | 1080.8080808080808 | 144.80808080810084 | 0 |  | 9.351851851851851 | 808 | 2023 | 3 | 2023_03_Asomata_english.xlsx
19 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.8 | 6320 | 40.47 | 2012.4 | -2640.00000000002 | 5651.891534391514 | 757.5 | 10.1 | 86.9226396323843 | 5511.5 | 7534.391534391534 | 140.39153439151414 | 0 |  | 8.76736111111111 | 757.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
20 | 0 | 100 | 100 | 0 | 0 | 3 | 100 | 55 | 0 | 2.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.8 | 8720 | 40.46 | 2000.7 | 2400 | 3410 | 1010 | 10.1 | 84.89173683723513 | 3374.4 | 0 | 35.59999999999991 | 0 |  | 11.689814814814815 | 1010 | 2023 | 3 | 2023_03_Asomata_english.xlsx
21 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.4 | 7760.00000000002 | 40.47 | 2012.4 | -959.99999999998 | 1020.7692307692507 | 750 | 10 | 86.54952830188678 | 757.5 | 1230.7692307692307 | 263.2692307692507 | 0 |  | 8.680555555555555 | 750 | 2023 | 3 | 2023_03_Asomata_english.xlsx
22 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.0199999999967986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.55 | 8120 | 40.47 | 2012.4 | 359.99999999998 | 3346.7927461139698 | 707 | 10.1 | 85.39051319938106 | 3263.4 | 2279.79274611399 | 83.39274611396968 | 0 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
23 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.3 | 7520 | 40.46 | 2000.7 | -600 | 5765.031088082901 | 707 | 10.1 | 85.89518526320718 | 5681.55 | 5658.031088082901 | 143.4810880829009 | 60 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
24 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 35 | 0 | 2.0800000000017462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.3 | 9920 | 40.45 | 1989.0000000000055 | 2400 | 6565.378306878307 | 858.5 | 10.1 | 83.91146273980748 | 6489.7 | 3306.878306878307 | 75.67830687830701 | 0 |  | 9.936342592592593 | 858.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.3 | 9920 | 40.46 | 2000.7 | 0 | 5644.5 | 707 | 10.1 | 83.91146273980748 | 5677.5 | 4937.5 | 27 | 60 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
26 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.9 | 8960.00000000002 | 40.48 | 2024.0999999999947 | -959.99999999998 | 7966.627659574488 | 724.5 | 10.35 | 82.64810873506525 | 8030 | 8202.127659574468 | 16.627659574487552 | 80 |  | 8.385416666666666 | 724.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
27 | 0 | 70 | 70 | 0 | 0 | 2 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.2 | 7280.000000000014 | 40.45 | 1989.0000000000055 | -1680.0000000000064 | 5101.468085106377 | 707 | 10.1 | 86.09872835624795 | 4861.8 | 6074.468085106383 | 239.66808510637748 | 0 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
28 | 25 | 155 | 180 | 0 | 0 | 3 | 180 | 108 | 0.4000000000014552 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 85.2 | 9680.000000000015 | 40.42 | 1953.9 | 2400 | 6164.571428571429 | 1836 | 10.2 | 83.28113652868555 | 6204.15 | 1928.5714285714284 | 20.421428571428805 | 60 |  | 21.25 | 1836 | 2023 | 3 | 2023_03_Asomata_english.xlsx
29 | 125 | 50 | 175 | 0 | 0 | 3 | 175 | 109 | 2.400000000001455 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.85 | 8839.999999999993 | 40.46 | 2000.7 | -840.0000000000218 | 2393.468586387413 | 1767.5 | 10.1 | 84.79267996811352 | 2182.95 | 1465.9685863874345 | 210.51858638741305 | 0 |  | 20.457175925925927 | 1767.5 | 2023 | 3 | 2023_03_Asomata_english.xlsx
30 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85 | 9200.000000000007 | 40.42 | 1953.9 | 360.00000000001455 | 5035.9119170984595 | 707 | 10.1 | 84.49689154962007 | 4865.7 | 3968.9119170984454 | 170.2119170984597 | 0 |  | 8.18287037037037 | 707 | 2023 | 3 | 2023_03_Asomata_english.xlsx
31 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 85.45 | 10280 | 40.5 | 2047.5 | 1080.0000000000073 | 4040.416666666674 | 700 | 10 | 84.45799769850403 | 3901.5 | 2260.4166666666665 | 138.9166666666738 | 0 |  | 8.101851851851851 | 700 | 2023 | 3 | 2023_03_Asomata_english.xlsx
1 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85.5 | 10400 | 40.48 | 2024.0999999999947 | 119.99999999999272 | 6875.128342245982 | 707 | 10.1 | 83.5256629111187 | 6818.2 | 6048.128342245989 | 56.928342245982094 | 0 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
2 | 0 | 235 | 235 | 0 | 0 | 3 | 235 | 54 | 0 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.25 | 9800.000000000007 | 40.5 | 2047.5 | -600 | 2308.3756345177662 | 2350 | 10 | 84.84855491329479 | 2256.75 | 558.3756345177665 | 51.62563451776623 | 0 |  | 27.199074074074073 | 2350 | 2023 | 4 | 2023_04_Asomata_english.xlsx
3 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 55 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85.25 | 9800.000000000007 | 40.47 | 2012.4 | 0 | 2721.7171717171714 | 1050 | 10 | 84.84855491329479 | 2379.3 | 1671.7171717171716 | 342.4171717171712 | 0 |  | 12.152777777777779 | 1050 | 2023 | 4 | 2023_04_Asomata_english.xlsx
4 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 45 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84 | 6800.000000000007 | 40.44 | 1977.3 | -3000 | 927.565217391304 | 808 | 10.1 | 86.50872230080151 | 945 | 3119.565217391304 | 42.56521739130403 | 60 |  | 9.351851851851851 | 808 | 2023 | 4 | 2023_04_Asomata_english.xlsx
5 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 45 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.45 | 7880.000000000014 | 40.46 | 2000.7 | 1080.0000000000064 | 2342.5000000000064 | 1262.5 | 10.1 | 85.5916687075068 | 2117 | 0 | 285.50000000000637 | 60 |  | 14.612268518518519 | 1262.5 | 2023 | 4 | 2023_04_Asomata_english.xlsx
6 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.55 | 8120 | 40.28 | 1790.1 | 239.99999999998636 | 946.9999999999864 | 707 | 10.1 | 85.39051319938106 | 693.5 | 0 | 253.49999999998636 | 0 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
7 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.65 | 8360.00000000002 | 40.49 | 2035.8 | 240.00000000002 | 2932.051282051302 | 1010 | 10.1 | 85.19030097617029 | 2713.2 | 1682.051282051282 | 218.8512820513024 | 0 |  | 11.689814814814815 | 1010 | 2023 | 4 | 2023_04_Asomata_english.xlsx
8 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 85.35 | 10040 | 40.38 | 1907.1000000000054 | 1679.9999999999727 | 5378.989361702101 | 757.5 | 10.1 | 83.81467904575926 | 5357.75 | 2941.4893617021276 | 81.23936170210072 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 4 | 2023_04_Asomata_english.xlsx
9 | 15 | 0 | 15 | 0 | 0 | 2 | 15 | 35 | 0.5499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.8 | 8720 | 40.09 | 1567.8000000000054 | -1319.9999999999927 | 890.6060606060678 | 150 | 10 | 85.74065420560747 | 696.15 | 2060.6060606060605 | 194.4560606060678 | 0 |  | 1.7361111111111112 | 150 | 2023 | 4 | 2023_04_Asomata_english.xlsx
10 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.4 | 7760.00000000002 | 40.27 | 1778.4000000000053 | -959.99999999998 | 2948.5744680851262 | 749 | 10.7 | 80.88740962793158 | 3044.1 | 3159.574468085106 | 14.474468085126318 | 110 |  | 8.668981481481481 | 749 | 2023 | 4 | 2023_04_Asomata_english.xlsx
11 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 40 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.3 | 7520 | 40.5 | 2047.5 | -240.00000000002 | 5465.959183673449 | 808 | 10.1 | 85.89518526320718 | 5248.7 | 4897.959183673469 | 217.25918367344912 | 0 |  | 9.351851851851851 | 808 | 2023 | 4 | 2023_04_Asomata_english.xlsx
12 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2.2000000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.7 | 8480.000000000015 | 40.5 | 2047.5 | 960.0000000000146 | 5312.3717948718095 | 757.5 | 10.1 | 85.09054652537853 | 5289.5 | 3594.871794871795 | 82.87179487180947 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 4 | 2023_04_Asomata_english.xlsx
13 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.35 | 7639.999999999993 | 40.47 | 2012.4 | -840.0000000000218 | 6318.612903225785 | 707 | 10.1 | 85.79377418261309 | 6202 | 6451.612903225807 | 176.61290322578498 | 60 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
14 | 65 | 0 | 65 | 0 | 0 | 2 | 65 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 83.3 | 5120 | 40.5 | 2047.5 | -2519.9999999999927 | 4281.461538461545 | 663 | 10.2 | 87.11247210748708 | 4351.2 | 6138.461538461538 | 20.26153846154466 | 90 |  | 7.673611111111111 | 663 | 2023 | 4 | 2023_04_Asomata_english.xlsx
15 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 45 | 0 | 2.1499999999941792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 85.25 | 9800.000000000007 | 40.5 | 2047.5 | 4680.000000000007 | 7584.653846153853 | 858.5 | 10.1 | 84.00847021118297 | 7570.2 | 2046.1538461538462 | 24.453846153852282 | 10 |  | 9.936342592592593 | 858.5 | 2023 | 4 | 2023_04_Asomata_english.xlsx
16 | 90 | 155 | 245 | 0 | 0 | 3 | 245 | 100 | 1.5999999999985448 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 85.15 | 9560.00000000002 | 40.5 | 2047.5 | -239.99999999998727 | 3367.1530612245024 | 2474.5 | 10.1 | 84.20315959753565 | 3261.6 | 1132.6530612244896 | 165.55306122450247 | 60 |  | 28.640046296296298 | 2474.5 | 2023 | 4 | 2023_04_Asomata_english.xlsx
17 | 130 | 0 | 130 | 0 | 0 | 3 | 130 | 55 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.95 | 9080.000000000015 | 40.5 | 2047.5 | -480.00000000000546 | 832.9999999999945 | 1313 | 10.1 | 84.59525812883966 | 676.4 | 0 | 156.59999999999457 | 0 |  | 15.19675925925926 | 1313 | 2023 | 4 | 2023_04_Asomata_english.xlsx
18 | 0 | 100 | 100 | 0 | 0 | 3 | 100 | 35 | 0 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.85 | 8839.999999999993 | 40.5 | 2047.5 | -240.00000000002183 | 769.9999999999782 | 1010 | 10.1 | 84.79267996811352 | 627.3 | 0 | 142.6999999999781 | 0 |  | 11.689814814814815 | 1010 | 2023 | 4 | 2023_04_Asomata_english.xlsx
19 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.9000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85 | 9200.000000000007 | 40.5 | 2047.5 | 360.00000000001455 | 1060.0000000000146 | 700 | 10 | 85.34186046511628 | 918 | 0 | 142.00000000001455 | 0 |  | 8.101851851851851 | 700 | 2023 | 4 | 2023_04_Asomata_english.xlsx
20 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.4 | 7760.00000000002 | 40.47 | 2012.4 | -1439.9999999999873 | 2137.466321243536 | 707 | 10.1 | 85.69260227909582 | 1965 | 2870.4663212435235 | 232.46632124353619 | 60 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
21 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 83.85 | 6439.999999999993 | 40.48 | 2024.0999999999947 | -1320.0000000000273 | 2998.702127659547 | 707 | 10.1 | 86.81878940582232 | 2956.5 | 3611.702127659574 | 72.20212765954693 | 30 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
22 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 40 | 0 | 2.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.6 | 8239.999999999993 | 40.55 | 2106 | 1800 | 7687.708333333333 | 757.5 | 10.1 | 85.29028959233953 | 7673.4 | 5130.208333333333 | 74.3083333333334 | 60 |  | 8.76736111111111 | 757.5 | 2023 | 4 | 2023_04_Asomata_english.xlsx
23 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 45 | 2.1000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.6 | 5839.999999999993 | 40.44 | 1977.3 | -2400 | 6312.255319148937 | 808 | 10.1 | 87.34053693830923 | 6270.7 | 7904.255319148937 | 101.55531914893709 | 60 |  | 9.351851851851851 | 808 | 2023 | 4 | 2023_04_Asomata_english.xlsx
24 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 16.4 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 24 | 84.9 | 8960.00000000002 | 40.54 | 2094.3 | 3120.0000000000273 | 7518.919191919219 | 707 | 10.1 | 84.6938540007847 | 7554.3 | 3691.9191919191917 | 24.619191919218792 | 60 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
25 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 25 | 85.1 | 9439.999999999993 | 40.62 | 2187.9 | 479.9999999999727 | 3917.5699481865013 | 707 | 10.1 | 84.30084307734718 | 3883.6 | 2730.5699481865286 | 93.96994818650137 | 60 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
26 | 80 | 0 | 80 | 0 | 0 | 2 | 80 | 40 | 2 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 26 | 84.5 | 8000.000000000007 | 40.46 | 2000.7 | -1439.9999999999854 | 1945.3195876288805 | 808 | 10.1 | 85.49097262667443 | 1846.9 | 2577.319587628866 | 158.41958762888044 | 60 |  | 9.351851851851851 | 808 | 2023 | 4 | 2023_04_Asomata_english.xlsx
27 | 80 | 0 | 80 | 0 | 0 | 2 | 80 | 35 | 2.2999999999956344 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 27 | 84.35 | 7639.999999999993 | 40.5 | 2047.5 | -360.00000000001455 | 5937.5833333333185 | 808 | 10.1 | 85.79377418261309 | 5909.4 | 5489.583333333333 | 88.18333333331884 | 60 |  | 9.351851851851851 | 808 | 2023 | 4 | 2023_04_Asomata_english.xlsx
28 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 28 | 85.25 | 9800.000000000007 | 40.5 | 2047.5 | 2160.0000000000146 | 7418.453367875662 | 745.5 | 10.65 | 79.67000461342235 | 7467.6 | 4512.953367875647 | 10.853367875662116 | 60 |  | 8.628472222222221 | 745.5 | 2023 | 4 | 2023_04_Asomata_english.xlsx
29 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 40 | 2.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 29 | 84.25 | 7400.000000000007 | 40.48 | 2024.0999999999947 | -2400 | 3477.984455958549 | 707 | 10.1 | 85.99683637002754 | 3431 | 5170.984455958549 | 106.98445595854946 | 60 |  | 8.18287037037037 | 707 | 2023 | 4 | 2023_04_Asomata_english.xlsx
30 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 40 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 30 | 85.2 | 9680.000000000015 | 40.48 | 2024.0999999999947 | 2280.0000000000073 | 4368.535353535361 | 735 | 9.8 | 86.68036659108087 | 4242.7 | 1353.5353535353536 | 125.83535353536081 | 0 |  | 8.506944444444445 | 735 | 2023 | 4 | 2023_04_Asomata_english.xlsx
1 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 50 | 0 | 4.099999999998545 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 85.2 | 9680.000000000015 | 40.68 | 2258.1 | -480.00000000000546 | 8490.499999999995 | 2070.5 | 10.1 | 84.10570223689035 | 8365.8 | 6900 | 184.69999999999527 | 60 |  | 23.96412037037037 | 2070.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
2 | 150 | 195 | 345 | 0 | 0 | 4 | 345 | 100 | 4.5900000000037835 | 5 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 84.8 | 8720 | 41.57 | 3299.4 | -960.0000000000146 | 2524.4999999999854 | 3484.5 | 10.1 | 84.89173683723513 | 2540.4 | 0 | 44.09999999998536 | 60 |  | 40.329861111111114 | 3484.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
3 | 0 | 270 | 270 | 0 | 0 | 3 | 270 | 55 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 85.35 | 10040 | 41.6 | 3334.5 | 1319.9999999999927 | 5501.195959595952 | 2721.6 | 10.08 | 83.98097801211989 | 5487 | 1459.5959595959596 | 14.195959595952445 | 0 |  | 31.5 | 2721.6 | 2023 | 6 | 2023_06_Asomata_english.xlsx
4 | 130 | 130 | 260 | 0 | 0 | 3 | 260 | 100 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 85.2 | 9680.000000000015 | 41.8 | 3568.5 | -359.9999999999782 | 9826.209424083792 | 2626 | 10.1 | 84.10570223689035 | 9831.95 | 7560.2094240837705 | 54.2594240837916 | 60 |  | 30.39351851851852 | 2626 | 2023 | 6 | 2023_06_Asomata_english.xlsx
5 | 135 | 120 | 255 | 0 | 0 | 3 | 255 | 90 | 3.099999999998545 | 2.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.3 | 7520 | 41.86 | 3638.7 | -2160.0000000000146 | 9505.92553191488 | 2575.5 | 10.1 | 85.89518526320718 | 9383.92 | 9090.425531914894 | 182.0055319148778 | 60 |  | 29.80902777777778 | 2575.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
6 | 145 | 145 | 290 | 0 | 0 | 3 | 290 | 108 | 2.900000000001455 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84.9 | 8960.00000000002 | 41.93 | 3720.6 | 1440.00000000002 | 11220.102564102584 | 3016 | 10.4 | 82.25076205845436 | 11263.9 | 6764.1025641025635 | 16.20256410258662 | 60 |  | 34.907407407407405 | 3016 | 2023 | 6 | 2023_06_Asomata_english.xlsx
7 | 320 | 0 | 320 | 0 | 0 | 3 | 320 | 50 | 7.149999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.3 | 9920 | 41.82 | 3591.9 | 959.99999999998 | 6752.60606060604 | 3232 | 10.1 | 83.91146273980748 | 6505.6 | 2560.6060606060605 | 247.0060606060406 | 0 |  | 37.407407407407405 | 3232 | 2023 | 6 | 2023_06_Asomata_english.xlsx
8 | 145 | 180 | 325 | 0 | 0 | 3 | 325 | 55 | 3.0500000000029104 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85.5 | 10400 | 41.8 | 3568.5 | 480.0000000000073 | 5557.371794871802 | 3282.5 | 10.1 | 83.5256629111187 | 5519.85 | 1794.871794871795 | 97.52179487180274 | 60 |  | 37.991898148148145 | 3282.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
9 | 360 | 0 | 360 | 0 | 0 | 3 | 360 | 50 | 7.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.2 | 9680.000000000015 | 42 | 3802.5 | -719.9999999999927 | 2880.0000000000073 | 3600 | 10 | 84.94675925925925 | 2779.7 | 0 | 100.300000000007 | 0 |  | 41.666666666666664 | 3600 | 2023 | 6 | 2023_06_Asomata_english.xlsx
10 | 210 | 265 | 475 | 0 | 0 | 3 | 475 | 100 | 4.540000000000873 | 5.4099999999962165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 85.1 | 9439.999999999993 | 41.95 | 3744 | -240.00000000002183 | 4509.999999999978 | 4750 | 10 | 85.14385150812066 | 4216 | 0 | 293.9999999999782 | 0 |  | 54.976851851851855 | 4750 | 2023 | 6 | 2023_06_Asomata_english.xlsx
11 | 180 | 165 | 345 | 0 | 0 | 3 | 345 | 90 | 4.010000000002037 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84 | 6800.000000000007 | 42 | 3802.5 | -2639.9999999999854 | 5046.627659574483 | 3484.5 | 10.1 | 86.50872230080151 | 5026 | 4202.127659574468 | 80.627659574483 | 60 |  | 40.329861111111114 | 3484.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
12 | 180 | 180 | 360 | 0 | 0 | 3 | 360 | 100 | 4 | 4.040000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 85.2 | 9680.000000000015 | 41.76 | 3521.7 | 2880.0000000000073 | 6480.000000000007 | 3600 | 10 | 84.94675925925925 | 6324 | 0 | 156.00000000000728 | 0 |  | 41.666666666666664 | 3600 | 2023 | 6 | 2023_06_Asomata_english.xlsx
13 | 190 | 190 | 380 | 0 | 0 | 3 | 380 | 100 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85.2 | 9680.000000000015 | 42 | 3802.5 | 0 | 8105.676767676768 | 3838 | 10.1 | 84.10570223689035 | 8067.75 | 4267.676767676768 | 97.92676767676767 | 60 |  | 44.4212962962963 | 3838 | 2023 | 6 | 2023_06_Asomata_english.xlsx
14 | 210 | 210 | 420 | 0 | 0 | 2 | 420 | 109 | 4.19999999999709 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.45 | 10280 | 42.03 | 3837.6 | 600 | 4842 | 4242 | 10.1 | 83.62177989950894 | 4820.2 | 0 | 21.800000000000182 | 0 |  | 49.09722222222222 | 4242 | 2023 | 6 | 2023_06_Asomata_english.xlsx
15 | 280 | 310 | 590 | 0 | 0 | 3 | 590 | 110 | 5.700000000004366 | 6.930000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84.7 | 8480.000000000015 | 41.95 | 3744 | -1800 | 4159 | 5959 | 10.1 | 85.09054652537853 | 3607.5 | 0 | 551.5 | 0 |  | 68.9699074074074 | 5959 | 2023 | 6 | 2023_06_Asomata_english.xlsx
16 | 155 | 180 | 335 | 0 | 0 | 2 | 335 | 110 | 3.3699999999953434 | 3.8700000000026193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 85.35 | 10040 | 41.96 | 3755.7 | 1559.9999999999782 | 4943.499999999978 | 3383.5 | 10.1 | 83.81467904575926 | 4468.8 | 0 | 474.6999999999789 | 0 |  | 39.160879629629626 | 3383.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
17 | 180 | 180 | 360 | 0 | 0 | 3 | 360 | 90 | 4 | 3.819999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.55 | 8120 | 41.97 | 3767.4 | -1919.9999999999927 | 4086.967741935491 | 3636 | 10.1 | 85.39051319938106 | 3862.4 | 2370.967741935484 | 284.56774193549154 | 60 |  | 42.083333333333336 | 3636 | 2023 | 6 | 2023_06_Asomata_english.xlsx
18 | 200 | 195 | 395 | 0 | 0 | 2 | 395 | 100 | 3.9800000000032014 | 3.9800000000032014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 85.05 | 9320 | 41.99 | 3790.8 | 1200 | 11692.064102564102 | 3989.5 | 10.1 | 84.3987534641966 | 11695.04 | 6502.564102564102 | 57.02410256410076 | 60 |  | 46.17476851851852 | 3989.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
19 | 210 | 220 | 430 | 0 | 0 | 3 | 430 | 110 | 4.080000000001746 | 4.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.4 | 10160 | 41.96 | 3755.7 | 840.00000000002 | 6854.717171717191 | 4343 | 10.1 | 83.71811835561435 | 6560.95 | 1671.7171717171716 | 293.76717171719156 | 0 |  | 50.2662037037037 | 4343 | 2023 | 6 | 2023_06_Asomata_english.xlsx
20 | 210 | 285 | 495 | 0 | 0 | 2 | 495 | 110 | 4.019999999996799 | 5.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 85.3 | 9920 | 41.98 | 3779.1 | -240.00000000002 | 4759.49999999998 | 4999.5 | 10.1 | 83.91146273980748 | 4635.7 | 0 | 153.79999999998017 | 30 |  | 57.864583333333336 | 4999.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
21 | 345 | 260 | 605 | 0 | 0 | 3 | 605 | 110 | 6.94999999999709 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85.3 | 9920 | 41.95 | 3744 | 0 | 8459.21794871795 | 6110.5 | 10.1 | 83.91146273980748 | 8167.5 | 2348.7179487179487 | 291.7179487179492 | 0 |  | 70.72337962962963 | 6110.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
22 | 315 | 315 | 630 | 0 | 0 | 3 | 630 | 110 | 6.400000000001455 | 6.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 85 | 9200.000000000007 | 42.05 | 3861 | -719.9999999999927 | 5643.000000000007 | 6363 | 10.1 | 84.49689154962007 | 5624.75 | 0 | 48.250000000007276 | 30 |  | 73.64583333333333 | 6363 | 2023 | 6 | 2023_06_Asomata_english.xlsx
23 | 295 | 300 | 595 | 0 | 0 | 3 | 595 | 110 | 5.599999999998545 | 5.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 85 | 9200.000000000007 | 41.84 | 3615.3 | 0 | 6009.5 | 6009.5 | 10.1 | 84.49689154962007 | 5669.6 | 0 | 339.90000000000055 | 0 |  | 69.55439814814815 | 6009.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
24 | 240 | 295 | 535 | 0 | 0 | 3 | 535 | 110 | 4.600000000005821 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 85.2 | 9680.000000000015 | 42.07 | 3884.4 | 480.0000000000073 | 7664.112244897966 | 5403.5 | 10.1 | 84.10570223689035 | 7482.05 | 1780.612244897959 | 182.0622448979666 | 0 |  | 62.54050925925926 | 5403.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
25 | 215 | 210 | 425 | 0 | 0 | 3 | 425 | 110 | 4.19999999999709 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 85 | 9200.000000000007 | 42.02 | 3825.9 | -480.0000000000073 | 7551.861702127652 | 4292.5 | 10.1 | 84.49689154962007 | 7380.3 | 3739.3617021276596 | 231.561702127653 | 60 |  | 49.68171296296296 | 4292.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
26 | 235 | 375 | 610 | 0 | 0 | 3 | 610 | 110 | 4.400000000001455 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.9 | 8960.00000000002 | 42.01 | 3814.2 | -239.99999999998727 | 6921.000000000013 | 6161 | 10.1 | 84.6938540007847 | 6712.45 | 1000 | 208.550000000012 | 0 |  | 71.30787037037037 | 6161 | 2023 | 6 | 2023_06_Asomata_english.xlsx
27 | 555 | 220 | 775 | 0 | 0 | 4 | 775 | 110 | 11.099999999998545 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 85.05 | 9320 | 42 | 3802.5 | 359.99999999998 | 8187.49999999998 | 7827.5 | 10.1 | 84.3987534641966 | 7782.4 | 0 | 405.09999999998035 | 0 |  | 90.59606481481481 | 7827.5 | 2023 | 6 | 2023_06_Asomata_english.xlsx
28 | 405 | 465 | 870 | 0 | 0 | 3 | 870 | 110 | 9.69999999999709 | 10.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 85 | 9200.000000000007 | 41.97 | 3767.4 | -119.99999999999272 | 8667.000000000007 | 8787 | 10.1 | 84.49689154962007 | 8565 | 0 | 162.00000000000728 | 60 |  | 101.70138888888889 | 8787 | 2023 | 6 | 2023_06_Asomata_english.xlsx
29 | 570 | 270 | 840 | 0 | 0 | 3 | 840 | 110 | 11.30000000000291 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 29 | 84.2 | 7280.000000000014 | 41.83 | 3603.6 | -1919.9999999999936 | 6564.000000000006 | 8484 | 10.1 | 86.09872835624795 | 6365.6 | 0 | 258.4000000000069 | 60 |  | 98.19444444444444 | 8484 | 2023 | 6 | 2023_06_Asomata_english.xlsx
30 | 0 | 530 | 530 | 0 | 0 | 4 | 530 | 45 | 0 | 11.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.3 | 7520 | 41.9 | 3685.5 | 239.99999999998636 | 5592.999999999986 | 5353 | 10.1 | 85.89518526320718 | 5428.8 | 0 | 224.19999999998618 | 60 |  | 61.95601851851852 | 5353 | 2023 | 6 | 2023_06_Asomata_english.xlsx
1 | 505 | 150 | 655 | 0 | 0 | 4 | 655 | 85 | 11.05000000000291 | 3.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 85.3 | 9920 | 41.95 | 3744 | 2400 | 9015.5 | 6615.5 | 10.1 | 83.91146273980748 | 8627.1 | 0 | 388.4 | 0 |  | 76.56828703703704 | 6615.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
2 | 280 | 585 | 865 | 0 | 0 | 5 | 865 | 110 | 5.149999999994179 | 11.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 85.35 | 10040 | 41.95 | 3744 | 119.99999999999272 | 11876.9081632653 | 8736.5 | 10.1 | 83.81467904575926 | 11460 | 3020.408163265306 | 416.90816326529966 | 0 |  | 101.11689814814815 | 8736.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
3 | 290 | 390 | 680 | 0 | 0 | 4 | 680 | 50 | 5.900000000001455 | 9 | 0 | 0 | 5.25 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ ΨΥΓΕΙΟΥ ΓΕΝΝΗΤΡΙΑΣ | 3 | 85 | 9200.000000000007 | 41.82 | 3591.9 | -839.9999999999854 | 6028.000000000015 | 6868 | 10.1 | 84.49689154962007 | 5798.8 | 0 | 229.20000000001437 | 0 |  | 79.49074074074075 | 6868 | 2023 | 7 | 2023_07_Asomata_english.xlsx
4 | 175 | 565 | 740 | 0 | 0 | 4 | 740 | 110 | 3.2000000000043656 | 11.14999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.95 | 9080.000000000015 | 41.92 | 3708.9 | -119.99999999999272 | 7354.000000000007 | 7474 | 10.1 | 84.59525812883966 | 7291.7 | 0 | 122.30000000000746 | 60 |  | 86.50462962962963 | 7474 | 2023 | 7 | 2023_07_Asomata_english.xlsx
5 | 500 | 190 | 690 | 0 | 0 | 4 | 690 | 100 | 11.049999999995634 | 4.830000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85 | 9200.000000000007 | 42 | 3802.5 | 119.99999999999272 | 7088.999999999993 | 6969 | 10.1 | 84.49689154962007 | 6900.3 | 0 | 188.69999999999254 | 0 |  | 80.65972222222223 | 6969 | 2023 | 7 | 2023_07_Asomata_english.xlsx
6 | 0 | 570 | 570 | 0 | 0 | 4 | 570 | 54 | 0 | 11.12000000000262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.45 | 10280 | 41.98 | 3779.1 | 1080.0000000000073 | 6723.000000000007 | 5643 | 9.9 | 85.3111087863677 | 6308.5 | 0 | 414.5000000000073 | 0 |  | 65.3125 | 5643 | 2023 | 7 | 2023_07_Asomata_english.xlsx
7 | 235 | 315 | 550 | 0 | 0 | 3 | 550 | 75 | 5.05000000000291 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 7 | 85.4 | 10160 | 41.75 | 3510 | -119.99999999999454 | 5435.0000000000055 | 5555 | 10.1 | 83.71811835561435 | 5224.4 | 0 | 210.6000000000049 | 0 |  | 64.29398148148148 | 5555 | 2023 | 7 | 2023_07_Asomata_english.xlsx
8 | 0 | 560 | 560 | 0 | 0 | 3 | 560 | 55 | 0 | 11.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.3 | 9920 | 41.92 | 3708.9 | -240.00000000002 | 9074.031088082882 | 5656 | 10.1 | 83.91146273980748 | 8810.85 | 3658.0310880829015 | 323.1810880828816 | 60 |  | 65.46296296296296 | 5656 | 2023 | 7 | 2023_07_Asomata_english.xlsx
9 | 605 | 300 | 905 | 0 | 0 | 4 | 905 | 108 | 12.19999999999709 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 85.1 | 9439.999999999993 | 41.81 | 3580.2 | -480.0000000000073 | 8660.499999999993 | 9140.5 | 10.1 | 84.30084307734718 | 8370 | 0 | 290.4999999999927 | 0 |  | 105.79282407407408 | 9140.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
10 | 100 | 555 | 655 | 0 | 0 | 3 | 655 | 110 | 2.099999999998545 | 11.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.1 | 9439.999999999993 | 41.96 | 3755.7 | 0 | 6615.5 | 6615.5 | 10.1 | 84.30084307734718 | 6436.69 | 0 | 178.81 | 0 |  | 76.56828703703704 | 6615.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
11 | 300 | 290 | 590 | 0 | 0 | 3 | 590 | 50 | 6.100000000005821 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.95 | 9080.000000000015 | 41.89 | 3673.8 | -359.9999999999782 | 5599.000000000022 | 5959 | 10.1 | 84.59525812883966 | 5347.5 | 0 | 251.50000000002183 | 0 |  | 68.9699074074074 | 5959 | 2023 | 7 | 2023_07_Asomata_english.xlsx
12 | 145 | 585 | 730 | 0 | 0 | 3 | 730 | 80 | 3.8099999999976717 | 13.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 85.05 | 9320 | 41.96 | 3755.7 | 239.99999999998545 | 7612.999999999985 | 7373 | 10.1 | 84.3987534641966 | 7248.85 | 0 | 364.1499999999851 | 0 |  | 85.33564814814815 | 7373 | 2023 | 7 | 2023_07_Asomata_english.xlsx
13 | 655 | 40 | 695 | 0 | 0 | 3 | 695 | 75 | 13.769999999996799 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.7 | 8480.000000000015 | 42 | 3802.5 | -839.9999999999854 | 6179.500000000015 | 7019.5 | 10.1 | 85.09054652537853 | 5966.75 | 0 | 212.75000000001455 | 0 |  | 81.24421296296296 | 7019.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
14 | 0 | 560 | 560 | 0 | 0 | 3 | 560 | 50 | 0 | 11.810000000004948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.8 | 8720 | 41.59 | 3322.8 | 239.99999999998545 | 8252.38297872339 | 5656 | 10.1 | 84.89173683723513 | 8051.9 | 2356.3829787234044 | 200.48297872338935 | 0 |  | 65.46296296296296 | 5656 | 2023 | 7 | 2023_07_Asomata_english.xlsx
15 | 255 | 305 | 560 | 0 | 0 | 3 | 560 | 55 | 4.819999999999709 | 6.040000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.7 | 8480.000000000015 | 41.15 | 2808 | -239.99999999998545 | 7756.425531914909 | 5656 | 10.1 | 85.09054652537853 | 7668 | 2340.425531914894 | 148.4255319149088 | 60 |  | 65.46296296296296 | 5656 | 2023 | 7 | 2023_07_Asomata_english.xlsx
16 | 0 | 590 | 590 | 0 | 0 | 3 | 590 | 55 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 83.9 | 6560.00000000002 | 40.97 | 2597.4 | -1919.9999999999945 | 7001.365591397855 | 5959 | 10.1 | 86.71518703182966 | 7041.6 | 2962.3655913978496 | 19.765591397854223 | 60 |  | 68.9699074074074 | 5959 | 2023 | 7 | 2023_07_Asomata_english.xlsx
17 | 295 | 310 | 605 | 0 | 0 | 3 | 605 | 54 | 6.330000000001746 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 85.25 | 9800.000000000007 | 40.74 | 2328.3 | 3239.9999999999873 | 9350.499999999987 | 6110.5 | 10.1 | 84.00847021118297 | 9139 | 0 | 211.49999999998727 | 0 |  | 70.72337962962963 | 6110.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
18 | 75 | 630 | 705 | 0 | 0 | 4 | 705 | 108 | 1.6900000000023283 | 12.12999999999738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.1 | 9439.999999999993 | 41.5 | 3217.5 | -360.00000000001455 | 10143.919689119157 | 7120.5 | 10.1 | 84.30084307734718 | 10162.3 | 3383.419689119171 | 41.619689119157556 | 60 |  | 82.41319444444444 | 7120.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
19 | 615 | 0 | 615 | 0 | 0 | 3 | 615 | 55 | 11.979999999995925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 85.4 | 10160 | 41.32 | 3006.9 | 720.0000000000273 | 10343.871134020646 | 6211.5 | 10.1 | 83.71811835561435 | 10455 | 3412.3711340206182 | 38.87113402064642 | 150 |  | 71.89236111111111 | 6211.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
20 | 70 | 610 | 680 | 0 | 0 | 3 | 680 | 70 | 1.9200000000055297 | 12.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 85.2 | 9680.000000000015 | 41.55 | 3276 | -480.00000000000546 | 6319.9999999999945 | 6800 | 10 | 84.94675925925925 | 5978.7 | 0 | 341.2999999999947 | 0 |  | 78.70370370370371 | 6800 | 2023 | 7 | 2023_07_Asomata_english.xlsx
21 | 570 | 210 | 780 | 0 | 0 | 3 | 780 | 110 | 12.07999999999447 | 5.019999999996799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85 | 9200.000000000007 | 42.05 | 3861 | -480.0000000000073 | 7319.999999999993 | 7800 | 10 | 85.34186046511628 | 7212.4 | 0 | 107.59999999999309 | 0 |  | 90.27777777777777 | 7800 | 2023 | 7 | 2023_07_Asomata_english.xlsx
22 | 80 | 620 | 700 | 0 | 0 | 3 | 700 | 100 | 2.220000000001164 | 13.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 85.1 | 9439.999999999993 | 42 | 3802.5 | 239.99999999998545 | 7309.999999999985 | 7070 | 10.1 | 84.30084307734718 | 7172.5 | 0 | 137.49999999998545 | 0 |  | 81.82870370370371 | 7070 | 2023 | 7 | 2023_07_Asomata_english.xlsx
23 | 650 | 95 | 745 | 0 | 0 | 3 | 745 | 100 | 13.180000000000291 | 2.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480.000000000015 | 42 | 3802.5 | -959.9999999999782 | 11088.309523809545 | 7524.5 | 10.1 | 85.09054652537853 | 10921.7 | 4523.809523809524 | 166.60952380954404 | 0 |  | 87.08912037037037 | 7524.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
24 | 95 | 650 | 745 | 0 | 0 | 3 | 745 | 100 | 2.2600000000020373 | 13.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.7 | 8480.000000000015 | 42 | 3802.5 | 0 | 7524.5 | 7524.5 | 10.1 | 85.09054652537853 | 7300.85 | 0 | 223.65 | 0 |  | 87.08912037037037 | 7524.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
25 | 660 | 0 | 660 | 0 | 0 | 3 | 660 | 54 | 12.639999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.95 | 9080.000000000015 | 42 | 3802.5 | 600 | 7200 | 6600 | 10 | 85.44121071012806 | 7060.4 | 0 | 139.6 | 0 |  | 76.38888888888889 | 6600 | 2023 | 7 | 2023_07_Asomata_english.xlsx
26 | 170 | 460 | 630 | 0 | 0 | 4 | 630 | 70 | 5.25 | 10.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 26 | 84.8 | 8720 | 42.02 | 3825.9 | -360.00000000001455 | 6002.999999999985 | 6363 | 10.1 | 84.89173683723513 | 5911.2 | 0 | 151.79999999998563 | 60 |  | 73.64583333333333 | 6363 | 2023 | 7 | 2023_07_Asomata_english.xlsx
27 | 590 | 75 | 665 | 0 | 0 | 3 | 665 | 100 | 11.849999999998545 | 1.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.45 | 7880.000000000014 | 42.11 | 3931.2 | -839.9999999999864 | 8229.131578947381 | 6716.5 | 10.1 | 85.5916687075068 | 8261.82 | 2352.6315789473683 | 27.31157894738135 | 60 |  | 77.73726851851852 | 6716.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
28 | 200 | 455 | 655 | 0 | 0 | 3 | 655 | 105 | 4 | 9 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 1 | 2 | ΕΡΕΥΝΕΣ ΑΠΟ ΟΜΑΔΑ ΔΙΑΣΩΣΗΣ ΕΜΑΚ ΣΤΗΝ ΛΙΜΝΗ ΑΝΑΡΡΥΘΜΙΣΗΣ | 28 | 83.75 | 6200.000000000007 | 42.13 | 3954.6 | -1680.0000000000064 | 9595.074468085098 | 6615.5 | 10.1 | 87.02673860200392 | 9438.9 | 4659.574468085106 | 156.17446808509885 | 0 |  | 76.56828703703704 | 6615.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
29 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.2 | 9680.000000000015 | 42 | 3802.5 | 3480.0000000000073 | 11571.030612244906 | 6514.5 | 10.1 | 84.10570223689035 | 11626.32 | 1576.5306122448978 | 4.71061224490586 | 60 |  | 75.39930555555556 | 6514.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
30 | 0 | 645 | 645 | 0 | 0 | 3 | 645 | 50 | 0 | 12.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.65 | 8360.00000000002 | 42.07 | 3884.4 | -1319.9999999999945 | 8673.223404255325 | 6514.5 | 10.1 | 85.19030097617029 | 8562.9 | 3478.723404255319 | 110.32340425532493 | 0 |  | 75.39930555555556 | 6514.5 | 2023 | 7 | 2023_07_Asomata_english.xlsx
31 | 295 | 375 | 670 | 0 | 0 | 3 | 670 | 55 | 6 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.8 | 8720 | 42.09 | 3907.8 | 359.99999999998 | 7126.99999999998 | 6767 | 10.1 | 84.89173683723513 | 7029.9 | 0 | 97.09999999998035 | 0 |  | 78.32175925925925 | 6767 | 2023 | 7 | 2023_07_Asomata_english.xlsx
1 | 640 | 90 | 730 | 0 | 0 | 3 | 730 | 100 | 13.099999999998545 | 2.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.75 | 8600.000000000007 | 42.1 | 3919.5 | -119.99999999999272 | 7253.000000000007 | 7373 | 10.1 | 84.9910254183313 | 7091.04 | 0 | 161.9600000000064 | 0 |  | 85.33564814814815 | 7373 | 2023 | 8 | 2023_08_Asomata_english.xlsx
2 | 0 | 665 | 665 | 0 | 0 | 5 | 665 | 55 | 0 | 13.10000000000582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 85 | 9200.000000000007 | 41.94 | 3732.3 | 600 | 7316.5 | 6716.5 | 10.1 | 84.49689154962007 | 7181.8 | 0 | 134.7 | 0 |  | 77.73726851851852 | 6716.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
3 | 630 | 130 | 760 | 0 | 0 | 2 | 760 | 95 | 13.150000000001455 | 3.1999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 85.15 | 9560.00000000002 | 42.07 | 3884.4 | 360.00000000001273 | 8036.000000000013 | 7676 | 10.1 | 84.20315959753565 | 8032.5 | 0 | 23.500000000012733 | 20 |  | 88.8425925925926 | 7676 | 2023 | 8 | 2023_08_Asomata_english.xlsx
4 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 50 | 0 | 12.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.45 | 10280 | 41.86 | 3638.7 | 719.9999999999945 | 7122.4999999999945 | 6402.5 | 9.85 | 85.74416010000408 | 6897.5 | 0 | 224.99999999999454 | 0 |  | 74.10300925925925 | 6402.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
5 | 525 | 180 | 705 | 0 | 0 | 3 | 705 | 105 | 10.849999999998545 | 3.4499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85.4 | 10160 | 41.65 | 3393 | -119.99999999999454 | 7000.5000000000055 | 7120.5 | 10.1 | 83.71811835561435 | 6960.8 | 0 | 39.700000000004366 | 0 |  | 82.41319444444444 | 7120.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
6 | 105 | 590 | 695 | 0 | 0 | 3 | 695 | 110 | 2.0500000000029104 | 11.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.65 | 8360.00000000002 | 41.7 | 3451.5 | -1800 | 10626.907407407407 | 7019.5 | 10.1 | 85.19030097617029 | 10582.5 | 5407.407407407407 | 104.40740740740694 | 60 |  | 81.24421296296296 | 7019.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
7 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 55 | 12.94999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.2 | 9680.000000000015 | 41.25 | 2925 | 1319.9999999999945 | 7869.9999999999945 | 6550 | 10 | 84.94675925925925 | 7774.8 | 0 | 95.19999999999527 | 0 |  | 75.81018518518519 | 6550 | 2023 | 8 | 2023_08_Asomata_english.xlsx
8 | 0 | 620 | 620 | 0 | 0 | 3 | 620 | 55 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.4 | 10160 | 41.02 | 2655.9 | 480.00000000000546 | 10614.34042553192 | 6262 | 10.1 | 83.71811835561435 | 10547.64 | 3872.3404255319147 | 66.7004255319207 | 0 |  | 72.47685185185185 | 6262 | 2023 | 8 | 2023_08_Asomata_english.xlsx
9 | 670 | 155 | 825 | 0 | 0 | 3 | 825 | 108 | 13.150000000001455 | 3.0499999999956344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 84.1 | 7039.999999999993 | 42.05 | 3861 | -3120.0000000000273 | 6844.932432432405 | 8332.5 | 10.1 | 86.3032383998495 | 6844.56 | 1632.4324324324325 | 60.37243243240573 | 60 |  | 96.44097222222223 | 8332.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
10 | 0 | 665 | 665 | 0 | 0 | 4 | 665 | 50 | 0 | 12.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 85.4 | 10160 | 41.78 | 3545.1 | 3120.0000000000273 | 9836.500000000027 | 6716.5 | 10.1 | 83.71811835561435 | 9636.8 | 0 | 199.700000000028 | 0 |  | 77.73726851851852 | 6716.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
11 | 690 | 0 | 690 | 0 | 0 | 3 | 690 | 55 | 13.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 85.1 | 9439.999999999993 | 41.79 | 3556.8 | -720.0000000000273 | 9427.947368421024 | 6969 | 10.1 | 84.30084307734718 | 9280.82 | 3178.9473684210525 | 147.12736842102458 | 0 |  | 80.65972222222223 | 6969 | 2023 | 8 | 2023_08_Asomata_english.xlsx
12 | 0 | 625 | 625 | 0 | 0 | 2 | 625 | 54 | 0 | 13.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85 | 9200.000000000007 | 41.93 | 3720.6 | -239.99999999998545 | 8854.414893617035 | 6312.5 | 10.1 | 84.49689154962007 | 8762.4 | 2781.9148936170213 | 152.01489361703352 | 60 |  | 73.0613425925926 | 6312.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
13 | 612 | 0 | 612 | 0 | 0 | 4 | 612 | 54 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.25 | 9800.000000000007 | 41.93 | 3720.6 | 600 | 10749.285106382978 | 6181.2 | 10.1 | 84.00847021118297 | 10533.6 | 3968.0851063829787 | 215.68510638297994 | 0 |  | 71.54166666666667 | 6181.2 | 2023 | 8 | 2023_08_Asomata_english.xlsx
14 | 296 | 363 | 659 | 0 | 0 | 2 | 659 | 55 | 6.100000000005821 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.1 | 9439.999999999993 | 41.98 | 3779.1 | -360.00000000001455 | 8015.476719576704 | 6655.9 | 10.1 | 84.30084307734718 | 7965.25 | 1719.5767195767196 | 110.22671957670445 | 60 |  | 77.03587962962963 | 6655.9 | 2023 | 8 | 2023_08_Asomata_english.xlsx
15 | 617 | 0 | 617 | 0 | 0 | 3 | 617 | 54 | 12.89999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.3 | 9920 | 41.93 | 3720.6 | 480.0000000000073 | 9259.068421052638 | 6231.7 | 10.1 | 83.91146273980748 | 9127.95 | 2547.3684210526317 | 131.11842105263713 | 0 |  | 72.1261574074074 | 6231.7 | 2023 | 8 | 2023_08_Asomata_english.xlsx
16 | 0 | 640 | 640 | 0 | 0 | 3 | 640 | 54 | 0 | 13.180000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 85.3 | 9920 | 42.05 | 3861 | 0 | 6400 | 6400 | 10 | 84.75057736720554 | 6304.74 | 0 | 95.26000000000022 | 0 |  | 74.07407407407408 | 6400 | 2023 | 8 | 2023_08_Asomata_english.xlsx
17 | 644 | 131 | 775 | 0 | 0 | 3 | 775 | 104 | 12.980000000003201 | 2.529999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 17 | 85.1 | 9439.999999999993 | 42 | 3802.5 | -480.0000000000073 | 7347.499999999993 | 7827.5 | 10.1 | 84.30084307734718 | 7250.4 | 0 | 157.0999999999931 | 60 |  | 90.59606481481481 | 7827.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
18 | 0 | 632 | 632 | 0 | 0 | 4 | 632 | 54 | 0 | 12.990000000005239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 85.05 | 9320 | 42 | 3802.5 | -119.99999999999272 | 6263.200000000007 | 6383.2 | 10.1 | 84.3987534641966 | 6142.5 | 0 | 150.7000000000071 | 30 |  | 73.87962962962963 | 6383.2 | 2023 | 8 | 2023_08_Asomata_english.xlsx
19 | 579 | 209 | 788 | 0 | 0 | 3 | 788 | 108 | 12.019999999996799 | 4.399999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 84.95 | 9080.000000000015 | 42 | 3802.5 | -239.99999999998545 | 9145.115789473697 | 7958.8 | 10.1 | 84.59525812883966 | 9035.36 | 1426.3157894736842 | 109.75578947369831 | 0 |  | 92.11574074074073 | 7958.8 | 2023 | 8 | 2023_08_Asomata_english.xlsx
20 | 0 | 589 | 589 | 0 | 0 | 3 | 589 | 54 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.4 | 10160 | 41.91 | 3697.2 | 1080.0000000000055 | 6822.7500000000055 | 5742.75 | 9.75 | 86.72338414273898 | 6706.7 | 0 | 116.05000000000473 | 0 |  | 66.46701388888889 | 5742.75 | 2023 | 8 | 2023_08_Asomata_english.xlsx
21 | 602 | 225 | 827 | 0 | 0 | 3 | 827 | 108 | 11.80000000000291 | 4.30000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.85 | 8839.999999999993 | 41.9 | 3685.5 | -1320.0000000000273 | 7032.699999999973 | 8352.7 | 10.1 | 84.79267996811349 | 6837.6 | 0 | 195.09999999997308 | 0 |  | 96.67476851851853 | 8352.7 | 2023 | 8 | 2023_08_Asomata_english.xlsx
22 | 248 | 568 | 816 | 0 | 0 | 3 | 816 | 108 | 5.019999999996799 | 10.980000000003201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84.2 | 7280.000000000014 | 42 | 3802.5 | -1559.999999999979 | 6681.600000000021 | 8241.6 | 10.1 | 86.09872835624795 | 6772.35 | 0 | 29.250000000021828 | 120 |  | 95.38888888888889 | 8241.6 | 2023 | 8 | 2023_08_Asomata_english.xlsx
23 | 540 | 184 | 724 | 0 | 0 | 3 | 724 | 108 | 10.10000000000582 | 3.6199999999953434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.15 | 9560.00000000002 | 42.02 | 3825.9 | 2280.0000000000064 | 9592.4 | 7312.4 | 10.1 | 84.20315959753565 | 9337.9 | 0 | 254.50000000000364 | 0 |  | 84.63425925925925 | 7312.4 | 2023 | 8 | 2023_08_Asomata_english.xlsx
24 | 0 | 564 | 564 | 0 | 0 | 3 | 564 | 54 | 0 | 11.040000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85.1 | 9439.999999999993 | 41.84 | 3615.3 | -120.00000000002728 | 5407.199999999973 | 5527.2 | 9.8 | 86.88148113073535 | 5311.8 | 0 | 95.39999999997417 | 0 |  | 63.972222222222236 | 5527.2 | 2023 | 8 | 2023_08_Asomata_english.xlsx
25 | 564 | 0 | 564 | 0 | 0 | 3 | 564 | 54 | 11.180000000000291 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 85.35 | 10040 | 41.75 | 3510 | 600 | 6127.2 | 5527.2 | 9.8 | 86.38043452675188 | 6045 | 0 | 82.20000000000073 | 0 |  | 63.972222222222236 | 5527.2 | 2023 | 8 | 2023_08_Asomata_english.xlsx
26 | 0 | 559 | 559 | 0 | 0 | 3 | 559 | 54 | 0 | 11.270000000004075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 85.1 | 9439.999999999993 | 41.67 | 3416.4 | -600 | 6620.368085106383 | 5645.9 | 10.1 | 84.30084307734718 | 6437.2 | 1574.468085106383 | 183.16808510638202 | 0 |  | 65.34606481481481 | 5645.9 | 2023 | 8 | 2023_08_Asomata_english.xlsx
27 | 553 | 0 | 553 | 0 | 0 | 3 | 553 | 53 | 11.219999999993888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.7 | 8480.000000000015 | 41.74 | 3498.3 | -959.9999999999782 | 6082.74680851066 | 5585.3 | 10.1 | 85.09054652537853 | 6055.1 | 1457.4468085106382 | 87.64680851065987 | 60 |  | 64.64467592592592 | 5585.3 | 2023 | 8 | 2023_08_Asomata_english.xlsx
28 | 478 | 336 | 814 | 0 | 0 | 3 | 814 | 107 | 9.80000000000291 | 7.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84.6 | 8239.999999999993 | 42 | 3802.5 | -240.00000000002183 | 7981.399999999978 | 8221.4 | 10.1 | 85.29028959233953 | 7873.6 | 0 | 167.79999999997926 | 60 |  | 95.1550925925926 | 8221.4 | 2023 | 8 | 2023_08_Asomata_english.xlsx
29 | 512 | 0 | 512 | 0 | 0 | 3 | 512 | 50 | 10.980000000003201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.85 | 8839.999999999993 | 41.8 | 3568.5 | 600 | 5668.8 | 5068.8 | 9.9 | 86.50566340181277 | 5409.3 | 0 | 259.5 | 0 |  | 58.666666666666664 | 5068.8 | 2023 | 8 | 2023_08_Asomata_english.xlsx
30 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 50 | 0 | 11.040000000000873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.4 | 10160 | 41.8 | 3568.5 | 1320.0000000000273 | 6520.000000000027 | 5200 | 10 | 84.55529953917049 | 6455.75 | 0 | 64.25000000002728 | 0 |  | 60.18518518518518 | 5200 | 2023 | 8 | 2023_08_Asomata_english.xlsx
31 | 195 | 335 | 530 | 0 | 0 | 3 | 530 | 50 | 4 | 7.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 85.05 | 9320 | 41.93 | 3720.6 | -840.00000000002 | 4486.499999999981 | 5326.5 | 10.05 | 84.81864776003835 | 4464 | 0 | 22.4999999999809 | 0 |  | 61.649305555555564 | 5326.5 | 2023 | 8 | 2023_08_Asomata_english.xlsx
1 | 330 | 190 | 520 | 0 | 0 | 3 | 520 | 50 | 7.039999999993597 | 4.010000000002037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 85.05 | 9320 | 42.09 | 3907.8 | 0 | 5252 | 5252 | 10.1 | 84.3987534641966 | 5328.4 | 0 | 23.600000000000364 | 100 |  | 60.78703703703704 | 5252 | 2023 | 9 | 2023_09_Asomata_english.xlsx
2 | 0 | 480 | 480 | 0 | 0 | 3 | 480 | 50 | 0 | 11.059999999997672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.2 | 9680.000000000015 | 42.04 | 3849.3 | 360.00000000001455 | 9727.789473684225 | 4752 | 9.9 | 85.8048073325851 | 9555.7 | 4615.789473684211 | 172.08947368422378 | 0 |  | 55 | 4752 | 2023 | 9 | 2023_09_Asomata_english.xlsx
3 | 235 | 220 | 455 | 0 | 0 | 3 | 455 | 80 | 5.560000000004948 | 4.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.9 | 8960.00000000002 | 42.03 | 3837.6 | -719.9999999999945 | 9141.457446808516 | 4595.5 | 10.1 | 84.6938540007847 | 9163.5 | 5265.95744680851 | 37.95744680851567 | 60 |  | 53.188657407407405 | 4595.5 | 2023 | 9 | 2023_09_Asomata_english.xlsx
4 | 0 | 465 | 465 | 0 | 0 | 2 | 465 | 45 | 0 | 10.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 83.75 | 6200.000000000007 | 42.06 | 3872.7 | -2760.0000000000127 | 5830.117021276583 | 4696.5 | 10.1 | 87.02673860200392 | 5679.4 | 3893.6170212765956 | 150.71702127658318 | 0 |  | 54.357638888888886 | 4696.5 | 2023 | 9 | 2023_09_Asomata_english.xlsx
5 | 455 | 15 | 470 | 0 | 0 | 3 | 470 | 88 | 11.099999999998545 | 0.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.55 | 8120 | 42.02 | 3825.9 | 1919.9999999999927 | 7772.263157894729 | 4747 | 10.1 | 85.39051319938106 | 7666.05 | 1105.2631578947369 | 166.2131578947301 | 60 |  | 54.942129629629626 | 4747 | 2023 | 9 | 2023_09_Asomata_english.xlsx
6 | 0 | 350 | 350 | 0 | 0 | 3 | 350 | 45 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.4 | 10160 | 41.86 | 3638.7 | 2040.00000000002 | 5470.00000000002 | 3430 | 9.8 | 86.28091789711274 | 5175.6 | 0 | 294.40000000002055 | 0 |  | 39.699074074074076 | 3430 | 2023 | 9 | 2023_09_Asomata_english.xlsx
7 | 268 | 69 | 337 | 0 | 0 | 3 | 337 | 90 | 5.400000000001455 | 1.4000000000014552 | 0 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | ΥΨΗΛΗ ΘΕΡΜΟΚΡΑΣΙΑ ΩΣΤΙΚΟΥ - ΟΔΗΓΟΥ ΕΔΡΑΝΟΥ | 7 | 85.3 | 9920 | 41.82 | 3591.9 | -240.00000000002 | 3472.2106382978523 | 3403.7 | 10.1 | 83.91146273980748 | 3285 | 308.51063829787233 | 247.21063829785226 | 60 |  | 39.394675925925924 | 3403.7 | 2023 | 9 | 2023_09_Asomata_english.xlsx
8 | 182 | 118 | 300 | 0 | 0 | 4 | 300 | 45 | 4.139999999999418 | 2.650000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85.4 | 10160 | 41.9 | 3685.5 | 240.00000000002 | 10559.148936170233 | 3000 | 10 | 84.55529953917049 | 10245.9 | 7319.148936170212 | 313.2489361702337 | 0 |  | 34.72222222222222 | 3000 | 2023 | 9 | 2023_09_Asomata_english.xlsx
9 | 277 | 0 | 277 | 0 | 0 | 3 | 277 | 47 | 6.1599999999962165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.3 | 9920 | 41.8 | 3568.5 | -240.00000000002 | 6621.5297872340225 | 2797.7 | 10.1 | 83.91146273980748 | 6414.45 | 4063.8297872340427 | 207.07978723402175 | 0 |  | 32.38078703703704 | 2797.7 | 2023 | 9 | 2023_09_Asomata_english.xlsx
10 | 0 | 178 | 178 | 0 | 0 | 3 | 178 | 45 | 0 | 4.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85.4 | 10160 | 41.18 | 2843.1 | 240.00000000002 | 9325.03404255321 | 1797.8 | 10.1 | 83.71811835561435 | 9148.6 | 7287.234042553191 | 176.43404255321002 | 0 |  | 20.80787037037037 | 1797.8 | 2023 | 9 | 2023_09_Asomata_english.xlsx
11 | 294 | 135 | 429 | 0 | 0 | 3 | 429 | 108 | 5.700000000004366 | 2.8500000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 84.8 | 8720 | 41.96 | 3755.7 | -1440.00000000002 | 2892.8999999999796 | 4332.9 | 10.1 | 84.89173683723513 | 2795.9 | 0 | 156.99999999997954 | 60 |  | 50.14930555555556 | 4332.9 | 2023 | 9 | 2023_09_Asomata_english.xlsx
12 | 0 | 268 | 268 | 0 | 0 | 3 | 268 | 46 | 0 | 6.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85 | 9200.000000000007 | 41.95 | 3744 | 480.0000000000073 | 3759.7166666666735 | 2706.8 | 10.1 | 84.49689154962007 | 3610.8 | 572.9166666666666 | 148.91666666667334 | 0 |  | 31.3287037037037 | 2706.8 | 2023 | 9 | 2023_09_Asomata_english.xlsx
13 | 336 | 0 | 336 | 0 | 0 | 2 | 336 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.7 | 8480.000000000015 | 42.02 | 3825.9 | -719.9999999999927 | 3580.335751295344 | 3393.6 | 10.1 | 85.09054652537853 | 3388.35 | 906.7357512953367 | 191.98575129534402 | 0 |  | 39.27777777777778 | 3393.6 | 2023 | 9 | 2023_09_Asomata_english.xlsx
14 | 0 | 365 | 365 | 0 | 0 | 3 | 365 | 53 | 0 | 7.80000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.5 | 8000.000000000007 | 41.95 | 3744 | -480.0000000000073 | 3206.4999999999927 | 3686.5 | 10.1 | 85.49097262667443 | 2993 | 0 | 213.49999999999272 | 0 |  | 42.667824074074076 | 3686.5 | 2023 | 9 | 2023_09_Asomata_english.xlsx
15 | 463 | 0 | 463 | 0 | 0 | 4 | 463 | 50 | 10.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.8 | 8720 | 41.9 | 3685.5 | 719.9999999999927 | 5396.299999999993 | 4676.3 | 10.1 | 84.89173683723513 | 5200.1 | 0 | 196.19999999999254 | 0 |  | 54.123842592592595 | 4676.3 | 2023 | 9 | 2023_09_Asomata_english.xlsx
16 | 74 | 447 | 521 | 0 | 0 | 3 | 521 | 108 | 1.5 | 9.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 85.15 | 9560.00000000002 | 42.07 | 3884.4 | 840.00000000002 | 7222.518848167559 | 5262.1 | 10.1 | 84.20315959753565 | 7040.25 | 1120.4188481675392 | 182.26884816755864 | 0 |  | 60.903935185185176 | 5262.1 | 2023 | 9 | 2023_09_Asomata_english.xlsx
17 | 360 | 0 | 360 | 0 | 0 | 3 | 360 | 54 | 7.630000000004657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.8 | 8720 | 42 | 3802.5 | -840.00000000002 | 6580.210526315769 | 3636 | 10.1 | 84.89173683723513 | 6409.2 | 3784.210526315789 | 171.0105263157693 | 0 |  | 42.083333333333336 | 3636 | 2023 | 9 | 2023_09_Asomata_english.xlsx
18 | 116 | 410 | 526 | 0 | 0 | 3 | 526 | 107 | 2.569999999999709 | 8.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.3 | 9920 | 41.86 | 3638.7 | 1200 | 8470.271957671957 | 5312.6 | 10.1 | 83.91146273980746 | 8325 | 1957.671957671958 | 145.27195767195735 | 0 |  | 61.488425925925924 | 5312.6 | 2023 | 9 | 2023_09_Asomata_english.xlsx
19 | 355 | 195 | 550 | 0 | 0 | 3 | 550 | 102 | 8 | 4.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.95 | 9080.000000000015 | 41.75 | 3510 | -839.9999999999854 | 7715.000000000015 | 5555 | 10.1 | 84.59525812883966 | 7723.65 | 3000 | 51.350000000014916 | 60 |  | 64.29398148148148 | 5555 | 2023 | 9 | 2023_09_Asomata_english.xlsx
20 | 0 | 444 | 444 | 0 | 0 | 3 | 444 | 53 | 0 | 9.700000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.9 | 8960.00000000002 | 42.05 | 3861 | -119.99999999999454 | 4364.400000000005 | 4484.4 | 10.1 | 84.6938540007847 | 4281.2 | 0 | 83.20000000000528 | 0 |  | 51.90277777777778 | 4484.4 | 2023 | 9 | 2023_09_Asomata_english.xlsx
21 | 510 | 0 | 510 | 0 | 0 | 3 | 510 | 50 | 12.14999999999418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.7 | 8480.000000000015 | 42 | 3802.5 | -480.00000000000546 | 4670.9999999999945 | 5151 | 10.1 | 85.09054652537853 | 4688.75 | 0 | 42.24999999999454 | 60 |  | 59.61805555555556 | 5151 | 2023 | 9 | 2023_09_Asomata_english.xlsx
22 | 0 | 531 | 531 | 0 | 0 | 3 | 531 | 54 | 0 | 11.87999999999738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.6 | 8239.999999999993 | 42 | 3802.5 | -240.00000000002183 | 5783.040425531893 | 5150.7 | 9.7 | 88.80741493635354 | 5526.1 | 872.3404255319149 | 256.9404255318923 | 0 |  | 59.614583333333336 | 5150.7 | 2023 | 9 | 2023_09_Asomata_english.xlsx
23 | 423 | 95 | 518 | 0 | 0 | 3 | 518 | 80 | 10.150000000001455 | 2.6699999999982538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 85.05 | 9320 | 41.9 | 3685.5 | 1080.0000000000073 | 6822.438297872348 | 5231.8 | 10.1 | 84.3987534641966 | 6852.4 | 510.63829787234044 | 30.038297872348267 | 60 |  | 60.55324074074074 | 5231.8 | 2023 | 9 | 2023_09_Asomata_english.xlsx
24 | 40 | 425 | 465 | 0 | 0 | 3 | 465 | 90 | 0.9000000000014552 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 84.7 | 8480.000000000015 | 41.98 | 3779.1 | -839.9999999999854 | 4557.474747474762 | 4650 | 10 | 85.94145199063232 | 4402 | 747.4747474747475 | 155.4747474747619 | 0 |  | 53.81944444444444 | 4650 | 2023 | 9 | 2023_09_Asomata_english.xlsx
25 | 342 | 90 | 432 | 0 | 0 | 3 | 432 | 70 | 8.80000000000291 | 2.6000000000058208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.6 | 8239.999999999993 | 41.94 | 3732.3 | -240.00000000002183 | 8979.582978723382 | 4363.2 | 10.1 | 85.29028959233953 | 9018.36 | 4856.382978723404 | 21.222978723380947 | 60 |  | 50.5 | 4363.2 | 2023 | 9 | 2023_09_Asomata_english.xlsx
26 | 0 | 380 | 380 | 0 | 0 | 3 | 380 | 54 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 26 | 84.35 | 7639.999999999993 | 42.04 | 3849.3 | -600 | 6312.468085106383 | 3838 | 10.1 | 85.79377418261309 | 6134.6 | 3074.468085106383 | 177.86808510638275 | 0 |  | 44.4212962962963 | 3838 | 2023 | 9 | 2023_09_Asomata_english.xlsx
27 | 400 | 185 | 585 | 0 | 0 | 3 | 585 | 106 | 9.5 | 3.6999999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.2 | 7280.000000000014 | 41.9 | 3685.5 | -359.9999999999791 | 6133.6063829787445 | 5908.5 | 10.1 | 86.09872835624795 | 5950 | 585.1063829787234 | 243.60638297874448 | 60 |  | 68.38541666666667 | 5908.5 | 2023 | 9 | 2023_09_Asomata_english.xlsx
28 | 195 | 359 | 554 | 0 | 0 | 3 | 554 | 99 | 4.110000000000582 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.7 | 8480.000000000015 | 41.94 | 3732.3 | 1200 | 8864.548936170213 | 5595.4 | 10.1 | 85.09054652537853 | 8840.3 | 2069.148936170213 | 84.24893617021371 | 60 |  | 64.76157407407408 | 5595.4 | 2023 | 9 | 2023_09_Asomata_english.xlsx
29 | 251 | 416 | 667 | 0 | 0 | 3 | 667 | 54 | 5.489999999997963 | 10.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85 | 9200.000000000007 | 41.89 | 3673.8 | 719.9999999999927 | 9307.763829787225 | 6736.7 | 10.1 | 84.4968915496201 | 9277.5 | 1851.063829787234 | 90.2638297872254 | 60 |  | 77.97106481481481 | 6736.7 | 2023 | 9 | 2023_09_Asomata_english.xlsx
30 | 114 | 383 | 497 | 0 | 0 | 3 | 497 | 98 | 2.900000000001455 | 8.589999999996508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.7 | 8480.000000000015 | 41.85 | 3627 | -719.9999999999927 | 8757.392553191497 | 5243.35 | 10.55 | 81.46109193424863 | 8822.52 | 4234.04255319149 | 34.87255319149881 | 100 |  | 60.6869212962963 | 5243.35 | 2023 | 9 | 2023_09_Asomata_english.xlsx
1 | 328 | 147 | 475 | 0 | 0 | 3 | 475 | 42 | 8.229999999995925 | 4.060000000004948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.2 | 7280.000000000014 | 42 | 3802.5 | -1200 | 8788.989361702126 | 4797.5 | 10.1 | 86.09872835624795 | 8723.5 | 5191.489361702128 | 125.48936170212619 | 60 |  | 55.526620370370374 | 4797.5 | 2023 | 10 | 2023_10_Asomata_english.xlsx
2 | 0 | 419 | 419 | 0 | 0 | 3 | 419 | 54 | 0 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.9 | 8960.00000000002 | 42 | 3802.5 | 1680.0000000000064 | 7798.891489361709 | 4315.7 | 10.3 | 83.0493131464005 | 7890 | 1803.1914893617022 | 3.8914893617093185 | 95 |  | 49.950231481481495 | 4315.7 | 2023 | 10 | 2023_10_Asomata_english.xlsx
3 | 464 | 188 | 652 | 0 | 0 | 3 | 652 | 108 | 9.520000000004075 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.95 | 9080.000000000015 | 40.97 | 2597.4 | 119.99999999999454 | 7673.621052631574 | 6585.2 | 10.1 | 84.59525812883966 | 7242.8 | 968.421052631579 | 430.8210526315743 | 0 |  | 76.2175925925926 | 6585.2 | 2023 | 10 | 2023_10_Asomata_english.xlsx
4 | 80 | 535 | 615 | 0 | 0 | 3 | 615 | 54 | 2 | 11.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.3 | 9920 | 41.91 | 3697.2 | 839.9999999999854 | 9110.010638297857 | 6211.5 | 10.1 | 83.91146273980748 | 8694.15 | 2058.5106382978724 | 415.8606382978578 | 0 |  | 71.89236111111111 | 6211.5 | 2023 | 10 | 2023_10_Asomata_english.xlsx
5 | 273 | 334 | 607 | 0 | 0 | 3 | 607 | 53 | 5.649999999994179 | 8.950000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.9 | 8960.00000000002 | 41.87 | 3650.4 | -959.99999999998 | 6340.912765957467 | 6130.7 | 10.1 | 84.6938540007847 | 6255 | 1170.212765957447 | 85.91276595746695 | 0 |  | 70.95717592592592 | 6130.7 | 2023 | 10 | 2023_10_Asomata_english.xlsx
6 | 400 | 210 | 610 | 0 | 0 | 3 | 610 | 80 | 10 | 5.19999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 85 | 9200.000000000007 | 41.94 | 3732.3 | 239.99999999998727 | 7250.740932642474 | 6161 | 10.1 | 84.49689154962007 | 7157.4 | 849.740932642487 | 93.3409326424744 | 0 |  | 71.30787037037037 | 6161 | 2023 | 10 | 2023_10_Asomata_english.xlsx
7 | 350 | 0 | 350 | 0 | 0 | 3 | 350 | 50 | 8.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.35 | 10040 | 41.98 | 3779.1 | 839.9999999999854 | 10078.510638297857 | 3430 | 9.8 | 86.38043452675188 | 9930.85 | 5808.510638297872 | 147.66063829785708 | 0 |  | 39.699074074074076 | 3430 | 2023 | 10 | 2023_10_Asomata_english.xlsx
8 | 89 | 579 | 668 | 0 | 0 | 3 | 668 | 107 | 2.2000000000043656 | 12.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 |  | 8 | 85.15 | 9560.00000000002 | 42 | 3802.5 | -479.9999999999727 | 9091.26808510641 | 6746.8 | 10.1 | 84.20315959753565 | 9022.25 | 2824.468085106383 | 69.01808510641058 | 0 |  | 78.08796296296295 | 6746.8 | 2023 | 10 | 2023_10_Asomata_english.xlsx
9 | 0 | 834 | 834 | 0 | 0 | 3 | 834 | 54 | 0 | 18.030000000006112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 85.2 | 9680.000000000015 | 41.88 | 3662.1 | 119.99999999999454 | 9656.220512820506 | 8423.4 | 10.1 | 84.10570223689035 | 9482.8 | 1112.8205128205127 | 173.4205128205067 | 0 |  | 97.49305555555556 | 8423.4 | 2023 | 10 | 2023_10_Asomata_english.xlsx
10 | 175 | 683 | 858 | 0 | 0 | 4 | 858 | 108 | 4.049999999995634 | 14.169999999998254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.05 | 9320 | 41.97 | 3767.4 | -360.00000000001455 | 8134.199999999986 | 8494.2 | 9.9 | 86.10377878670562 | 7918 | 0 | 216.19999999998527 | 0 |  | 98.3125 | 8494.2 | 2023 | 10 | 2023_10_Asomata_english.xlsx
11 | 426 | 531 | 957 | 0 | 0 | 3 | 957 | 100 | 9.400000000001455 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 85.3 | 9920 | 41.97 | 3767.4 | 600 | 10521.175531914894 | 9330.75 | 9.75 | 86.9236690945698 | 10201.8 | 590.4255319148937 | 319.37553191489496 | 0 |  | 107.99479166666667 | 9330.75 | 2023 | 10 | 2023_10_Asomata_english.xlsx
12 | 528 | 331 | 859 | 0 | 0 | 3 | 859 | 107 | 13.099999999998545 | 7.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.95 | 9080.000000000015 | 42 | 3802.5 | -839.9999999999854 | 7750.000000000015 | 8590 | 10 | 85.44121071012806 | 7518.4 | 0 | 231.60000000001492 | 0 |  | 99.42129629629629 | 8590 | 2023 | 10 | 2023_10_Asomata_english.xlsx
13 | 892 | 91 | 983 | 0 | 0 | 3 | 983 | 70 | 22.599999999998545 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.8 | 8720 | 41.8 | 3568.5 | -360.00000000001455 | 9568.299999999985 | 9928.3 | 10.1 | 84.89173683723513 | 9603.05 | 0 | 25.249999999985448 | 60 |  | 114.91087962962963 | 9928.3 | 2023 | 10 | 2023_10_Asomata_english.xlsx
14 | 133 | 467 | 600 | 0 | 0 | 3 | 600 | 108 | 2.780000000006112 | 9.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.8 | 8720 | 41.93 | 3720.6 | 0 | 6060 | 6060 | 10.1 | 84.89173683723513 | 5952 | 0 | 108 | 0 |  | 70.13888888888889 | 6060 | 2023 | 10 | 2023_10_Asomata_english.xlsx
15 | 520 | 0 | 520 | 0 | 0 | 3 | 520 | 50 | 12.019999999996799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.1 | 9439.999999999993 | 41.89 | 3673.8 | 719.9999999999927 | 5815.999999999993 | 5096 | 9.8 | 86.88148113073535 | 5727.25 | 0 | 88.74999999999272 | 0 |  | 58.98148148148148 | 5096 | 2023 | 10 | 2023_10_Asomata_english.xlsx
16 | 497 | 393 | 890 | 0 | 0 | 3 | 890 | 95 | 11.900000000001455 | 7.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 16 | 84.2 | 7280.000000000014 | 42 | 3802.5 | -2159.999999999979 | 6740.000000000021 | 8900 | 10 | 86.95971563981043 | 6682.5 | 0 | 57.50000000002092 | 0 |  | 103.00925925925925 | 8900 | 2023 | 10 | 2023_10_Asomata_english.xlsx
17 | 587 | 109 | 696 | 0 | 0 | 3 | 696 | 87 | 12.299999999995634 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 85.1 | 9439.999999999993 | 41.3 | 2983.5 | 2159.999999999979 | 9050.39999999998 | 6890.4 | 9.9 | 86.0038904122431 | 8747.6 | 0 | 302.7999999999811 | 0 |  | 79.75 | 6890.4 | 2023 | 10 | 2023_10_Asomata_english.xlsx
18 | 0 | 782 | 782 | 0 | 0 | 3 | 782 | 54 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.75 | 8600.000000000007 | 42 | 3802.5 | -839.9999999999854 | 7058.200000000014 | 7898.2 | 10.1 | 84.9910254183313 | 6986.1 | 0 | 72.10000000001492 | 0 |  | 91.41435185185185 | 7898.2 | 2023 | 10 | 2023_10_Asomata_english.xlsx
19 | 318 | 444 | 762 | 0 | 0 | 3 | 762 | 104 | 7.100000000005821 | 10.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.85 | 8839.999999999993 | 41.9 | 3685.5 | 239.99999999998545 | 7669.499999999985 | 7429.5 | 9.75 | 87.83651976184066 | 7496.2 | 0 | 173.29999999998472 | 0 |  | 85.98958333333333 | 7429.5 | 2023 | 10 | 2023_10_Asomata_english.xlsx
20 | 470 | 223 | 693 | 0 | 0 | 3 | 693 | 54 | 12 | 4.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.9 | 8960.00000000002 | 41.74 | 3498.3 | 120.00000000002728 | 6911.400000000027 | 6791.4 | 9.8 | 87.28652300080871 | 6710.8 | 0 | 200.60000000002674 | 0 |  | 78.60416666666667 | 6791.4 | 2023 | 10 | 2023_10_Asomata_english.xlsx
21 | 165 | 321 | 486 | 0 | 0 | 3 | 486 | 50 | 4.099999999998545 | 8.599999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85.3 | 9920 | 41.9 | 3685.5 | 959.99999999998 | 10835.706806282702 | 4860 | 10 | 84.75057736720554 | 10633.8 | 5015.706806282722 | 201.90680628270275 | 0 |  | 56.25 | 4860 | 2023 | 10 | 2023_10_Asomata_english.xlsx
22 | 200 | 311 | 511 | 0 | 0 | 3 | 511 | 107 | 3.75 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 83.2 | 4880.000000000014 | 41.85 | 3627 | -5039.999999999986 | 5361.831693989084 | 5314.4 | 10.4 | 85.64460418222555 | 5369 | 5087.4316939890705 | 52.83169398908376 | 60 |  | 61.50925925925926 | 5314.4 | 2023 | 10 | 2023_10_Asomata_english.xlsx
23 | 525 | 298 | 823 | 0 | 0 | 3 | 823 | 108 | 10.549999999995634 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 23 | 84.6 | 8239.999999999993 | 41.87 | 3650.4 | 3359.999999999979 | 11590 | 8230 | 10 | 86.14319248826293 | 11436.92 | 0 | 153.0799999999781 | 0 |  | 95.25462962962963 | 8230 | 2023 | 10 | 2023_10_Asomata_english.xlsx
24 | 364 | 270 | 634 | 0 | 0 | 3 | 634 | 108 | 6.370000000002619 | 5.120000000002619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 84.6 | 8239.999999999993 | 41.9 | 3685.5 | 0 | 6664.468085106383 | 6340 | 10 | 86.14319248826293 | 6488.75 | 324.468085106383 | 175.7180851063831 | 0 |  | 73.37962962962963 | 6340 | 2023 | 10 | 2023_10_Asomata_english.xlsx
25 | 423 | 159 | 582 | 0 | 0 | 3 | 582 | 54 | 7.930000000000291 | 2.9799999999959255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.8 | 8720 | 41.91 | 3697.2 | 480.0000000000073 | 6270.900000000007 | 5790.9 | 9.95 | 86.17151176442964 | 6153.25 | 0 | 117.65000000000691 | 0 |  | 67.02430555555556 | 5790.9 | 2023 | 10 | 2023_10_Asomata_english.xlsx
26 | 154 | 478 | 632 | 0 | 0 | 3 | 632 | 108 | 3 | 9.580000000001746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 26 | 84.7 | 8480.000000000015 | 41.9 | 3685.5 | -239.99999999998545 | 6080.000000000015 | 6320 | 10 | 85.94145199063232 | 5835.9 | 0 | 244.10000000001492 | 0 |  | 73.14814814814815 | 6320 | 2023 | 10 | 2023_10_Asomata_english.xlsx
27 | 414 | 96 | 510 | 0 | 0 | 3 | 510 | 108 | 8 | 1.9700000000011642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 85.3 | 9920 | 41.64 | 3381.3 | 1439.9999999999854 | 6590.999999999985 | 5151 | 10.1 | 83.91146273980748 | 6510 | 0 | 140.99999999998545 | 60 |  | 59.61805555555556 | 5151 | 2023 | 10 | 2023_10_Asomata_english.xlsx
28 | 0 | 244 | 244 | 0 | 0 | 3 | 244 | 50 | 0 | 6.55000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.95 | 9080.000000000015 | 41.82 | 3591.9 | -839.9999999999854 | 7977.6595744681 | 2440 | 10 | 85.44121071012806 | 7908.6 | 6377.659574468085 | 129.05957446810044 | 60 |  | 28.24074074074074 | 2440 | 2023 | 10 | 2023_10_Asomata_english.xlsx
29 | 225 | 0 | 225 | 0 | 0 | 3 | 225 | 54 | 5.900000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.4 | 7760.00000000002 | 41.84 | 3615.3 | -1319.9999999999945 | 5341.973684210532 | 2272.5 | 10.1 | 85.69260227909582 | 5120.8 | 4389.473684210527 | 221.17368421053197 | 0 |  | 26.302083333333332 | 2272.5 | 2023 | 10 | 2023_10_Asomata_english.xlsx
30 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 45 | 0 | 2.5 | 0 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 30 | 84.2 | 7280.000000000014 | 41.49 | 3205.8 | -480.00000000000637 | 2327.93617021276 | 909 | 10.1 | 86.09872835624795 | 2219.2 | 1898.936170212766 | 108.73617021276004 | 0 |  | 10.520833333333334 | 909 | 2023 | 10 | 2023_10_Asomata_english.xlsx
31 | 103 | 0 | 103 | 0 | 0 | 3 | 103 | 35 | 2.9399999999950523 | 0 | 0 | 14 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 31 | 84.8 | 8720 | 41.63 | 3369.6 | 1439.9999999999864 | 2542.0999999999863 | 1102.1 | 10.7 | 80.13145252860514 | 2394 | 0 | 208.09999999998627 | 60 |  | 12.755787037037036 | 1102.1 | 2023 | 10 | 2023_10_Asomata_english.xlsx
1 | 244 | 99 | 343 | 0 | 0 | 3 | 343 | 96 | 4.860000000000582 | 2.099999999998545 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 1 | 85.2 | 9680.000000000015 | 41.9 | 3685.5 | 960.0000000000146 | 6738.717948717963 | 3430 | 10 | 84.94675925925925 | 6465 | 2348.7179487179483 | 273.7179487179628 | 0 |  | 39.699074074074076 | 3430 | 2023 | 11 | 2023_11_Asomata_english.xlsx
2 | 0 | 170 | 170 | 0 | 0 | 3 | 170 | 54 | 0 | 3.400000000001455 | 0 | 8.5 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 2 | 85.4 | 10160 | 41.74 | 3498.3 | 480.00000000000546 | 6936.361702127665 | 1717 | 10.1 | 83.71811835561435 | 6909.25 | 4739.36170212766 | 87.11170212766501 | 60 |  | 19.872685185185187 | 1717 | 2023 | 11 | 2023_11_Asomata_english.xlsx
3 | 132 | 68 | 200 | 0 | 0 | 3 | 200 | 70 | 3.1600000000034925 | 1.9899999999979627 | 0 | 9 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 3 | 85.2 | 9680.000000000015 | 41.93 | 3720.6 | -480.00000000000546 | 8709.312169312165 | 2020 | 10.1 | 84.10570223689035 | 8650.5 | 7169.31216931217 | 58.81216931216477 | 0 |  | 23.37962962962963 | 2020 | 2023 | 11 | 2023_11_Asomata_english.xlsx
4 | 55 | 0 | 55 | 0 | 0 | 3 | 55 | 40 | 1.5500000000029104 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 4 | 84.6 | 8239.999999999993 | 41.78 | 3545.1 | -1440.0000000000218 | 9780.936170212744 | 572 | 10.4 | 82.82999277717589 | 9701.01 | 10648.936170212766 | 139.92617021274418 | 60 |  | 6.62037037037037 | 572 | 2023 | 11 | 2023_11_Asomata_english.xlsx
5 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 5 | 84.65 | 8360.00000000002 | 41.16 | 2819.7 | 120.00000000002728 | 8098.835978836007 | 0 | 10.1 |  | 8110.3 | 7978.835978835979 | 48.535978836007416 | 60 |  | 0 | 0 | 2023 | 11 | 2023_11_Asomata_english.xlsx
6 | 0 | 216 | 216 | 0 | 0 | 3 | 216 | 54 | 0 | 4.059999999997672 | 0 | 6.57 | 0 | 0 | 0 | 6.57 | 0 | 0 | 0 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 6 | 84.9 | 8960.00000000002 | 41.98 | 3779.1 | 600 | 8942.497021276595 | 2198.88 | 10.18 | 84.02828343889247 | 8913.3 | 6143.617021276596 | 89.19702127659548 | 60 |  | 25.45 | 2198.88 | 2023 | 11 | 2023_11_Asomata_english.xlsx
7 | 203 | 103 | 306 | 0 | 0 | 3 | 306 | 90 | 4.94999999999709 | 2.5900000000037835 | 0 | 9.5 | 0 | 0 | 0 | 9.5 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 7 | 84.8 | 8720 | 40.83 | 2433.6 | -240.00000000002 | 2850.5999999999794 | 3090.6 | 10.1 | 84.89173683723516 | 2664.5 | 0 | 246.09999999997945 | 60 |  | 35.77083333333333 | 3090.6 | 2023 | 11 | 2023_11_Asomata_english.xlsx
8 | 121 | 264 | 385 | 0 | 0 | 3 | 385 | 108 | 2.3399999999965075 | 5.040000000000873 | 0 | 8.5 | 0 | 0 | 0 | 8.5 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 8 | 84.75 | 8600.000000000007 | 39.65 | 1053 | -119.99999999999272 | 3768.5000000000073 | 3888.5 | 10.1 | 84.9910254183313 | 3701.1 | 0 | 67.40000000000737 | 0 |  | 45.00578703703704 | 3888.5 | 2023 | 11 | 2023_11_Asomata_english.xlsx
9 | 263 | 137 | 400 | 0 | 0 | 3 | 400 | 108 | 5 | 2.6199999999953434 | 0 | 8.16 | 0 | 0 | 0 | 8.16 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 9 | 84.8 | 8720 | 42.13 | 3954.6 | 119.99999999999272 | 7509.230769230762 | 4020 | 10.05 | 85.3140837866741 | 7402.2 | 3369.230769230769 | 107.03076923076242 | 0 |  | 46.52777777777778 | 4020 | 2023 | 11 | 2023_11_Asomata_english.xlsx
10 | 84 | 191 | 275 | 0 | 0 | 2 | 275 | 75 | 2.400000000001455 | 4.599999999998545 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 1 | ΑΝΤΙΚΑΤΑΣΤΑΣΗ Δ/Κ Ρ10 | 10 | 85.3 | 9920 | 41.86 | 3638.7 | 1200 | 3922.5 | 2722.5 | 9.9 | 85.60664380525813 | 3810 | 0 | 112.5 | 0 |  | 31.510416666666668 | 2722.5 | 2023 | 11 | 2023_11_Asomata_english.xlsx
11 | 162 | 0 | 162 | 0 | 0 | 3 | 162 | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85.4 | 10160 | 41.84 | 3615.3 | 240.00000000002 | 8455.6871794872 | 1636.2 | 10.1 | 83.71811835561435 | 8310.4 | 6579.48717948718 | 145.28717948720077 | 0 |  | 18.9375 | 1636.2 | 2023 | 11 | 2023_11_Asomata_english.xlsx
12 | 0 | 207 | 207 | 0 | 0 | 3 | 207 | 54 | 0 | 5.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.15 | 7160.00000000002 | 41.88 | 3662.1 | -3000 | 7292.827659574467 | 2090.7 | 10.1 | 86.20086207909047 | 7293.6 | 8202.127659574468 | 59.227659574467 | 60 |  | 24.197916666666664 | 2090.7 | 2023 | 11 | 2023_11_Asomata_english.xlsx
13 | 339 | 0 | 339 | 0 | 0 | 3 | 339 | 54 | 7.130000000004657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.5 | 8000.000000000007 | 41.84 | 3615.3 | 839.9999999999873 | 12013.9 | 3423.9 | 10.1 | 85.49097262667443 | 11950.1 | 7750 | 63.79999999998836 | 0 |  | 39.62847222222222 | 3423.9 | 2023 | 11 | 2023_11_Asomata_english.xlsx
14 | 0 | 264 | 264 | 0 | 0 | 3 | 264 | 53 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 85.1 | 9439.999999999993 | 41.76 | 3521.7 | 1439.9999999999854 | 6412.09948186527 | 2666.4 | 10.1 | 84.30084307734718 | 6313.65 | 2305.6994818652847 | 98.44948186527017 | 0 |  | 30.86111111111111 | 2666.4 | 2023 | 11 | 2023_11_Asomata_english.xlsx
15 | 0 | 264 | 264 | 0 | 0 | 3 | 264 | 54 | 0 | 5 | 0 | 0 | 0 | 1.35 | 0 | 0 | 0 | 1.35 | 0 | 1 | ΑΠΟΚΑΤΑΣΤΑΣΗ ΒΛΑΒΗΣ Δ/Κ Ρ60 ΡΑΧΙΑΣ | 15 | 84.9 | 8960.00000000002 | 41.94 | 3732.3 | -479.9999999999727 | 5427.237696335105 | 2666.4 | 10.1 | 84.6938540007847 | 5197.6 | 3240.8376963350784 | 229.63769633510492 | 0 |  | 30.86111111111111 | 2666.4 | 2023 | 11 | 2023_11_Asomata_english.xlsx
16 | 0 | 266 | 266 | 0 | 0 | 3 | 266 | 54 | 0 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.55 | 8120 | 41.99 | 3790.8 | -840.00000000002 | 5367.652631578927 | 2686.6 | 10.1 | 85.39051319938106 | 5226.8 | 3521.052631578947 | 140.85263157892769 | 0 |  | 31.09490740740741 | 2686.6 | 2023 | 11 | 2023_11_Asomata_english.xlsx
17 | 224 | 0 | 224 | 0 | 0 | 3 | 224 | 54 | 4.919999999998254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.2 | 9680.000000000015 | 41.84 | 3615.3 | 1560.0000000000146 | 3822.4000000000146 | 2262.4 | 10.1 | 84.10570223689035 | 3586.8 | 0 | 235.60000000001492 | 0 |  | 26.185185185185187 | 2262.4 | 2023 | 11 | 2023_11_Asomata_english.xlsx
18 | 0 | 140 | 140 | 0 | 0 | 3 | 140 | 35 | 0 | 4.049999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85.25 | 9800.000000000007 | 41.91 | 3697.2 | 119.99999999999272 | 7888.838709677412 | 1414 | 10.1 | 84.00847021118297 | 7854.36 | 6354.8387096774195 | 94.47870967741164 | 60 |  | 16.36574074074074 | 1414 | 2023 | 11 | 2023_11_Asomata_english.xlsx
19 | 240 | 0 | 240 | 0 | 0 | 3 | 240 | 54 | 4.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.5 | 8000.000000000007 | 41.95 | 3744 | -1800 | 9001.659574468085 | 2424 | 10.1 | 85.49097262667443 | 9008.2 | 8377.659574468085 | 53.45957446808461 | 60 |  | 28.055555555555557 | 2424 | 2023 | 11 | 2023_11_Asomata_english.xlsx
20 | 126 | 232 | 358 | 0 | 0 | 3 | 358 | 100 | 3 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.3 | 7520 | 41.86 | 3638.7 | -480.0000000000073 | 5779.417021276588 | 3615.8 | 10.1 | 85.89518526320718 | 5745.6 | 2643.6170212765956 | 63.817021276587184 | 30 |  | 41.84953703703703 | 3615.8 | 2023 | 11 | 2023_11_Asomata_english.xlsx
21 | 320 | 0 | 320 | 0 | 0 | 3 | 320 | 54 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.5 | 8000.000000000007 | 41.95 | 3744 | 480.0000000000073 | 3712.0000000000073 | 3232 | 10.1 | 85.49097262667443 | 3547.8 | 0 | 164.20000000000755 | 0 |  | 37.407407407407405 | 3232 | 2023 | 11 | 2023_11_Asomata_english.xlsx
22 | 0 | 270 | 270 | 0 | 0 | 3 | 270 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.9 | 6560.00000000002 | 41.98 | 3779.1 | -1439.9999999999873 | 2767.7446808510767 | 2862 | 10.6 | 82.6248480208943 | 2750.4 | 1345.7446808510638 | 77.34468085107665 | 60 |  | 33.125 | 2862 | 2023 | 11 | 2023_11_Asomata_english.xlsx
23 | 353 | 144 | 497 | 0 | 0 | 4 | 497 | 107 | 8.400000000001455 | 2.9500000000043656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.55 | 8120 | 41.88 | 3662.1 | 1559.99999999998 | 6579.69999999998 | 5019.7 | 10.1 | 85.39051319938106 | 6600.7 | 0 | 38.99999999997908 | 60 |  | 58.098379629629626 | 5019.7 | 2023 | 11 | 2023_11_Asomata_english.xlsx
24 | 0 | 260 | 260 | 0 | 0 | 3 | 260 | 54 | 0 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.45 | 10280 | 41.9 | 3685.5 | 2160.0000000000146 | 7087.02040816328 | 2626 | 10.1 | 83.62177989950894 | 6874.6 | 2301.020408163265 | 212.42040816327972 | 0 |  | 30.39351851851852 | 2626 | 2023 | 11 | 2023_11_Asomata_english.xlsx
25 | 113 | 0 | 113 | 0 | 0 | 4 | 113 | 50 | 3.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.35 | 10040 | 41.58 | 3311.1 | -240.00000000002183 | 8545.2790575916 | 1141.3 | 10.1 | 83.81467904575926 | 8515.35 | 7643.979057591623 | 89.92905759160021 | 60 |  | 13.20949074074074 | 1141.3 | 2023 | 11 | 2023_11_Asomata_english.xlsx
26 | 28 | 263 | 291 | 0 | 0 | 3 | 291 | 100 | 0.8000000000029104 | 6.549999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.5 | 8000.000000000007 | 42 | 3802.5 | -2039.9999999999854 | 2515.3162162162307 | 2939.1 | 10.1 | 85.49097262667443 | 2474.7 | 1616.2162162162163 | 100.6162162162309 | 60 |  | 34.017361111111114 | 2939.1 | 2023 | 11 | 2023_11_Asomata_english.xlsx
27 | 271 | 40 | 311 | 0 | 0 | 3 | 311 | 80 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 85.2 | 9680.000000000015 | 41.94 | 3732.3 | 1680.0000000000073 | 4821.100000000008 | 3141.1 | 10.1 | 84.10570223689035 | 4680 | 0 | 141.10000000000764 | 0 |  | 36.355324074074076 | 3141.1 | 2023 | 11 | 2023_11_Asomata_english.xlsx
28 | 0 | 337 | 337 | 0 | 0 | 3 | 337 | 51 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.3 | 9920 | 41.97 | 3767.4 | 239.99999999998545 | 10550.435751295321 | 3403.7 | 10.1 | 83.91146273980748 | 10387.9 | 6906.735751295337 | 162.53575129532146 | 0 |  | 39.394675925925924 | 3403.7 | 2023 | 11 | 2023_11_Asomata_english.xlsx
29 | 277 | 0 | 277 | 0 | 0 | 4 | 277 | 50 | 7.05000000000291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.2 | 9680.000000000015 | 41.97 | 3767.4 | -239.99999999998545 | 7126.121052631594 | 2797.7 | 10.1 | 84.10570223689035 | 6963.4 | 4568.421052631579 | 162.721052631593 | 0 |  | 32.38078703703704 | 2797.7 | 2023 | 11 | 2023_11_Asomata_english.xlsx
30 | 0 | 277 | 277 | 0 | 0 | 3 | 277 | 47 | 0 | 7.1600000000034925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.2 | 9680.000000000015 | 41.87 | 3650.4 | 0 | 5824.2957446808505 | 2797.7 | 10.1 | 84.10570223689035 | 5807.25 | 3026.595744680851 | 77.04574468085048 | 60 |  | 32.38078703703704 | 2797.7 | 2023 | 11 | 2023_11_Asomata_english.xlsx
1 | 216 | 0 | 216 | 0 | 0 | 3 | 216 | 40 | 5.799999999995634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85.4 | 10160 | 41.79 | 3556.8 | 480.00000000000546 | 9475.429787234048 | 2181.6 | 10.1 | 83.71811835561435 | 9405.4 | 6813.829787234043 | 70.02978723404885 | 0 |  | 25.25 | 2181.6 | 2023 | 12 | 2023_12_Asomata_english.xlsx
2 | 0 | 292 | 292 | 0 | 0 | 3 | 292 | 54 | 0 | 6.0899999999965075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85.4 | 10160 | 41.88 | 3662.1 | 0 | 6273.668085106383 | 2949.2 | 10.1 | 83.71811835561435 | 6038.4 | 3324.468085106383 | 235.2680851063824 | 0 |  | 34.13425925925926 | 2949.2 | 2023 | 12 | 2023_12_Asomata_english.xlsx
3 | 146 | 0 | 146 | 0 | 0 | 3 | 146 | 54 | 3.0500000000029104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85.25 | 9800.000000000007 | 41.7 | 3451.5 | -360.00000000001273 | 8182.662827225118 | 1474.6 | 10.1 | 84.00847021118297 | 8015.4 | 7068.062827225131 | 167.2628272251186 | 0 |  | 17.06712962962963 | 1474.6 | 2023 | 12 | 2023_12_Asomata_english.xlsx
4 | 156 | 496 | 652 | 0 | 0 | 3 | 652 | 108 | 2.900000000001455 | 9.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.2 | 7280.000000000014 | 41.92 | 3708.9 | -2519.9999999999936 | 4065.2000000000053 | 6585.2 | 10.1 | 86.09872835624796 | 3963.9 | 0 | 101.30000000000564 | 0 |  | 76.21759259259258 | 6585.2 | 2023 | 12 | 2023_12_Asomata_english.xlsx
5 | 0 | 305 | 305 | 0 | 0 | 3 | 305 | 54 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 5 | 84.85 | 8839.999999999993 | 41.91 | 3697.2 | 1559.999999999979 | 6645.681347150238 | 3080.5 | 10.1 | 84.79267996811352 | 6432.6 | 2005.181347150259 | 213.0813471502379 | 0 |  | 35.65393518518518 | 3080.5 | 2023 | 12 | 2023_12_Asomata_english.xlsx
6 | 0 | 378 | 378 | 0 | 0 | 4 | 378 | 54 | 0 | 7.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85.25 | 9800.000000000007 | 41.82 | 3591.9 | 960.0000000000146 | 4740.000000000015 | 3780 | 10 | 84.84855491329479 | 4605.6 | 0 | 134.4000000000142 | 0 |  | 43.75 | 3780 | 2023 | 12 | 2023_12_Asomata_english.xlsx
7 | 256 | 47 | 303 | 0 | 0 | 3 | 303 | 107 | 5.129999999997381 | 0.9700000000011642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 85.35 | 10040 | 41.96 | 3755.7 | 239.99999999998545 | 5157.179487179473 | 3030 | 10 | 84.65282583621685 | 4886.8 | 1887.179487179487 | 270.3794871794735 | 0 |  | 35.06944444444444 | 3030 | 2023 | 12 | 2023_12_Asomata_english.xlsx
8 | 161 | 313 | 474 | 0 | 0 | 3 | 474 | 108 | 2.8700000000026193 | 6.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 85.35 | 10040 | 41.92 | 3708.9 | 0 | 5783.661538461539 | 4645.2 | 9.8 | 86.38043452675188 | 5519.05 | 1138.4615384615383 | 264.61153846153957 | 0 |  | 53.7638888888889 | 4645.2 | 2023 | 12 | 2023_12_Asomata_english.xlsx
9 | 245 | 0 | 245 | 0 | 0 | 3 | 245 | 54 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.5 | 10400 | 41.94 | 3732.3 | 360.00000000001455 | 4288.723404255334 | 2450 | 10 | 84.36091954022989 | 4196.85 | 1478.723404255319 | 91.87340425533421 | 0 |  | 28.35648148148148 | 2450 | 2023 | 12 | 2023_12_Asomata_english.xlsx
10 | 0 | 350 | 350 | 0 | 0 | 3 | 350 | 54 | 0 | 7.099999999998545 | 0 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΚΟΜΠΡΕΣΕΡ ΑΕΡΑ Δ/Κ ΜΟΝ Νο Ι | 10 | 85.15 | 9560.00000000002 | 41.9 | 3685.5 | -839.9999999999873 | 2695.0000000000127 | 3535 | 10.1 | 84.20315959753565 | 2533.1 | 0 | 191.90000000001282 | 30 |  | 40.914351851851855 | 3535 | 2023 | 12 | 2023_12_Asomata_english.xlsx
11 | 0 | 440 | 440 | 0 | 0 | 3 | 440 | 54 | 0 | 8.400000000001455 | 0 | 0 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΚΟΜΠΡΕΣΕΡ ΑΕΡΑ Δ/Κ ΜΟΝ Νο Ι | 11 | 84.65 | 8360.00000000002 | 41.9 | 3685.5 | -1200 | 3512.421052631579 | 4444 | 10.1 | 85.19030097617029 | 3344.25 | 268.42105263157896 | 168.1710526315792 | 0 |  | 51.43518518518518 | 4444 | 2023 | 12 | 2023_12_Asomata_english.xlsx
12 | 86 | 205 | 291 | 0 | 0 | 4 | 291 | 70 | 1.9499999999970896 | 3.9499999999970896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 83.8 | 6320 | 41.6 | 3334.5 | -2040.00000000002 | 3510.8021276595546 | 2939.1 | 10.1 | 86.9226396323843 | 3445.6 | 2611.7021276595747 | 125.20212765955466 | 60 |  | 34.017361111111114 | 2939.1 | 2023 | 12 | 2023_12_Asomata_english.xlsx
13 | 219 | 0 | 219 | 0 | 0 | 3 | 219 | 54 | 4.849999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.25 | 9800.000000000007 | 40.65 | 2223 | 3480.0000000000073 | 7635.452020202028 | 2135.25 | 9.75 | 87.02415888543057 | 7470.8 | 2020.20202020202 | 164.65202020202833 | 0 |  | 24.713541666666668 | 2135.25 | 2023 | 12 | 2023_12_Asomata_english.xlsx
14 | 0 | 250 | 250 | 0 | 0 | 4 | 250 | 54 | 0 | 5.150000000001455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 85.4 | 10160 | 40.23 | 1731.5999999999947 | 360.00000000001273 | 9932.872340425545 | 2525 | 10.1 | 83.71811835561435 | 9900.63 | 7047.8723404255325 | 92.24234042554417 | 60 |  | 29.224537037037038 | 2525 | 2023 | 12 | 2023_12_Asomata_english.xlsx
15 | 185 | 65 | 250 | 0 | 0 | 3 | 250 | 108 | 4.30000000000291 | 1.4000000000014552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 85.2 | 9680.000000000015 | 41.22 | 2889.9 | -480.00000000000546 | 4138.264248704658 | 2525 | 10.1 | 84.10570223689035 | 4056.78 | 2093.2642487046633 | 81.48424870465806 | 0 |  | 29.224537037037038 | 2525 | 2023 | 12 | 2023_12_Asomata_english.xlsx
16 | 0 | 226 | 226 | 0 | 0 | 3 | 226 | 54 | 0 | 4.69999999999709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85.4 | 10160 | 41.26 | 2936.7 | 480.00000000000546 | 6568.882722513094 | 2282.6 | 10.1 | 83.71811835561435 | 6401.85 | 3806.282722513089 | 167.032722513095 | 0 |  | 26.41898148148148 | 2282.6 | 2023 | 12 | 2023_12_Asomata_english.xlsx
17 | 152 | 0 | 152 | 0 | 0 | 3 | 152 | 54 | 3.029999999998836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.15 | 9560.00000000002 | 40.65 | 2223 | -600 | 6068.178723404255 | 1535.2 | 10.1 | 84.20315959753565 | 5903.37 | 5132.978723404255 | 164.80872340425503 | 0 |  | 17.76851851851852 | 1535.2 | 2023 | 12 | 2023_12_Asomata_english.xlsx
18 | 0 | 271 | 271 | 0 | 0 | 4 | 271 | 54 | 0 | 5.760000000002037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.95 | 9080.000000000015 | 40.29 | 1801.8 | -480.00000000000546 | 8778.152631578942 | 2737.1 | 10.1 | 84.59525812883966 | 8761.2 | 6521.052631578947 | 76.9526315789426 | 60 |  | 31.67939814814815 | 2737.1 | 2023 | 12 | 2023_12_Asomata_english.xlsx
19 | 221 | 167 | 388 | 0 | 0 | 3 | 388 | 107 | 4.569999999999709 | 3.4400000000023283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.1 | 9439.999999999993 | 41.94 | 3732.3 | 359.9999999999782 | 9491.565957446786 | 3918.8 | 10.1 | 84.30084307734718 | 9346.2 | 5212.765957446809 | 145.36595744678561 | 0 |  | 45.35648148148148 | 3918.8 | 2023 | 12 | 2023_12_Asomata_english.xlsx
20 | 0 | 258 | 258 | 0 | 0 | 3 | 258 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 85.3 | 9920 | 41.8 | 3568.5 | 480.0000000000073 | 3970.994764397913 | 2580 | 10 | 84.75057736720554 | 3717.9 | 910.9947643979058 | 253.09476439791297 | 0 |  | 29.86111111111111 | 2580 | 2023 | 12 | 2023_12_Asomata_english.xlsx
21 | 263 | 77 | 340 | 0 | 0 | 3 | 340 | 108 | 5.05000000000291 | 1.5999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 85.25 | 9800.000000000007 | 41.84 | 3615.3 | -119.99999999999272 | 3178.0000000000073 | 3298 | 9.7 | 87.47273702401526 | 3014.75 | 0 | 163.25000000000728 | 0 |  | 38.1712962962963 | 3298 | 2023 | 12 | 2023_12_Asomata_english.xlsx
22 | 0 | 261 | 261 | 0 | 0 | 4 | 261 | 54 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85.2 | 9680.000000000015 | 41.86 | 3638.7 | -119.99999999999272 | 10726.626315789481 | 2636.1 | 10.1 | 84.10570223689035 | 10731 | 8210.526315789473 | 55.62631578948094 | 60 |  | 30.510416666666668 | 2636.1 | 2023 | 12 | 2023_12_Asomata_english.xlsx
23 | 203 | 0 | 203 | 0 | 0 | 3 | 203 | 51 | 5.149999999994179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.35 | 10040 | 41.56 | 3287.7 | 359.9999999999782 | 7729.448936170191 | 2050.3 | 10.1 | 83.81467904575928 | 7481.4 | 5319.148936170212 | 248.04893617019115 | 0 |  | 23.730324074074073 | 2050.3 | 2023 | 12 | 2023_12_Asomata_english.xlsx
24 | 0 | 262 | 262 | 0 | 0 | 3 | 262 | 54 | 0 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 85.25 | 9800.000000000007 | 41.65 | 3393 | -239.99999999998545 | 9374.285106382993 | 2646.2 | 10.1 | 84.00847021118297 | 9390 | 6968.085106382979 | 44.285106382993035 | 60 |  | 30.627314814814813 | 2646.2 | 2023 | 12 | 2023_12_Asomata_english.xlsx
25 | 270 | 0 | 270 | 0 | 0 | 3 | 270 | 54 | 5.100000000005821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.3 | 9920 | 41.94 | 3732.3 | 119.99999999999272 | 9926.787234042546 | 2727 | 10.1 | 83.91146273980748 | 9908.6 | 7079.787234042553 | 78.18723404254524 | 60 |  | 31.5625 | 2727 | 2023 | 12 | 2023_12_Asomata_english.xlsx
26 | 0 | 203 | 203 | 0 | 0 | 3 | 203 | 50 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600.000000000007 | 41.75 | 3510 | -1319.9999999999927 | 9724.923655913984 | 2050.3 | 10.1 | 84.99102541833132 | 9691.2 | 8994.623655913978 | 93.72365591398375 | 60 |  | 23.730324074074073 | 2050.3 | 2023 | 12 | 2023_12_Asomata_english.xlsx
27 | 244 | 0 | 244 | 0 | 0 | 3 | 244 | 54 | 5.110000000000582 | 0 | 0 | 0 | 5.32 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | ΒΛΑΒΗ ΚΟΜΠΡΕΣΕΡ ΑΕΡΑ Δ/Κ Μον. Νο Ι | 27 | 84.8 | 8720 | 41.84 | 3615.3 | 119.99999999999272 | 5256.8085106382905 | 2440 | 10 | 85.74065420560747 | 5141.55 | 2696.808510638298 | 115.25851063829123 | 0 |  | 28.24074074074074 | 2440 | 2023 | 12 | 2023_12_Asomata_english.xlsx
28 | 187 | 267 | 454 | 0 | 0 | 4 | 454 | 107 | 3.4899999999979627 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.9 | 8960.00000000002 | 41.85 | 3627 | 240.00000000002 | 8197.740425531934 | 4585.4 | 10.1 | 84.6938540007847 | 8150.3 | 3372.3404255319147 | 87.44042553193412 | 40 |  | 53.07175925925926 | 4585.4 | 2023 | 12 | 2023_12_Asomata_english.xlsx
29 | 257 | 0 | 257 | 0 | 0 | 3 | 257 | 54 | 5.099999999998545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85.35 | 10040 | 41.83 | 3603.6 | 1079.9999999999727 | 9165.061702127632 | 2595.7 | 10.1 | 83.81467904575926 | 9118.8 | 5489.36170212766 | 106.261702127631 | 60 |  | 30.042824074074073 | 2595.7 | 2023 | 12 | 2023_12_Asomata_english.xlsx
30 | 0 | 329 | 329 | 0 | 0 | 3 | 329 | 54 | 0 | 6.200000000004366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.4 | 10160 | 41.9 | 3685.5 | 120.00000000002728 | 4284.7367346939045 | 3322.9 | 10.1 | 83.71811835561435 | 4215.15 | 841.8367346938775 | 69.58673469390396 | 0 |  | 38.45949074074074 | 3322.9 | 2023 | 12 | 2023_12_Asomata_english.xlsx
31 | 558 | 57 | 615 | 0 | 0 | 3 | 615 | 108 | 11.19999999999709 | 1.0999999999985448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 85.1 | 9439.999999999993 | 41.78 | 3545.1 | -720.0000000000273 | 5552.999999999972 | 6273 | 10.2 | 83.47436422364771 | 5590.2 | 0 | 22.799999999971078 | 60 |  | 72.60416666666666 | 6273 | 2023 | 12 | 2023_12_Asomata_english.xlsx