## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 590 | 160 | 750 | 0 | 0 | 5 | 745 | 105 | 13.2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.55 | 8120 | 42.001 | 3803.67 | -600 | 10024.3404 | 7752 | 10.336 | 83.4408 | 9840.4 | 2872.3404 | 243.9404 | 60 |  | 89.7222 | 7752
2 | 600 | 0 | 600 | 0 | 0 | 5 | 595 | 55 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.5 | 8000 | 41.151 | 2809.17 | -120 | 7780.4255 | 6060 | 10.1 | 85.491 | 7784 | 1840.4255 | 56.4255 | 60 |  | 70.1389 | 6060
3 | 235 | 0 | 235 | 0 | 0 | 4 | 231 | 54 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.6 | 8240 | 40.865 | 2474.55 | 240 | 2754.5 | 2514.5 | 10.7 | 80.5077 | 2628 | 0 | 156.5 | 30 |  | 29.103 | 2514.5
4 | 355 | 0 | 355 | 0 | 0 | 5 | 350 | 54 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 83.55 | 5720 | 41.3 | 2983.5 | -2520 | 3465.193 | 3628.81 | 10.222 | 86.402 | 3268.8 | 2356.383 | 256.393 | 60 |  | 42.0001 | 3628.81
5 | 195 | 0 | 195 | 0 | 0 | 5 | 190 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 83.6 | 5840 | 40.452 | 1991.34 | 120 | 2206.5 | 2086.5 | 10.7 | 82.4429 | 2275.2 | 0 | 81.3 | 150 |  | 24.1493 | 2086.5
6 | 145 | 0 | 145 | 0 | 0 | 0 | 145 | 40 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 83.65 | 5960 | 40.6725 | 2249.325 | 120 | 1657 | 1537 | 10.6 | 83.1208 | 1470 | 0 | 187 | 0 |  | 17.7894 | 1537
7 | 270 | 0 | 270 | 0 | 0 | 5 | 265 | 54 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 83.7 | 6080 | 41.1015 | 2751.255 | 120 | 2901 | 2781 | 10.3 | 85.4392 | 2686.4 | 0 | 214.6 | 0 |  | 32.1875 | 2781
8 | 285 | 0 | 285 | 0 | 0 | 6 | 279 | 54 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.7 | 8480 | 40.76 | 2351.7 | 2400 | 5178.75 | 2778.75 | 9.75 | 88.1451 | 4819.5 | 0 | 359.25 | 0 |  | 32.1615 | 2778.75
9 | 205 | 0 | 205 | 0 | 0 | 7 | 198 | 55 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.4 | 7760 | 40.858 | 2466.36 | -720 | 3316.1824 | 2203.75 | 10.75 | 80.5112 | 3218.4 | 1832.4324 | 197.7824 | 100 |  | 25.5064 | 2203.75
10 | 180 | 0 | 180 | 0 | 0 | 5 | 175 | 55 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84 | 6800 | 40.85 | 2457 | -960 | 3355.5319 | 1890 | 10.5 | 83.2132 | 3322.6 | 2425.5319 | 32.9319 | 0 |  | 21.875 | 1890
11 | 85 | 0 | 85 | 0 | 0 | 5 | 80 | 55 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 83.55 | 5720 | 40.93 | 2550.6 | -1080 | 2225.2287 | 922.25 | 10.85 | 81.401 | 2022.1 | 2382.9787 | 203.1287 | 0 |  | 10.6742 | 922.25
12 | 65 | 0 | 65 | 0 | 0 | 5 | 60 | 35 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.1 | 7040 | 39.781 | 1206.27 | 1320 | 1960.25 | 640.25 | 9.85 | 88.4937 | 1530 | 0 | 430.25 | 0 |  | 7.4103 | 640.25
13 | 305 | 165 | 470 | 0 | 0 | 5 | 465 | 109 | 5.9 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.4 | 7760 | 41.95 | 3744 | 720 | 5467 | 4747 | 10.1 | 85.6926 | 5439 | 0 | 88 | 60 |  | 54.9421 | 4747
14 | 165 | 0 | 165 | 0 | 0 | 4 | 161 | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.8 | 8720 | 40.707 | 2289.69 | 960 | 4459.1386 | 1773.75 | 10.75 | 79.7587 | 4123.35 | 1725.3886 | 335.7886 | 0 |  | 20.5295 | 1773.75
15 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.8 | 8720 | 40.6 | 2164.5 | 0 | 3057.8333 | 724.5 | 10.35 | 82.8412 | 2945.2 | 2333.3333 | 112.6333 | 0 |  | 8.3854 | 724.5
16 | 0 | 125 | 125 | 0 | 0 | 4 | 121 | 40 | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.35 | 7640 | 40.41 | 1942.2 | -1080 | 2441.7784 | 1212.5 | 9.7 | 89.3317 | 2443 | 2309.2784 | 98.7784 | 100 |  | 14.0336 | 1212.5
17 | 70 | 0 | 70 | 0 | 0 | 6 | 64 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.6 | 8240 | 40.032 | 1499.94 | 600 | 1307 | 707 | 10.1 | 85.2903 | 1226.4 | 0 | 140.6 | 60 |  | 8.1829 | 707
18 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.55 | 8120 | 39.9279 | 1378.143 | -120 | 3012.5319 | 707 | 10.1 | 85.3905 | 3022.2 | 2425.5319 | 50.3319 | 60 |  | 8.1829 | 707
19 | 70 | 0 | 70 | 0 | 0 | 6 | 64 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.7 | 8480 | 39.848 | 1284.66 | 360 | 1046 | 686 | 9.8 | 87.6954 | 766.5 | 0 | 279.5 | 0 |  | 7.9398 | 686
20 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 83.05 | 4520 | 39.853 | 1290.51 | -3960 | 1443.9239 | 795 | 10.6 | 84.3357 | 1576.8 | 4608.9239 | 37.1239 | 170 |  | 9.2014 | 795
21 | 75 | 0 | 75 | 0 | 0 | 5 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 83.45 | 5480 | 39.9101 | 1357.317 | 960 | 1766.25 | 806.25 | 10.75 | 82.3564 | 1361.6 | 0 | 404.65 | 0 |  | 9.3316 | 806.25
22 | 80 | 0 | 80 | 0 | 0 | 4 | 76 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 83.5 | 5600 | 41.15 | 2808 | 120 | 928 | 808 | 10.1 | 87.551 | 795 | 0 | 133 | 0 |  | 9.3519 | 808
23 | 85 | 0 | 85 | 0 | 0 | 4 | 81 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.8 | 6320 | 40.547 | 2102.49 | 720 | 1633.75 | 913.75 | 10.75 | 81.6669 | 1372 | 0 | 261.75 | 0 |  | 10.5758 | 913.75
24 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 83.9 | 6560 | 40.36 | 1883.7 | 240 | 999.5 | 759.5 | 10.85 | 80.721 | 737.3 | 0 | 262.2 | 0 |  | 8.7905 | 759.5
25 | 180 | 0 | 180 | 0 | 0 | 4 | 176 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.2 | 7280 | 41.24 | 2913.3 | 720 | 2538 | 1818 | 10.1 | 86.0987 | 2401.7 | 0 | 196.3 | 60 |  | 21.0417 | 1818
26 | 95 | 0 | 95 | 0 | 0 | 5 | 90 | 35 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.3 | 7520 | 40.815 | 2416.05 | 240 | 2346.3564 | 1021.25 | 10.75 | 80.7015 | 2160 | 1085.1064 | 186.3564 | 0 |  | 11.82 | 1021.25
27 | 90 | 0 | 90 | 0 | 0 | 5 | 85 | 40 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.4 | 7760 | 41.001 | 2633.67 | 240 | 1167 | 927 | 10.3 | 84.0287 | 967.5 | 0 | 199.5 | 0 |  | 10.7292 | 927
28 | 0 | 415 | 415 | 0 | 0 | 5 | 410 | 55 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.55 | 8120 | 41.1385 | 2794.545 | 360 | 6967.75 | 4295.25 | 10.35 | 83.3279 | 6832.8 | 2312.5 | 194.95 | 60 |  | 49.7135 | 4295.25
29 | 0 | 200 | 200 | 0 | 0 | 4 | 196 | 35 | 0 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.3 | 7520 | 41.601 | 3335.67 | -600 | 1390 | 1990 | 9.95 | 87.1901 | 1323.45 | 0 | 66.55 | 0 |  | 23.0324 | 1990
30 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.65 | 8360 | 40.5455 | 2100.735 | 840 | 1526 | 686 | 9.8 | 87.7982 | 1211.8 | 0 | 314.2 | 0 |  | 7.9398 | 686
31 | 85 | 0 | 85 | 0 | 0 | 4 | 81 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 85 | 9200 | 40.6 | 2164.5 | 840 | 1698.5 | 858.5 | 10.1 | 84.4969 | 1472.6 | 0 | 225.9 | 0 |  | 9.9363 | 858.5
| 4865 | 1065 | 5930 | 0 | 0 | 142 | 5788 | 109 | 109.1 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 6 |  |  | 84.2 | 7280 | 40.7406 | 2328.9794 | 480 | 92021.2145 | 61031.06 | 10.2919 | 84.4932 | 87043.6 | 30510.1545 | 6007.6145 | 1030 |  | 22.7864 | 61031.06