## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 115 | 0 | 115 | 0 | 0 | 0 | 115 | 35 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.8 | 8720 | 41 | 2632.5 | -480 | 2884.2857 | 1150 | 10 | 85.7407 | 2829.6 | 2214.2857 | 54.6857 | 0 |  | 13.3102 | 1150
2 | 85 | 0 | 85 | 0 | 0 | 10 | 75 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.05 | 6920 | 41.199 | 2865.33 | -1800 | 2381.9737 | 892.5 | 10.5 | 83.1142 | 2450 | 3289.4737 | 31.9737 | 100 |  | 10.3299 | 892.5
3 | 70 | 0 | 70 | 0 | 0 | 6 | 64 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.25 | 7400 | 41.189 | 2853.63 | 480 | 1162.5 | 682.5 | 9.75 | 89.0839 | 825 | 0 | 337.5 | 0 |  | 7.8993 | 682.5
4 | 65 | 0 | 65 | 0 | 0 | 5 | 60 | 35 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.4 | 7760 | 40.618 | 2185.56 | 360 | 1016.5 | 656.5 | 10.1 | 85.6926 | 915 | 0 | 161.5 | 60 |  | 7.5984 | 656.5
5 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.6 | 8240 | 40.63 | 2199.6 | 480 | 1267.5 | 787.5 | 10.5 | 82.0411 | 1087.5 | 0 | 180 | 0 |  | 9.1146 | 787.5
6 | 70 | 0 | 70 | 0 | 0 | 5 | 65 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 84.6 | 8240 | 40.56 | 2117.7 | 0 | 2446.3617 | 707 | 10.1 | 85.2903 | 2204.6 | 1739.3617 | 241.7617 | 0 |  | 8.1829 | 707
7 | 90 | 0 | 90 | 0 | 0 | 5 | 85 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.75 | 8600 | 40.704 | 2286.18 | 360 | 3715.7979 | 967.5 | 10.75 | 79.852 | 3598.9 | 2388.2979 | 116.8979 | 0 |  | 11.1979 | 967.5
8 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 85.15 | 9560 | 40.9 | 2515.5 | 960 | 1705.5 | 745.5 | 10.65 | 79.8546 | 1445.4 | 0 | 260.1 | 0 |  | 8.6285 | 745.5
9 | 75 | 0 | 75 | 0 | 0 | 5 | 70 | 55 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.65 | 8360 | 41 | 2632.5 | -1200 | 1389.734 | 802.5 | 10.7 | 80.4133 | 1416.2 | 1787.234 | 33.534 | 60 |  | 9.2882 | 802.5
10 | 0 | 70 | 70 | 0 | 0 | 0 | 70 | 36 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.65 | 8360 | 41.002 | 2634.84 | 0 | 3080.6243 | 742 | 10.6 | 81.1719 | 2989.1 | 2338.6243 | 151.5243 | 60 |  | 8.588 | 742
11 | 95 | 0 | 95 | 0 | 0 | 4 | 91 | 40 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84 | 6800 | 41.157 | 2816.19 | -1560 | 1193.2088 | 1021.25 | 10.75 | 81.278 | 1065 | 1731.9588 | 128.2088 | 0 |  | 11.82 | 1021.25
12 | 70 | 0 | 70 | 0 | 0 | 8 | 62 | 35 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.05 | 6920 | 41.211 | 2879.37 | 120 | 2642.1335 | 752.5 | 10.75 | 81.1813 | 2555 | 1769.6335 | 147.1335 | 60 |  | 8.7095 | 752.5
13 | 80 | 0 | 80 | 0 | 0 | 7 | 73 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.5 | 8000 | 40.689 | 2268.63 | 1080 | 3074.1702 | 808 | 10.1 | 85.491 | 2920 | 1186.1702 | 154.1702 | 0 |  | 9.3519 | 808
14 | 145 | 0 | 145 | 0 | 0 | 5 | 140 | 54 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.6 | 8240 | 40.999 | 2631.33 | 240 | 1791.5 | 1551.5 | 10.7 | 80.5077 | 1687.5 | 0 | 164 | 60 |  | 17.9572 | 1551.5
15 | 85 | 0 | 85 | 0 | 0 | 5 | 80 | 54 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.7 | 8480 | 41.05 | 2691 | 240 | 2942.0532 | 909.5 | 10.7 | 80.3191 | 2693.7 | 1792.5532 | 248.3532 | 0 |  | 10.5266 | 909.5
16 | 75 | 0 | 75 | 0 | 0 | 5 | 70 | 54 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 85.05 | 9320 | 41.02 | 2655.9 | 840 | 1594.875 | 754.875 | 10.065 | 84.6922 | 1554.9 | 0 | 99.975 | 60 |  | 8.737 | 754.875
17 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 54 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.3 | 7520 | 41 | 2632.5 | -1800 | 894.016 | 731.25 | 9.75 | 88.9786 | 846.8 | 1962.766 | 107.216 | 60 |  | 8.4635 | 731.25
18 | 90 | 0 | 90 | 0 | 0 | 4 | 86 | 55 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.35 | 7640 | 41.101 | 2750.67 | 120 | 3937.1667 | 963 | 10.7 | 80.9829 | 3890.9 | 2854.1667 | 46.2667 | 0 |  | 11.1458 | 963
19 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 85.2 | 9680 | 41.04 | 2679.3 | 2040 | 3950.7474 | 802.5 | 10.7 | 79.3895 | 3916.8 | 1108.2474 | 33.9474 | 0 |  | 9.2882 | 802.5
20 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 54 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 20 | 85.05 | 9320 | 40.953 | 2577.51 | -360 | 2708.7021 | 707 | 10.1 | 84.3988 | 2569.6 | 2361.7021 | 139.1021 | 0 |  | 8.1829 | 707
21 | 120 | 0 | 120 | 0 | 0 | 5 | 115 | 54 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.9 | 8960 | 41.28 | 2960.1 | -360 | 4354.5907 | 1212 | 10.1 | 84.6939 | 4161 | 3502.5907 | 193.5907 | 0 |  | 14.0278 | 1212
22 | 70 | 0 | 70 | 0 | 0 | 5 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.9 | 8960 | 40.92 | 2538.9 | 0 | 2518.8766 | 747.6 | 10.68 | 80.0944 | 2489.3 | 1771.2766 | 89.5766 | 60 |  | 8.6528 | 747.6
23 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 55 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 83.9 | 6560 | 41.08 | 2726.1 | -2400 | 1900.8871 | 752.5 | 10.75 | 81.4719 | 1967 | 3548.3871 | 13.8871 | 80 |  | 8.7095 | 752.5
24 | 155 | 0 | 155 | 0 | 0 | 4 | 151 | 55 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 83.65 | 5960 | 41.671 | 3417.57 | -600 | 4491.6383 | 1581 | 10.2 | 86.3804 | 4438 | 3510.6383 | 53.6383 | 0 |  | 18.2986 | 1581
25 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.95 | 6680 | 40.52 | 2070.9 | 720 | 2649.4036 | 802.5 | 10.7 | 81.7551 | 2569.6 | 1126.9036 | 79.8036 | 0 |  | 9.2882 | 802.5
26 | 75 | 0 | 75 | 0 | 0 | 4 | 71 | 35 | 2.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.05 | 6920 | 40.555 | 2111.85 | 240 | 990 | 750 | 10 | 87.2699 | 876 | 0 | 174 | 60 |  | 8.6806 | 750
27 | 145 | 0 | 145 | 0 | 0 | 4 | 141 | 55 | 3.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.15 | 7160 | 41.03 | 2667.6 | 240 | 2847.3571 | 1464.5 | 10.1 | 86.2009 | 2671.8 | 1142.8571 | 235.5571 | 60 |  | 16.9502 | 1464.5
28 | 70 | 0 | 70 | 0 | 0 | 4 | 66 | 35 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.053 | 6927.2 | 40.297 | 1809.99 | -232.8 | 1690.1894 | 731.5 | 10.45 | 83.5059 | 1444 | 1191.4894 | 306.1894 | 60 |  | 8.4664 | 731.5
| 1835 | 70 | 1905 | 0 | 0 | 108 | 1797 | 55 | 41.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1 |  |  | 84.4733 | 7935.9714 | 40.942 | 2564.5982 | -2272.8 | 67222.2929 | 25176.475 | 13.216 | 65.3754 | 64078.2 | 44318.6179 | 3984.0929 | 840 |  | 10.4069