## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 220 | 90 | 310 | 0 | 0 | 4 | 310 | 110 | 4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.5 | 8000 | 42.127 | 3951.09 | -480 | 3127.1489 | 3038 | 9.8 | 88.108 | 2671.8 | 569.1489 | 455.3489 | 0 |  | 35.162 | 3038
2 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 55 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.4 | 7760 | 41.079 | 2724.93 | -240 | 883.5 | 1123.5 | 10.7 | 80.8874 | 912.5 | 0 | 71 | 100 |  | 13.0035 | 1123.5
3 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 54 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.45 | 7880 | 40.75 | 2340 | 120 | 809.5 | 689.5 | 9.85 | 87.764 | 788.4 | 0 | 81.1 | 60 |  | 7.9803 | 689.5
4 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 54 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 83.6 | 5840 | 40.502 | 2049.84 | -2040 | 2569.7128 | 689.5 | 9.85 | 89.5573 | 2438.2 | 3920.2128 | 131.5128 | 0 |  | 7.9803 | 689.5
5 | 80 | 0 | 80 | 0 | 0 | 6 | 80 | 55 | 1.7 | 0 | 0 | 0 | 0 | 0 | 16.45 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 5 | 84 | 6800 | 40.518 | 2068.56 | 960 | 1748 | 788 | 9.85 | 88.7044 | 1554.9 | 0 | 193.1 | 0 |  | 9.1204 | 788
6 | 175 | 0 | 175 | 0 | 0 | 4 | 175 | 54 | 3.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 6 | 84.4 | 7760 | 41.086 | 2733.12 | 960 | 2683.75 | 1723.75 | 9.85 | 87.8675 | 2489.3 | 0 | 194.45 | 0 |  | 19.9508 | 1723.75
7 | 290 | 0 | 290 | 0 | 0 | 4 | 290 | 55 | 5.4 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 7 | 84.6 | 8240 | 41.6 | 3334.5 | 480 | 3380 | 2900 | 10 | 86.1432 | 3248.5 | 0 | 131.5 | 0 |  | 33.5648 | 2900
8 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 55 | 3.6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 8 | 84.7 | 8480 | 41.497 | 3213.99 | 240 | 2053 | 1813 | 9.8 | 87.6954 | 1693.6 | 0 | 359.4 | 0 |  | 20.9838 | 1813
9 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 9 | 84.85 | 8840 | 41.821 | 3593.07 | 360 | 2133 | 1773 | 9.85 | 86.9448 | 2044 | 0 | 89 | 0 |  | 20.5208 | 1773
10 | 265 | 0 | 265 | 0 | 0 | 4 | 265 | 55 | 5.1 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 10 | 84.8 | 8720 | 41.852 | 3629.34 | -120 | 2490.25 | 2610.25 | 9.85 | 87.0463 | 2336 | 0 | 154.25 | 0 |  | 30.2112 | 2610.25
11 | 90 | 0 | 90 | 0 | 0 | 3 | 90 | 40 | 2.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 11 | 84.8 | 8720 | 40.953 | 2577.51 | 0 | 967.5 | 967.5 | 10.75 | 79.7587 | 584 | 0 | 383.5 | 0 |  | 11.1979 | 967.5
12 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 40 | 4.6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 12 | 84.8 | 8720 | 41.597 | 3330.99 | 0 | 2142 | 2142 | 10.2 | 84.0595 | 1898 | 0 | 244 | 0 |  | 24.7917 | 2142
13 | 150 | 0 | 150 | 0 | 0 | 4 | 150 | 55 | 3.2 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 13 | 85 | 9200 | 40.912 | 2529.54 | 480 | 2017.5 | 1537.5 | 10.25 | 83.2604 | 1609.65 | 0 | 407.85 | 0 |  | 17.7951 | 1537.5
14 | 185 | 0 | 185 | 0 | 0 | 2 | 185 | 55 | 3.6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 14 | 84.8 | 8720 | 41.111 | 2762.37 | -480 | 1407 | 1887 | 10.2 | 84.0595 | 1197.2 | 0 | 209.8 | 0 |  | 21.8403 | 1887
15 | 190 | 0 | 190 | 0 | 0 | 3 | 190 | 54 | 4.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 15 | 84.75 | 8600 | 41.29 | 2971.8 | -120 | 1799 | 1919 | 10.1 | 84.991 | 1560 | 0 | 239 | 0 |  | 22.2106 | 1919
16 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 54 | 4.3 | 0 | 0 | 0 | 0 | 0 | 20.5 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 16 | 84.65 | 8360 | 41.477 | 3190.59 | -240 | 2017.5 | 2257.5 | 10.5 | 81.945 | 1695 | 0 | 322.5 | 0 |  | 26.1285 | 2257.5
17 | 75 | 170 | 245 | 0 | 0 | 4 | 245 | 108 | 1.5 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.4 | 7760 | 41.702 | 3453.84 | -600 | 1972.5 | 2572.5 | 10.5 | 82.4281 | 1687.5 | 0 | 285 | 0 |  | 29.7743 | 2572.5
18 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 54 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.6 | 8240 | 41.583 | 3314.61 | 480 | 2480 | 2000 | 10 | 86.1432 | 2347.5 | 0 | 132.5 | 0 |  | 23.1481 | 2000
19 | 0 | 220 | 220 | 0 | 0 | 4 | 220 | 54 | 0 | 4.2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 19 | 84.7 | 8480 | 41.755 | 3515.85 | 240 | 2561 | 2321 | 10.55 | 81.4611 | 2255.7 | 0 | 305.3 | 0 |  | 26.8634 | 2321
20 | 0 | 240 | 240 | 0 | 0 | 4 | 240 | 54 | 0 | 5.3 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 20 | 84.85 | 8840 | 41.948 | 3741.66 | 360 | 2844 | 2484 | 10.35 | 82.7445 | 2416.3 | 0 | 427.7 | 0 |  | 28.75 | 2484
21 | 0 | 280 | 280 | 0 | 0 | 3 | 280 | 40 | 0 | 6.2 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 21 | 84.85 | 8840 | 41.97 | 3767.4 | 0 | 2954 | 2954 | 10.55 | 81.1759 | 2649.9 | 0 | 304.1 | 0 |  | 34.1898 | 2954
22 | 0 | 370 | 370 | 0 | 0 | 3 | 370 | 53 | 0 | 8.3 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 22 | 84.6 | 8240 | 41.887 | 3670.29 | -600 | 3192.5 | 3792.5 | 10.25 | 84.0421 | 3021.75 | 0 | 170.75 | 0 |  | 43.8947 | 3792.5
23 | 0 | 325 | 325 | 0 | 0 | 3 | 325 | 53 | 0 | 6.5 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 23 | 84.65 | 8360 | 41.637 | 3377.79 | 120 | 3516.25 | 3396.25 | 10.45 | 82.337 | 3217.5 | 0 | 298.75 | 0 |  | 39.3084 | 3396.25
24 | 0 | 365 | 365 | 0 | 0 | 4 | 365 | 54 | 0 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 24 | 84.9 | 8960 | 42.002 | 3804.84 | 600 | 4286.5 | 3686.5 | 10.1 | 84.6939 | 3876.3 | 0 | 410.2 | 0 |  | 42.6678 | 3686.5
25 | 0 | 305 | 305 | 0 | 0 | 0 | 305 | 49 | 0 | 7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 25 | 85.2 | 9680 | 41.738 | 3495.96 | 720 | 3876.75 | 3156.75 | 10.35 | 82.0742 | 3810.6 | 0 | 66.15 | 0 |  | 36.5365 | 3156.75
26 | 0 | 350 | 350 | 0 | 0 | 5 | 350 | 55 | 0 | 6.9 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 26 | 85.4 | 10160 | 41.4544 | 3164.148 | 480 | 3910 | 3430 | 9.8 | 86.2809 | 3592.5 | 0 | 317.5 | 0 |  | 39.6991 | 3430
27 | 0 | 355 | 355 | 0 | 0 | 5 | 355 | 55 | 0 | 8.05 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 27 | 85 | 9200 | 41.87 | 3650.4 | -960 | 2465.75 | 3425.75 | 9.65 | 88.4372 | 2279.7 | 0 | 186.05 | 0 |  | 39.6499 | 3425.75
28 | 0 | 355 | 355 | 0 | 0 | 3 | 355 | 44 | 0 | 8.55 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 28 | 84.9 | 8960 | 42.03 | 3837.6 | -240 | 3444.9 | 3684.9 | 10.38 | 82.4092 | 3175.2 | 0 | 269.7 | 0 |  | 42.6493 | 3684.9
29 | 0 | 380 | 380 | 0 | 0 | 3 | 380 | 55 | 0 | 8.6 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 29 | 84.95 | 9080 | 42.08 | 3896.1 | 120 | 5622.9746 | 3838 | 10.1 | 84.5953 | 5241.4 | 1664.9746 | 381.5746 | 0 |  | 44.4213 | 3838
30 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 55 | 0 | 8.9 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 30 | 84.8 | 8720 | 41.997 | 3798.99 | -360 | 3987 | 4347 | 10.35 | 82.8412 | 3788.7 | 0 | 198.3 | 0 |  | 50.3125 | 4347
31 | 0 | 250 | 250 | 0 | 0 | 3 | 250 | 45 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 31 | 84.85 | 8840 | 42.004 | 3807.18 | 120 | 2557.5 | 2437.5 | 9.75 | 87.8365 | 2212.35 | 0 | 345.15 | 0 |  | 28.2118 | 2437.5
| 2885 | 4545 | 7430 | 0 | 0 | 110 | 7320 | 110 | 59.9 | 98.9 | 273.5 | 0 | 0 | 0 | 276.95 | 0 | 0 | 0 | 17 | 22 |  |  | 84.7016 | 8483.871 | 41.5429 | 3267.6741 | 360 | 81899.9863 | 75385.65 | 10.1461 | 84.7006 | 74293.95 | 6154.3363 | 7766.0363 | 160 |  | 28.1458 | 75385.65