## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 225 | 0 | 225 | 0 | 0 | 4 | 225 | 40 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.9 | 8960 | 41.7 | 3451.5 | 120 | 2448.75 | 2328.75 | 10.35 | 82.6481 | 2263 | 0 | 185.75 | 0 |  | 26.9531 | 2328.75
2 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 55 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.35 | 7640 | 41.849 | 3625.83 | -1320 | 2103.7 | 3423.7 | 10.22 | 84.7864 | 2138.85 | 0 | 24.85 | 60 |  | 39.6262 | 3423.7
3 | 260 | 0 | 260 | 0 | 0 | 4 | 260 | 55 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.45 | 7880 | 41.428 | 3133.26 | 240 | 2931 | 2691 | 10.35 | 83.5242 | 2642.6 | 0 | 288.4 | 0 |  | 31.1458 | 2691
4 | 30 | 355 | 385 | 0 | 0 | 5 | 385 | 104 | 0.55 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.1 | 7040 | 41.761 | 3522.87 | -840 | 4803.8191 | 3888.5 | 10.1 | 86.3032 | 4730.4 | 1755.3191 | 133.4191 | 60 |  | 45.0058 | 3888.5
5 | 370 | 0 | 370 | 0 | 0 | 5 | 370 | 50 | 8.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.35 | 7640 | 41.77 | 3533.4 | 600 | 4429.5 | 3829.5 | 10.35 | 83.7215 | 4033 | 0 | 396.5 | 0 |  | 44.3229 | 3829.5
6 | 380 | 0 | 380 | 0 | 0 | 3 | 380 | 55 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.5 | 8000 | 41.88 | 3662.1 | 360 | 4198 | 3838 | 10.1 | 85.491 | 4164.55 | 0 | 33.45 | 0 |  | 44.4213 | 3838
7 | 350 | 0 | 350 | 0 | 0 | 3 | 350 | 55 | 7.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.1 | 9440 | 41.84 | 3615.3 | 1440 | 5027.5 | 3587.5 | 10.25 | 83.0672 | 4817.4 | 0 | 210.1 | 0 |  | 41.522 | 3587.5
8 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 45 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.95 | 9080 | 42.008 | 3811.86 | -360 | 3781 | 4141 | 10.1 | 84.5953 | 3587.2 | 0 | 193.8 | 0 |  | 47.9282 | 4141
9 | 435 | 0 | 435 | 0 | 0 | 3 | 435 | 55 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.95 | 9080 | 42.12 | 3942.9 | 0 | 4284.75 | 4284.75 | 9.85 | 86.7423 | 3912.8 | 0 | 371.95 | 0 |  | 49.592 | 4284.75
10 | 0 | 435 | 435 | 0 | 0 | 3 | 435 | 55 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.9 | 8960 | 42.061 | 3873.87 | -120 | 4360.5 | 4480.5 | 10.3 | 83.0493 | 4124.5 | 0 | 236 | 0 |  | 51.8576 | 4480.5
11 | 0 | 420 | 420 | 0 | 0 | 3 | 420 | 55 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 85.1 | 9440 | 42.079 | 3894.93 | 480 | 4680 | 4200 | 10 | 85.1439 | 4373.25 | 0 | 306.75 | 0 |  | 48.6111 | 4200
12 | 420 | 40 | 460 | 0 | 0 | 4 | 460 | 55 | 8.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.9 | 8960 | 41.982 | 3781.44 | -480 | 4166 | 4646 | 10.1 | 84.6939 | 4040.4 | 0 | 125.6 | 0 |  | 53.7731 | 4646
13 | 445 | 0 | 445 | 0 | 0 | 4 | 445 | 54 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85 | 9200 | 41.7 | 3451.5 | 240 | 4578.75 | 4338.75 | 9.75 | 87.5301 | 4277.8 | 0 | 300.95 | 0 |  | 50.217 | 4338.75
14 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 55 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 85.15 | 9560 | 41.68 | 3428.1 | 360 | 4385.5 | 4025.5 | 9.7 | 87.6755 | 4139.1 | 0 | 246.4 | 0 |  | 46.5914 | 4025.5
15 | 390 | 0 | 390 | 0 | 0 | 4 | 390 | 54 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.9 | 8960 | 42.101 | 3920.67 | -600 | 3436.5 | 4036.5 | 10.35 | 82.6481 | 3219.3 | 0 | 217.2 | 0 |  | 46.7188 | 4036.5
16 | 400 | 0 | 400 | 0 | 0 | 3 | 400 | 45 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 85 | 9200 | 41.066 | 2709.72 | 240 | 4120 | 3880 | 9.7 | 87.9813 | 3877.5 | 0 | 242.5 | 0 |  | 44.9074 | 3880
17 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 55 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.6 | 8240 | 41.881 | 3663.27 | -960 | 3742.5 | 4702.5 | 10.45 | 82.4337 | 3489.4 | 0 | 253.1 | 0 |  | 54.4271 | 4702.5
18 | 0 | 410 | 410 | 0 | 0 | 3 | 410 | 45 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.8 | 8720 | 41.92 | 3708.9 | 480 | 4559.5 | 4079.5 | 9.95 | 86.1715 | 4423.8 | 0 | 135.7 | 0 |  | 47.2164 | 4079.5
19 | 420 | 0 | 420 | 0 | 0 | 3 | 420 | 54 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.3 | 7520 | 41.87 | 3650.4 | -1200 | 3021 | 4221 | 10.05 | 86.3225 | 2767.5 | 0 | 253.5 | 0 |  | 48.8542 | 4221
20 | 410 | 0 | 410 | 0 | 0 | 3 | 410 | 54 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.4 | 7760 | 41.749 | 3508.83 | 240 | 4463 | 4223 | 10.3 | 84.0287 | 4285.1 | 0 | 237.9 | 60 |  | 48.8773 | 4223
21 | 485 | 0 | 485 | 0 | 0 | 5 | 485 | 54 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 42.083 | 3899.61 | -240 | 4610 | 4850 | 10 | 86.7541 | 4474.9 | 0 | 135.1 | 0 |  | 56.1343 | 4850
22 | 435 | 0 | 435 | 0 | 0 | 4 | 435 | 53 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.45 | 7880 | 42.1175 | 3939.975 | 360 | 4710 | 4350 | 10 | 86.4476 | 4431.1 | 0 | 278.9 | 0 |  | 50.3472 | 4350
23 | 440 | 0 | 440 | 0 | 0 | 4 | 440 | 44 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.5 | 8000 | 42.062 | 3875.04 | 120 | 4564 | 4444 | 10.1 | 85.491 | 4504.1 | 0 | 59.9 | 0 |  | 51.4352 | 4444
24 | 515 | 40 | 555 | 0 | 0 | 4 | 555 | 107 | 10.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 24 | 84.6 | 8240 | 41.901 | 3686.67 | 240 | 5845.5 | 5605.5 | 10.1 | 85.2903 | 5655 | 0 | 190.5 | 0 |  | 64.8785 | 5605.5
25 | 525 | 0 | 525 | 0 | 0 | 3 | 525 | 53 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84 | 6800 | 41.749 | 3508.83 | -1440 | 3862.5 | 5302.5 | 10.1 | 86.5087 | 3956.6 | 0 | 25.9 | 120 |  | 61.3715 | 5302.5
26 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 53 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84 | 6800 | 41.978 | 3776.76 | 0 | 5252 | 5252 | 10.1 | 86.5087 | 5219.5 | 0 | 132.5 | 100 |  | 60.787 | 5252
27 | 515 | 0 | 515 | 0 | 0 | 3 | 515 | 54 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84 | 6800 | 41.941 | 3733.47 | 0 | 5201.5 | 5201.5 | 10.1 | 86.5087 | 5161.1 | 0 | 40.4 | 0 |  | 60.2025 | 5201.5
28 | 470 | 0 | 470 | 0 | 0 | 4 | 470 | 54 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.6 | 8240 | 41.602 | 3336.84 | 1440 | 6187 | 4747 | 10.1 | 85.2903 | 6051.7 | 0 | 135.3 | 0 |  | 54.9421 | 4747
29 | 560 | 0 | 560 | 0 | 0 | 4 | 560 | 44 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.4 | 7760 | 41.871 | 3651.57 | -480 | 5064 | 5544 | 9.9 | 87.4238 | 4961.25 | 0 | 102.75 | 0 |  | 64.1667 | 5544
30 | 250 | 285 | 535 | 0 | 0 | 5 | 535 | 53 | 5.1 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.65 | 8360 | 41.961 | 3756.87 | 600 | 5950 | 5350 | 10 | 86.0422 | 5731.55 | 0 | 218.45 | 0 |  | 61.9213 | 5350
| 10005 | 2840 | 12845 | 0 | 0 | 112 | 12733 | 107 | 213.8 | 61.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 14 |  |  | 84.6067 | 8256 | 41.857 | 3635.2095 | -480 | 130767.7691 | 129492.45 | 10.0812 | 85.4363 | 125454.25 | 1755.3191 | 5713.5191 | 400 |  | 49.9585 | 129492.45