## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 45 | 650 | 695 | 0 | 0 | 4 | 695 | 90 | 1.3 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.9 | 8960 | 41.95 | 3744 | -480 | 6539.5 | 7019.5 | 10.1 | 84.6939 | 6483.56 | 0 | 115.94 | 60 |  | 81.2442 | 7019.5
2 | 0 | 660 | 660 | 0 | 0 | 4 | 660 | 50 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.7 | 8480 | 41.93 | 3720.6 | -480 | 6186 | 6666 | 10.1 | 85.0905 | 5982.9 | 0 | 203.1 | 0 |  | 77.1528 | 6666
3 | 0 | 710 | 710 | 0 | 0 | 4 | 710 | 54 | 0 | 14.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 3 | 84.5 | 8000 | 42.08 | 3896.1 | -480 | 6691 | 7171 | 10.1 | 85.491 | 6657.6 | 0 | 63.4 | 30 |  | 82.9977 | 7171
4 | 730 | 30 | 760 | 0 | 0 | 3 | 760 | 55 | 13.6 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.55 | 8120 | 42.12 | 3942.9 | 120 | 7796 | 7676 | 10.1 | 85.3905 | 7634.76 | 0 | 161.24 | 0 |  | 88.8426 | 7676
5 | 380 | 315 | 695 | 0 | 0 | 3 | 695 | 50 | 7.5 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.5 | 8000 | 42 | 3802.5 | -120 | 6899.5 | 7019.5 | 10.1 | 85.491 | 6767.1 | 0 | 132.4 | 0 |  | 81.2442 | 7019.5
6 | 365 | 260 | 625 | 0 | 0 | 4 | 625 | 50 | 7.3 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84 | 6800 | 41.65 | 3393 | -1200 | 5050 | 6250 | 10 | 87.3738 | 4898.3 | 0 | 151.7 | 0 |  | 72.338 | 6250
7 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 55 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 84 | 6800 | 42 | 3802.5 | 0 | 6767 | 6767 | 10.1 | 86.5087 | 6811.2 | 0 | 15.8 | 60 |  | 78.3218 | 6767
8 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 50 | 0 | 14.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.7 | 8480 | 42.05 | 3861 | 1680 | 8447 | 6767 | 10.1 | 85.0905 | 8312.85 | 0 | 134.15 | 0 |  | 78.3218 | 6767
9 | 0 | 545 | 545 | 0 | 0 | 4 | 545 | 50 | 0 | 10.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 83.7 | 6080 | 41.751 | 3511.17 | -2400 | 4314.1774 | 5504.5 | 10.1 | 87.1311 | 4224.5 | 1209.6774 | 149.6774 | 60 |  | 63.7095 | 5504.5
10 | 0 | 540 | 540 | 0 | 0 | 3 | 540 | 50 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.8 | 6320 | 41.849 | 3625.83 | 240 | 5694 | 5454 | 10.1 | 86.9226 | 5613.7 | 0 | 140.3 | 60 |  | 63.125 | 5454
11 | 590 | 0 | 590 | 0 | 0 | 4 | 590 | 55 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 83.65 | 5960 | 42.101 | 3920.67 | -360 | 5599 | 5959 | 10.1 | 87.2357 | 5482.3 | 0 | 116.7 | 0 |  | 68.9699 | 5959
12 | 400 | 260 | 660 | 0 | 0 | 4 | 660 | 50 | 8.1 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.9 | 8960 | 41.802 | 3570.84 | 3000 | 9699 | 6699 | 10.15 | 84.2766 | 9627.6 | 0 | 71.4 | 0 |  | 77.5347 | 6699
13 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 53 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.85 | 8840 | 42 | 3802.5 | -120 | 6200.75 | 6320.75 | 9.65 | 88.7467 | 6150.85 | 0 | 49.9 | 0 |  | 73.1568 | 6320.75
14 | 630 | 0 | 630 | 0 | 0 | 4 | 630 | 54 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.95 | 9080 | 41.7 | 3451.5 | 240 | 6414 | 6174 | 9.8 | 87.1849 | 6399.55 | 0 | 14.45 | 0 |  | 71.4583 | 6174
15 | 0 | 625 | 625 | 0 | 0 | 3 | 625 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.5 | 8000 | 41.63 | 3369.6 | -1080 | 5232.5 | 6312.5 | 10.1 | 85.491 | 5212.2 | 0 | 80.3 | 60 |  | 73.0613 | 6312.5
16 | 540 | 135 | 675 | 0 | 0 | 5 | 675 | 107 | 10.8 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.6 | 8240 | 41.781 | 3546.27 | 240 | 6821.25 | 6581.25 | 9.75 | 88.352 | 6555.4 | 0 | 265.85 | 0 |  | 76.1719 | 6581.25
17 | 0 | 530 | 530 | 0 | 0 | 4 | 530 | 49 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 85.1 | 9440 | 41.26 | 2936.7 | 1200 | 6314.5 | 5114.5 | 9.65 | 88.232 | 5913 | 0 | 401.5 | 0 |  | 59.1956 | 5114.5
18 | 335 | 255 | 590 | 0 | 0 | 4 | 590 | 49 | 7.2 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 85.2 | 9680 | 41.2 | 2866.5 | 240 | 6199 | 5959 | 10.1 | 84.1057 | 6000.6 | 0 | 198.4 | 0 |  | 68.9699 | 5959
19 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 49 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 85.1 | 9440 | 41.41 | 3112.2 | -240 | 5919.5 | 6159.5 | 9.7 | 87.7772 | 5854.6 | 0 | 64.9 | 0 |  | 71.2905 | 6159.5
20 | 0 | 655 | 655 | 0 | 0 | 4 | 655 | 50 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.95 | 9080 | 41.829 | 3602.43 | -360 | 6059 | 6419 | 9.8 | 87.1849 | 5855.85 | 0 | 203.15 | 0 |  | 74.294 | 6419
21 | 0 | 630 | 630 | 0 | 0 | 4 | 630 | 53 | 0 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.95 | 9080 | 42.078 | 3893.76 | 0 | 6205.5 | 6205.5 | 9.85 | 86.7423 | 6044.4 | 0 | 161.1 | 0 |  | 71.8229 | 6205.5
22 | 0 | 655 | 655 | 0 | 0 | 4 | 655 | 55 | 0 | 12.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85 | 9200 | 42.071 | 3885.57 | 120 | 6506.25 | 6386.25 | 9.75 | 87.5301 | 6379.8 | 0 | 186.45 | 60 |  | 73.9149 | 6386.25
23 | 260 | 380 | 640 | 0 | 0 | 4 | 640 | 55 | 5 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.6 | 8240 | 41.705 | 3457.35 | -960 | 5376 | 6336 | 9.9 | 87.0133 | 5140.25 | 0 | 235.75 | 0 |  | 73.3333 | 6336
24 | 290 | 355 | 645 | 0 | 0 | 3 | 645 | 53 | 5.3 | 7.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 1 | 1 | Ασυμφωνία θέσεως πόλων Δ/Κ Ρ25 Μον. ΝοΙΙ | 24 | 84.3 | 7520 | 41.979 | 3777.93 | -720 | 5794.5 | 6514.5 | 10.1 | 85.8952 | 5745.1 | 0 | 49.4 | 0 |  | 75.3993 | 6514.5
25 | 645 | 0 | 645 | 0 | 0 | 4 | 645 | 55 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.55 | 2 | 0 | Ασυμφωνία θέσεως πόλων Δ/Κ Ρ25 Μον. ΝοΙΙ | 25 | 84.6 | 8240 | 42.051 | 3862.17 | 720 | 7008.75 | 6288.75 | 9.75 | 88.352 | 6921.05 | 0 | 147.7 | 60 |  | 72.7865 | 6288.75
26 | 20 | 645 | 665 | 0 | 0 | 3 | 665 | 53 | 0.3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.3 | 7520 | 41.951 | 3745.17 | -720 | 6222.25 | 6942.25 | 10.4395 | 83.102 | 6156.15 | 0 | 66.1 | 0 |  | 80.3501 | 6942.25
27 | 285 | 305 | 590 | 0 | 0 | 3 | 590 | 53 | 5.6 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.7 | 8480 | 41.839 | 3614.13 | 960 | 6653.5 | 5693.5 | 9.65 | 89.0585 | 6421.1 | 0 | 232.4 | 0 |  | 65.897 | 5693.5
28 | 345 | 245 | 590 | 0 | 0 | 3 | 590 | 53 | 6.6 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.4 | 7760 | 41.811 | 3581.37 | -720 | 5091.5 | 5811.5 | 9.85 | 87.8675 | 4783.35 | 0 | 308.15 | 0 |  | 67.2627 | 5811.5
29 | 0 | 595 | 595 | 0 | 0 | 3 | 595 | 50 | 0 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.55 | 8120 | 41.941 | 3733.47 | 360 | 6191 | 5831 | 9.8 | 88.0045 | 6117.4 | 0 | 73.6 | 0 |  | 67.4884 | 5831
30 | 0 | 490 | 490 | 0 | 0 | 5 | 490 | 50 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.5 | 8000 | 41.74 | 3498.3 | -120 | 4829 | 4949 | 10.1 | 85.491 | 4870.32 | 0 | 18.68 | 60 |  | 57.2801 | 4949
31 | 0 | 475 | 475 | 0 | 0 | 6 | 475 | 50 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.85 | 8840 | 41.468 | 3180.06 | 840 | 5471.25 | 4631.25 | 9.75 | 87.8365 | 5270.6 | 0 | 200.65 | 0 |  | 53.6024 | 4631.25
| 6515 | 12920 | 19435 | 0 | 0 | 117 | 19318 | 107 | 128.7 | 263.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.75 | 23 | 41 |  |  | 84.5774 | 8185.8065 | 41.8299 | 3603.4868 | -600 | 194192.1774 | 193582.5 | 9.9605 | 86.5306 | 190287.94 | 1209.6774 | 4414.2374 | 510 |  | 72.2754 | 193582.5