## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 54 | 0 | 1.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 84.6 | 8240 | 41.15 | 2808 | -960 | 3341.883 | 695.5 | 10.7 | 80.5077 | 3164 | 3606.383 | 237.883 | 60 |  | 8.0498 | 695.5
2 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 83.95 | 6680 | 41.048 | 2688.66 | -1560 | 2164.3617 | 735 | 10.5 | 83.3123 | 1971 | 2989.3617 | 253.3617 | 60 |  | 8.5069 | 735
3 | 60 | 0 | 60 | 0 | 0 | 3 | 60 | 35 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.1 | 7040 | 40.71 | 2293.2 | 360 | 939 | 579 | 9.65 | 90.3277 | 938 | 0 | 61 | 60 |  | 6.7014 | 579
4 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85.2 | 9680 | 40.77 | 2363.4 | 2640 | 3549 | 909 | 10.1 | 84.1057 | 3124.4 | 0 | 484.6 | 60 |  | 10.5208 | 909
5 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 55 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5 | 84.8 | 8720 | 40.7685 | 2361.645 | -960 | 1912.6064 | 787.5 | 10.5 | 81.6578 | 1827 | 2085.1064 | 145.6064 | 60 |  | 9.1146 | 787.5
6 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.55 | 8120 | 40.8 | 2398.5 | -600 | 3573.5026 | 702 | 10.8 | 79.8559 | 3430 | 3471.5026 | 203.5026 | 60 |  | 8.125 | 702
7 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 84.2 | 7280 | 40.7 | 2281.5 | -840 | 2225.4787 | 682.5 | 10.5 | 82.8188 | 2117 | 2382.9787 | 168.4787 | 60 |  | 7.8993 | 682.5
8 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 54 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 85.2 | 9680 | 40.67 | 2246.4 | 2400 | 4777.25 | 627.25 | 9.65 | 88.0277 | 4693.9 | 1750 | 143.35 | 60 |  | 7.2598 | 627.25
9 | 0 | 195 | 195 | 0 | 0 | 5 | 195 | 54 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 85.1 | 9440 | 41.45 | 3159 | -240 | 3418.3457 | 1881.75 | 9.65 | 88.232 | 3058.7 | 1776.5957 | 419.6457 | 60 |  | 21.7795 | 1881.75
10 | 180 | 0 | 180 | 0 | 0 | 2 | 180 | 54 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 85.2 | 9680 | 41.1895 | 2854.215 | 240 | 5589.1064 | 1764 | 9.8 | 86.6804 | 5248.7 | 3585.1064 | 340.4064 | 0 |  | 20.4167 | 1764
11 | 0 | 110 | 110 | 0 | 0 | 4 | 110 | 40 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 11 | 85.05 | 9320 | 41.013 | 2647.71 | -360 | 4284.9043 | 1171.5 | 10.65 | 80.0401 | 4219.4 | 3473.4043 | 65.5043 | 0 |  | 13.559 | 1171.5
12 | 205 | 80 | 285 | 0 | 0 | 4 | 285 | 110 | 3.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.7 | 8480 | 41.1 | 2749.5 | -840 | 3304.6543 | 2921.25 | 10.25 | 83.8453 | 3343.4 | 1223.4043 | 21.2543 | 60 |  | 33.8108 | 2921.25
13 | 0 | 190 | 190 | 0 | 0 | 4 | 190 | 54 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 85 | 9200 | 41.062 | 2705.04 | 720 | 3843.9583 | 1900 | 10 | 85.3419 | 3555 | 1223.9583 | 288.9583 | 0 |  | 21.9907 | 1900
14 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 40 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.7 | 8480 | 40.83 | 2433.6 | -720 | 1455.0962 | 1021.25 | 10.75 | 79.9455 | 1468.8 | 1153.8462 | 11.2962 | 25 |  | 11.82 | 1021.25
15 | 170 | 375 | 545 | 0 | 0 | 4 | 545 | 109 | 3.6 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 15 | 85.2 | 9680 | 41.429 | 3134.43 | 1200 | 8429.8886 | 5504.5 | 10.1 | 84.1057 | 8343.9 | 1725.3886 | 85.9886 | 0 |  | 63.7095 | 5504.5
16 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 54 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 85 | 9200 | 41.35 | 3042 | -480 | 5260.6489 | 2171.5 | 10.1 | 84.4969 | 5005.5 | 3569.1489 | 315.1489 | 60 |  | 25.1331 | 2171.5
17 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 54 | 2.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85.2 | 9680 | 40.95 | 2574 | 480 | 4776.3731 | 1400 | 10 | 84.9468 | 4650.1 | 2896.3731 | 126.2731 | 0 |  | 16.2037 | 1400
18 | 0 | 135 | 135 | 0 | 0 | 4 | 135 | 46 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.85 | 8840 | 41.159 | 2818.53 | -840 | 2842.6489 | 1363.5 | 10.1 | 84.7927 | 2766.7 | 2319.1489 | 75.9489 | 0 |  | 15.7812 | 1363.5
19 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.9 | 8960 | 40.7557 | 2346.669 | 120 | 4348.2766 | 707 | 10.1 | 84.6939 | 4051.5 | 3521.2766 | 296.7766 | 0 |  | 8.1829 | 707
20 | 165 | 85 | 250 | 0 | 0 | 4 | 250 | 80 | 4.3 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 20 | 84.95 | 9080 | 41.701 | 3452.67 | 120 | 5533.2979 | 2525 | 10.1 | 84.5953 | 5453.1 | 2888.2979 | 80.1979 | 0 |  | 29.2245 | 2525
21 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 55 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 85.2 | 9680 | 41.639 | 3380.13 | 600 | 5040.1489 | 2121 | 10.1 | 84.1057 | 4971.3 | 2319.1489 | 68.8489 | 0 |  | 24.5486 | 2121
22 | 185 | 115 | 300 | 0 | 0 | 4 | 300 | 55 | 3.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 85.2 | 9680 | 41.82 | 3591.9 | 0 | 6541.0638 | 2940 | 9.8 | 86.6804 | 6445.9 | 3601.0638 | 95.1638 | 0 |  | 34.0278 | 2940
23 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 53 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 84.6 | 8240 | 41.53 | 3252.6 | -1440 | 5772.1596 | 3584.5 | 10.7 | 80.5077 | 5738.4 | 3627.6596 | 93.7596 | 60 |  | 41.4873 | 3584.5
24 | 0 | 430 | 430 | 0 | 0 | 4 | 430 | 55 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.3 | 7520 | 41.6 | 3334.5 | -720 | 7125.1634 | 4291.4 | 9.98 | 86.928 | 7119 | 3553.7634 | 66.1634 | 60 |  | 49.669 | 4291.4
25 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.6 | 8240 | 40.42 | 1953.9 | 720 | 3755.6554 | 745.5 | 10.65 | 80.8856 | 3591.6 | 2290.1554 | 164.0554 | 0 |  | 8.6285 | 745.5
26 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 54 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.8 | 8720 | 40.58 | 2141.1 | 480 | 4497.7713 | 1650.75 | 10.65 | 80.5077 | 4358.1 | 2367.0213 | 199.6713 | 60 |  | 19.1059 | 1650.75
27 | 0 | 110 | 110 | 0 | 0 | 4 | 110 | 54 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.7 | 8480 | 40.53 | 2082.6 | -240 | 3458.2766 | 1177 | 10.7 | 80.3191 | 3346.2 | 2521.2766 | 172.0766 | 60 |  | 13.6227 | 1177
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.9 | 8960 | 40.171 | 1662.57 | 480 | 2912.8462 | 679 | 9.7 | 88.1864 | 2876.2 | 1753.8462 | 96.6462 | 60 |  | 7.8588 | 679
29 | 200 | 200 | 400 | 0 | 0 | 4 | 400 | 110 | 4.75 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.95 | 9080 | 41.78 | 3545.1 | 120 | 4020 | 3900 | 9.75 | 87.632 | 3993.95 | 0 | 86.05 | 60 |  | 45.1389 | 3900
30 | 250 | 0 | 250 | 0 | 0 | 4 | 250 | 54 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.8 | 8720 | 41.67 | 3416.4 | -360 | 3933.4211 | 2525 | 10.1 | 84.8917 | 3841.1 | 1768.4211 | 152.3211 | 60 |  | 29.2245 | 2525
| 2410 | 2885 | 5295 | 0 | 0 | 117 | 5178 | 110 | 51.8 | 64.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 23 |  |  | 84.8167 | 8760 | 41.0782 | 2723.9823 | -480 | 122626.7878 | 53663.15 | 10.1347 | 84.5683 | 118711.85 | 69443.6378 | 5019.9378 | 1105 |  | 20.7034