## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.9 | 8960 | 41.047 | 2687.49 | 240 | 4623.0769 | 860 | 10.75 | 79.5728 | 4350.8 | 3523.0769 | 272.2769 | 0 |  | 9.9537 | 860
2 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.9 | 8960 | 40.7 | 2281.5 | 0 | 3687.4112 | 860 | 10.75 | 79.5728 | 3542.4 | 2827.4112 | 145.0112 | 0 |  | 9.9537 | 860
3 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 35 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 84.4 | 7760 | 40.85 | 2457 | -1200 | 2680.7181 | 806.25 | 10.75 | 80.5112 | 2664.5 | 3074.4681 | 76.2181 | 60 |  | 9.3316 | 806.25
4 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 54 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.8 | 8720 | 41.247 | 2921.49 | 960 | 5048.6073 | 1764 | 9.8 | 87.4905 | 4811.95 | 2324.6073 | 236.6573 | 0 |  | 20.4167 | 1764
5 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 54 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85 | 9200 | 40.7 | 2281.5 | 480 | 3607.4935 | 806.25 | 10.75 | 79.3878 | 3445.6 | 2321.2435 | 221.8935 | 60 |  | 9.3316 | 806.25
6 | 280 | 0 | 280 | 0 | 0 | 4 | 280 | 54 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 85 | 9200 | 42.071 | 3885.57 | 0 | 5584.9223 | 2730 | 9.75 | 87.5301 | 5305.3 | 2854.9223 | 339.6223 | 60 |  | 31.5972 | 2730
7 | 105 | 0 | 105 | 0 | 0 | 4 | 105 | 35 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.75 | 8600 | 40.85 | 2457 | -600 | 2811.5638 | 1060.5 | 10.1 | 84.991 | 2530.25 | 2351.0638 | 341.3138 | 60 |  | 12.2743 | 1060.5
8 | 340 | 135 | 475 | 0 | 0 | 4 | 475 | 90 | 7.5 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 8 | 84.7 | 8480 | 41.45 | 3159 | -120 | 6359.5513 | 4797.5 | 10.1 | 85.0905 | 6124.7 | 1682.0513 | 234.8513 | 0 |  | 55.5266 | 4797.5
9 | 420 | 470 | 890 | 0 | 0 | 4 | 890 | 108 | 8.8 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.85 | 8840 | 40.78 | 2375.1 | 360 | 9349 | 8989 | 10.1 | 84.7927 | 8970 | 0 | 439 | 60 |  | 104.0394 | 8989
10 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 54 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.95 | 9080 | 40.701 | 2282.67 | 240 | 4426.766 | 1224 | 10.2 | 83.7659 | 4245.8 | 2962.766 | 240.966 | 60 |  | 14.1667 | 1224
11 | 280 | 50 | 330 | 0 | 0 | 4 | 330 | 70 | 6.5 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 85.1 | 9440 | 41.512 | 3231.54 | 360 | 6501.2085 | 3194.4 | 9.68 | 87.9585 | 6394.5 | 2946.8085 | 166.7085 | 60 |  | 36.9722 | 3194.4
12 | 0 | 295 | 295 | 0 | 0 | 4 | 295 | 55 | 0 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85 | 9200 | 40.9107 | 2528.019 | -240 | 6888.4362 | 2979.5 | 10.1 | 84.4969 | 6920.4 | 4148.9362 | 28.0362 | 60 |  | 34.485 | 2979.5
13 | 0 | 205 | 205 | 0 | 0 | 4 | 205 | 55 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 13 | 85.15 | 9560 | 40.5215 | 2072.655 | 360 | 5938.1489 | 2009 | 9.8 | 86.7808 | 5791.8 | 3569.1489 | 146.3489 | 0 |  | 23.2523 | 2009
14 | 280 | 90 | 370 | 0 | 0 | 5 | 370 | 108 | 6.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84.55 | 8120 | 41.4438 | 3151.746 | -1440 | 6647.1277 | 3885 | 10.5 | 82.1375 | 6682.5 | 4202.1277 | 24.6277 | 60 |  | 44.9653 | 3885
15 | 190 | 90 | 280 | 0 | 0 | 4 | 280 | 54 | 3.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.95 | 9080 | 40.0718 | 1546.506 | 960 | 3788 | 2828 | 10.1 | 84.5953 | 3685.2 | 0 | 162.8 | 60 |  | 32.7315 | 2828
16 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 54 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 85.1 | 9440 | 39.9987 | 1460.979 | 360 | 3721.0638 | 1010 | 10.1 | 84.3008 | 3569.7 | 2351.0638 | 211.3638 | 60 |  | 11.6898 | 1010
17 | 75 | 130 | 205 | 0 | 0 | 4 | 205 | 80 | 1.9 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.8 | 8720 | 40.583 | 2144.61 | -720 | 5697.0213 | 2050 | 10 | 85.7407 | 5457.6 | 4367.0213 | 269.4213 | 30 |  | 23.7269 | 2050
18 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 85 | 9200 | 40.019 | 1484.73 | 480 | 3075.7447 | 750 | 10 | 85.3419 | 2890.8 | 1845.7447 | 214.9447 | 30 |  | 8.6806 | 750
19 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 35 | 3.8 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | Εγκατάσταση Μετεο & Σταθμημέτρων από συνεργείο δυτών | 19 | 84.3 | 7520 | 40.551 | 2107.1583 | -1680 | 2132.9362 | 1414 | 10.1 | 85.8952 | 2073.2 | 2398.9362 | 119.7362 | 60 |  | 16.3657 | 1414
20 | 280 | 130 | 410 | 0 | 0 | 4 | 410 | 110 | 6.3 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 20 | 85.1 | 9440 | 41.35 | 3042 | 1920 | 6020 | 4100 | 10 | 85.1439 | 5621 | 0 | 399 | 0 |  | 47.4537 | 4100
21 | 0 | 85 | 85 | 0 | 0 | 3 | 85 | 55 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 21 | 84.9 | 8960 | 40.1482 | 1635.894 | -480 | 3419.2581 | 867 | 10.2 | 83.8635 | 3416 | 3032.2581 | 63.2581 | 60 |  | 10.0347 | 867
22 | 185 | 0 | 185 | 0 | 0 | 4 | 185 | 55 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.35 | 7640 | 39.981 | 1440.27 | -1320 | 2812.367 | 1988.75 | 10.75 | 80.6062 | 2529.6 | 2143.617 | 282.767 | 0 |  | 23.0179 | 1988.75
23 | 115 | 0 | 115 | 0 | 0 | 5 | 115 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.9 | 8960 | 40.65 | 2223 | 1320 | 4137.4423 | 1109.75 | 9.65 | 88.6433 | 3920.1 | 1707.6923 | 217.3423 | 0 |  | 12.8443 | 1109.75
24 | 190 | 0 | 190 | 0 | 0 | 5 | 190 | 35 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.9 | 8960 | 41.243 | 2916.81 | 0 | 3611.3077 | 1919 | 10.1 | 84.6939 | 3504 | 1692.3077 | 167.3077 | 60 |  | 22.2106 | 1919
25 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.2 | 9680 | 40.343 | 1863.81 | 720 | 5844.5258 | 707 | 10.1 | 84.1057 | 5847.3 | 4417.5258 | 57.2258 | 60 |  | 8.1829 | 707
26 | 175 | 0 | 175 | 0 | 0 | 4 | 175 | 35 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.9 | 8960 | 40.323 | 1840.41 | -720 | 2834.734 | 1767.5 | 10.1 | 84.6939 | 2701 | 1787.234 | 133.734 | 0 |  | 20.4572 | 1767.5
27 | 65 | 155 | 220 | 0 | 0 | 4 | 220 | 70 | 1.8 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 85.15 | 9560 | 41.02 | 2655.9 | 600 | 4561.7959 | 2222 | 10.1 | 84.2032 | 4569.8 | 1739.7959 | 11.9959 | 20 |  | 25.7176 | 2222
28 | 0 | 125 | 125 | 0 | 0 | 4 | 125 | 35 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.1 | 9440 | 40.63 | 2199.6 | -120 | 4039.1346 | 1343.75 | 10.75 | 79.2036 | 3934.7 | 2815.3846 | 104.4346 | 0 |  | 15.5527 | 1343.75
29 | 0 | 185 | 185 | 0 | 0 | 4 | 185 | 35 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 85 | 9200 | 41.65 | 3393 | -240 | 3352.8243 | 1868.5 | 10.1 | 84.4969 | 3150 | 1724.3243 | 262.8243 | 60 |  | 21.6262 | 1868.5
30 | 260 | 450 | 710 | 0 | 0 | 4 | 710 | 70 | 7.2 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 30 | 83.6 | 5840 | 41.35 | 3042 | -3360 | 7084.3617 | 7455 | 10.5 | 84.0133 | 7070.4 | 2989.3617 | 73.9617 | 60 |  | 86.2847 | 7455
31 | 125 | 90 | 215 | 0 | 0 | 4 | 215 | 70 | 3.3 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.45 | 7880 | 40.552 | 2108.34 | 2040 | 7361.3298 | 2257.5 | 10.5 | 82.331 | 7132.1 | 3063.8298 | 229.2298 | 0 |  | 26.1285 | 2257.5
| 4165 | 2880 | 7045 | 0 | 0 | 126 | 6919 | 110 | 99.4 | 71.6 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 31 | 20 |  |  | 84.8306 | 8793.5484 | 40.8144 | 2415.3967 | -840 | 147647.8789 | 71623.15 | 10.1665 | 84.2759 | 142853 | 76864.7289 | 5894.8789 | 1100 |  | 26.741 | 71623.15