## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 370 | 115 | 485 | 0 | 0 | 4 | 485 | 80 | 8.95 | 2.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.9 | 8960 | 41.598 | 3332.16 | 1080 | 8457.2234 | 4898.5 | 10.1 | 84.6939 | 8373.1 | 2478.7234 | 84.1234 | 0 |  | 56.6956 | 4898.5
2 | 170 | 265 | 435 | 0 | 0 | 5 | 435 | 95 | 4.05 | 5.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.2 | 7280 | 41.55 | 3276 | -1680 | 4266.6735 | 4263 | 9.8 | 88.7344 | 4139.1 | 1683.6735 | 127.5735 | 0 |  | 49.3403 | 4263
3 | 210 | 625 | 835 | 0 | 0 | 5 | 835 | 110 | 3.9 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 3 | 84.4 | 7760 | 41.461 | 3171.87 | 480 | 8788.25 | 8308.25 | 9.95 | 86.9845 | 8789.2 | 0 | 59.05 | 60 |  | 96.1603 | 8308.25
4 | 185 | 0 | 185 | 0 | 0 | 5 | 185 | 55 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 83.5 | 5600 | 39.998 | 1460.16 | -2160 | 898.6425 | 1988.75 | 10.75 | 82.2572 | 847 | 1069.8925 | 111.6425 | 60 |  | 23.0179 | 1988.75
5 | 0 | 245 | 245 | 0 | 0 | 4 | 245 | 54 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5 | 83.95 | 6680 | 40.15 | 1638 | 1080 | 3493.25 | 2413.25 | 9.85 | 88.8101 | 3486.1 | 0 | 67.15 | 60 |  | 27.9311 | 2413.25
6 | 40 | 580 | 620 | 0 | 0 | 4 | 620 | 104 | 0.9 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 84 | 6800 | 41.547 | 3272.49 | 120 | 6498 | 6378 | 10.2871 | 84.9353 | 6387.75 | 0 | 170.25 | 60 |  | 73.8194 | 6378
7 | 0 | 445 | 445 | 0 | 0 | 4 | 445 | 55 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 84.4 | 7760 | 41.248 | 2922.66 | 960 | 5276.5 | 4316.5 | 9.7 | 89.2263 | 4995 | 0 | 281.5 | 0 |  | 49.9595 | 4316.5
8 | 140 | 710 | 850 | 0 | 0 | 4 | 850 | 80 | 3.2 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.3 | 7520 | 41.8 | 3568.5 | -240 | 8345 | 8585 | 10.1 | 85.8952 | 8256.3 | 0 | 148.7 | 60 |  | 99.3634 | 8585
9 | 350 | 265 | 615 | 0 | 0 | 4 | 615 | 100 | 6.85 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 84 | 6800 | 41.7 | 3451.5 | -720 | 5491.5 | 6211.5 | 10.1 | 86.5087 | 5462.6 | 0 | 88.9 | 60 |  | 71.8924 | 6211.5
10 | 130 | 0 | 130 | 0 | 0 | 4 | 130 | 55 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.2 | 7280 | 40.7 | 2281.5 | 480 | 1747.5 | 1267.5 | 9.75 | 89.1895 | 1641.6 | 0 | 105.9 | 0 |  | 14.6701 | 1267.5
11 | 95 | 70 | 165 | 0 | 0 | 4 | 165 | 80 | 2.5 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.85 | 8840 | 40.698 | 2279.16 | 1560 | 3152.25 | 1592.25 | 9.65 | 88.7467 | 3056.2 | 0 | 96.05 | 0 |  | 18.4288 | 1592.25
12 | 0 | 555 | 555 | 0 | 0 | 5 | 555 | 55 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.7 | 8480 | 41.931 | 3721.77 | -360 | 8130.7872 | 5661 | 10.2 | 84.2563 | 8092.8 | 2829.7872 | 97.9872 | 60 |  | 65.5208 | 5661
13 | 145 | 175 | 320 | 0 | 0 | 5 | 320 | 110 | 2.8 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.1 | 7040 | 41.089 | 2736.63 | -1440 | 4829.5187 | 3200 | 10 | 87.1663 | 4963 | 3069.5187 | 16.5187 | 150 |  | 37.037 | 3200
14 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.85 | 8840 | 39.09 | 397.8 | 1800 | 5511.5305 | 909.5 | 10.7 | 80.038 | 5270.4 | 2802.0305 | 241.1305 | 0 |  | 10.5266 | 909.5
15 | 290 | 70 | 360 | 0 | 0 | 4 | 360 | 70 | 7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 1 | Βλάβη Απ/Ζ 26 | 15 | 84.6 | 8240 | 40.982 | 2611.44 | -600 | 3072 | 3672 | 10.2 | 84.4541 | 2937.8 | 0 | 134.2 | 0 |  | 42.5 | 3672
16 | 0 | 120 | 120 | 0 | 0 | 4 | 120 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85 | 9200 | 40.4 | 1930.5 | 960 | 2112 | 1152 | 9.6 | 88.8978 | 1959.35 | 0 | 152.65 | 0 |  | 13.3333 | 1152
17 | 95 | 90 | 185 | 0 | 0 | 4 | 185 | 55 | 2.1 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.9 | 8960 | 40.598 | 2162.16 | -240 | 1582.25 | 1822.25 | 9.85 | 86.8434 | 1445.4 | 0 | 136.85 | 0 |  | 21.0909 | 1822.25
18 | 300 | 70 | 370 | 0 | 0 | 5 | 370 | 70 | 7 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 84.7 | 8480 | 41.8 | 3568.5 | -480 | 4908.8883 | 3663 | 9.9 | 86.8095 | 4857.4 | 1725.8883 | 51.4883 | 0 |  | 42.3958 | 3663
19 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 35 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.75 | 8600 | 40.08 | 1556.1 | 120 | 2136.7021 | 1155 | 10.5 | 81.7533 | 2102.4 | 861.7021 | 84.3021 | 50 |  | 13.3681 | 1155
20 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 35 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.9 | 8960 | 40.36 | 1883.7 | 360 | 2828.4422 | 780 | 9.75 | 87.7341 | 2579.85 | 1688.4422 | 248.5922 | 0 |  | 9.0278 | 780
21 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 54 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.75 | 8600 | 40.018 | 1483.56 | -360 | 2190 | 2550 | 10 | 85.8409 | 2051.3 | 0 | 138.7 | 0 |  | 29.5139 | 2550
22 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.9 | 8960 | 40.67 | 2246.4 | 360 | 1760 | 1400 | 10 | 85.5408 | 1620.6 | 0 | 139.4 | 0 |  | 16.2037 | 1400
23 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.95 | 9080 | 39.698 | 1109.16 | 120 | 2733.0816 | 909 | 10.1 | 84.5953 | 2708.1 | 1704.0816 | 24.9816 | 0 |  | 10.5208 | 909
24 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 55 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.35 | 7640 | 41.192 | 2857.14 | -1440 | 5985.7979 | 3787.5 | 10.1 | 85.7938 | 5978 | 3638.2979 | 67.7979 | 60 |  | 43.8368 | 3787.5
25 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.4 | 7760 | 40.32 | 1836.9 | 120 | 3462.1596 | 1464.5 | 10.1 | 85.6926 | 3233.5 | 1877.6596 | 228.6596 | 0 |  | 16.9502 | 1464.5
26 | 0 | 420 | 420 | 0 | 0 | 5 | 420 | 55 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.85 | 8840 | 40.921 | 2540.07 | 1080 | 5238 | 4158 | 9.9 | 86.5057 | 5002.4 | 0 | 235.6 | 0 |  | 48.125 | 4158
27 | 215 | 280 | 495 | 0 | 0 | 4 | 495 | 55 | 4 | 5.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84 | 6800 | 41.467 | 3178.89 | -2040 | 4803.1809 | 5098.5 | 10.3 | 84.8289 | 4746 | 1744.6809 | 117.1809 | 60 |  | 59.0104 | 5098.5
28 | 85 | 0 | 85 | 0 | 0 | 4 | 85 | 55 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.75 | 8600 | 39.555 | 941.85 | 1800 | 2624.5 | 824.5 | 9.7 | 88.4958 | 2340 | 0 | 284.5 | 0 |  | 9.5428 | 824.5
29 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.5 | 8000 | 40.089 | 1566.63 | -600 | 3688.266 | 2575.5 | 10.1 | 85.491 | 3715.2 | 1712.766 | 3.066 | 30 |  | 29.809 | 2575.5
30 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 40 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.85 | 8840 | 40.65 | 2223 | 840 | 3241 | 2401 | 9.8 | 87.3884 | 3167.85 | 0 | 73.15 | 0 |  | 27.7894 | 2401
31 | 475 | 280 | 755 | 0 | 0 | 5 | 755 | 110 | 10.3 | 6.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84.8 | 8720 | 41.2679 | 2945.943 | -120 | 9172.4574 | 7776.5 | 10.3 | 83.2434 | 9081.2 | 1515.9574 | 151.2574 | 60 |  | 90.0058 | 7776.5
| 4995 | 5460 | 10455 | 0 | 0 | 132 | 10323 | 110 | 113.6 | 115.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 33 | 24 |  |  | 84.5258 | 8061.9355 | 40.7944 | 2392.0046 | 840 | 136425.3518 | 105182.25 | 10.0605 | 85.7748 | 133286.5 | 30403.1018 | 3968.8518 | 830 |  | 39.2706 | 105182.25