## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 460 | 370 | 830 | 0 | 0 | 4 | 830 | 110 | 9.9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.8 | 8720 | 42.028 | 3835.26 | 0 | 13843.5897 | 8300 | 10 | 85.7407 | 13209 | 5543.5897 | 694.5897 | 60 |  | 96.0648 | 8300
2 | 100 | 430 | 530 | 0 | 0 | 4 | 530 | 70 | 2.7 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84 | 6800 | 40.3 | 1813.5 | -1920 | 8426.7234 | 5618 | 10.6 | 82.4281 | 8431.5 | 4728.7234 | 55.2234 | 60 |  | 65.0231 | 5618
3 | 350 | 810 | 1160 | 0 | 0 | 5 | 1160 | 110 | 6.3 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 3 | 85.3 | 9920 | 41.808 | 3577.86 | 3120 | 17634.5957 | 12238 | 10.55 | 80.3323 | 17191.5 | 2276.5957 | 503.0957 | 60 |  | 141.6435 | 12238
4 | 545 | 1135 | 1680 | 0 | 0 | 5 | 1680 | 110 | 11 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 85.1 | 9440 | 41.0015 | 2634.255 | -480 | 16488 | 16968 | 10.1 | 84.3008 | 15946.6 | 0 | 601.4 | 60 |  | 196.3889 | 16968
5 | 390 | 520 | 910 | 0 | 0 | 4 | 910 | 110 | 9.9 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 84.1 | 7040 | 40.4385 | 1975.545 | -2400 | 6791 | 9191 | 10.1 | 86.3032 | 6773.4 | 0 | 17.6 | 0 |  | 106.3773 | 9191
6 | 760 | 870 | 1630 | 0 | 0 | 4 | 1630 | 110 | 15.8 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 6 | 83.5 | 5600 | 41.158 | 2817.36 | -1440 | 17859.2027 | 17196.5 | 10.55 | 83.8166 | 17906.9 | 2102.7027 | 12.3027 | 60 |  | 199.0336 | 17196.5
7 | 935 | 785 | 1720 | 0 | 0 | 4 | 1720 | 110 | 19.2 | 16.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.3 | 7520 | 41.901 | 3686.67 | 1920 | 19292 | 17372 | 10.1 | 85.8952 | 19240 | 0 | 52 | 0 |  | 201.0648 | 17372
8 | 695 | 800 | 1495 | 0 | 0 | 4 | 1495 | 110 | 15 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.5 | 8000 | 41.018 | 2653.56 | 480 | 15205.75 | 14725.75 | 9.85 | 87.6608 | 15157.5 | 0 | 48.25 | 0 |  | 170.4369 | 14725.75
9 | 525 | 765 | 1290 | 0 | 0 | 4 | 1290 | 110 | 10.3 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 83.1 | 4640 | 41.25 | 2925 | -3360 | 10249.5 | 13609.5 | 10.55 | 84.6323 | 10205.1 | 0 | 104.4 | 60 |  | 157.5174 | 13609.5
10 | 510 | 815 | 1325 | 0 | 0 | 4 | 1325 | 110 | 10 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 10 | 83 | 4400 | 41.6586 | 3403.062 | -240 | 15369.7872 | 13780 | 10.4 | 86.0624 | 15358.2 | 1829.7872 | 11.5872 | 0 |  | 159.4907 | 13780
11 | 810 | 925 | 1735 | 0 | 0 | 5 | 1735 | 110 | 14.9 | 16.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 82.6 | 3520 | 41.86 | 3638.7 | -880 | 16955.8 | 17835.8 | 10.28 | 87.9248 | 16940 | 0 | 75.8 | 60 |  | 206.4329 | 17835.8
12 | 930 | 845 | 1775 | 0 | 0 | 4 | 1775 | 108 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 83.15 | 4760 | 41.57 | 3299.4 | 1240 | 19495.875 | 18255.875 | 10.285 | 86.7075 | 19469.45 | 0 | 86.425 | 60 |  | 211.2948 | 18255.875
13 | 825 | 700 | 1525 | 0 | 0 | 5 | 1525 | 108 | 15.6 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 13 | 83.2 | 4880 | 42 | 3802.5 | 120 | 15903.75 | 15783.75 | 10.35 | 86.0583 | 15932 | 0 | 31.75 | 60 |  | 182.6823 | 15783.75
14 | 920 | 865 | 1785 | 0 | 0 | 4 | 1785 | 110 | 17 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.5 | 5600 | 41.5 | 3217.5 | 720 | 19819.5 | 19099.5 | 10.7 | 82.6416 | 19856.34 | 0 | 23.16 | 60 |  | 221.059 | 19099.5
15 | 960 | 950 | 1910 | 0 | 0 | 5 | 1910 | 110 | 17.9 | 18.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 81.7 | 1540 | 41.448 | 3156.66 | -4060 | 16472.5 | 20532.5 | 10.75 | 85.9868 | 16592.7 | 0 | 29.8 | 150 |  | 237.6447 | 20532.5
16 | 910 | 815 | 1725 | 0 | 0 | 4 | 1725 | 110 | 16.9 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 82.7 | 3740 | 41.699 | 3450.33 | 2200 | 20640.25 | 18440.25 | 10.69 | 84.3448 | 20650 | 0 | 50.25 | 60 |  | 213.4288 | 18440.25
17 | 915 | 875 | 1790 | 0 | 0 | 4 | 1790 | 110 | 16.7 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 83.05 | 4520 | 42.008 | 3811.86 | 780 | 19843.5 | 19063.5 | 10.65 | 83.9398 | 19821.5 | 0 | 82 | 60 |  | 220.6424 | 19063.5
18 | 990 | 935 | 1925 | 0 | 0 | 4 | 1925 | 110 | 17.9 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 82.8 | 3960 | 41.9 | 3685.5 | -560 | 19267.5 | 19827.5 | 10.3 | 87.3239 | 19236 | 0 | 91.5 | 60 |  | 229.485 | 19827.5
19 | 915 | 830 | 1745 | 0 | 0 | 4 | 1745 | 110 | 17 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 82.3 | 2860 | 41.398 | 3098.16 | -1100 | 17397 | 18497 | 10.6 | 85.9052 | 17439.7 | 0 | 17.3 | 60 |  | 214.0856 | 18497
20 | 690 | 945 | 1635 | 0 | 0 | 4 | 1635 | 110 | 12.6 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 20 | 83.1 | 4640 | 41.57 | 3299.4 | 1780 | 19274.5 | 17494.5 | 10.7 | 83.4459 | 19338.2 | 0 | 36.3 | 100 |  | 202.4826 | 17494.5
21 | 920 | 570 | 1490 | 0 | 0 | 4 | 1490 | 110 | 16.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 83.8 | 6320 | 41.9675 | 3764.475 | 1680 | 17623 | 15943 | 10.7 | 82.0485 | 17625.6 | 0 | 57.4 | 60 |  | 184.5255 | 15943
22 | 990 | 965 | 1955 | 0 | 0 | 4 | 1955 | 110 | 17.9 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 82.75 | 3850 | 41.851 | 3628.17 | -2470 | 18644 | 21114 | 10.8 | 83.3833 | 18711 | 0 | 13 | 80 |  | 244.375 | 21114
23 | 945 | 925 | 1870 | 0 | 0 | 4 | 1870 | 109 | 17.3 | 17.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.25 | 5000 | 41.648 | 3390.66 | 1150 | 19850 | 18700 | 10 | 88.9624 | 19688.1 | 0 | 161.9 | 0 |  | 216.4352 | 18700
24 | 930 | 940 | 1870 | 0 | 0 | 4 | 1870 | 109 | 17 | 17.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83.8 | 6320 | 41.22 | 2889.9 | 1320 | 20207 | 18887 | 10.1 | 86.9226 | 19823.98 | 0 | 443.02 | 60 |  | 218.5995 | 18887
25 | 840 | 960 | 1800 | 0 | 0 | 4 | 1800 | 109 | 14.4 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.7 | 8480 | 41.73 | 3486.6 | 2160 | 19980 | 17820 | 9.9 | 86.8095 | 19869.15 | 0 | 170.85 | 60 |  | 206.25 | 17820
26 | 985 | 955 | 1940 | 0 | 0 | 4 | 1940 | 110 | 19 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.8 | 8720 | 41.619 | 3356.73 | 240 | 19349 | 19109 | 9.85 | 87.0463 | 18915 | 0 | 434 | 0 |  | 221.169 | 19109
27 | 995 | 975 | 1970 | 0 | 0 | 4 | 1970 | 110 | 17.9 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.75 | 8600 | 41.884 | 3666.78 | -120 | 19580 | 19700 | 10 | 85.8409 | 19466.25 | 0 | 173.75 | 60 |  | 228.0093 | 19700
28 | 860 | 660 | 1520 | 0 | 0 | 4 | 1520 | 109 | 16.6 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 83.5 | 5600 | 41.382 | 3079.44 | -3000 | 12732 | 15732 | 10.35 | 85.4362 | 12514.95 | 0 | 277.05 | 60 |  | 182.0833 | 15732
| 21600 | 22935 | 44535 | 0 | 0 | 117 | 44418 | 110 | 410.6 | 447.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 |  |  | 83.6125 | 5892.5 | 41.5291 | 3251.6013 | -3120 | 474195.3238 | 460833.925 | 10.3477 | 85.2244 | 471309.62 | 16481.3988 | 4355.7038 | 1470 |  | 190.4902