## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 525 | 240 | 765 | 0 | 0 | 3 | 765 | 110 | 10 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 85.25 | 9800 | 40.95 | 2574 | 1680 | 11378.5459 | 7458.75 | 9.75 | 87.0242 | 11225.8 | 2239.7959 | 212.7459 | 60 |  | 86.3281 | 7458.75
2 | 490 | 495 | 985 | 0 | 0 | 4 | 985 | 109 | 9.7 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 2 | 84.5 | 8000 | 41.49 | 3205.8 | -1800 | 10717.2703 | 10047 | 10.2 | 84.6528 | 10738 | 2470.2703 | 39.2703 | 60 |  | 116.2847 | 10047
3 | 525 | 485 | 1010 | 0 | 0 | 4 | 1010 | 109 | 10.1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.35 | 7640 | 42.041 | 3850.47 | -360 | 9639 | 9999 | 9.9 | 87.527 | 9446.2 | 0 | 252.8 | 60 |  | 115.7292 | 9999
4 | 510 | 465 | 975 | 0 | 0 | 4 | 975 | 109 | 10.4 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84.6 | 8240 | 41.9589 | 3754.413 | 600 | 10350 | 9750 | 10 | 86.1432 | 10336.8 | 0 | 73.2 | 60 |  | 112.8472 | 9750
5 | 470 | 525 | 995 | 0 | 0 | 4 | 995 | 109 | 9.6 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 5 | 84.3 | 7520 | 41.6485 | 3391.245 | -720 | 9203.875 | 9923.875 | 9.9737 | 86.9825 | 9234.5 | 0 | 29.375 | 60 |  | 114.8597 | 9923.875
6 | 455 | 470 | 925 | 0 | 0 | 4 | 925 | 109 | 8.65 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 6 | 84.25 | 7400 | 41.13 | 2784.6 | -120 | 9222.5 | 9342.5 | 10.1 | 85.9968 | 9007.15 | 0 | 275.35 | 60 |  | 108.1308 | 9342.5
7 | 520 | 460 | 980 | 0 | 0 | 4 | 980 | 109 | 9.5 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 7 | 84.3 | 7520 | 41.22 | 2889.9 | 120 | 12215.3368 | 9800 | 10 | 86.7541 | 12054 | 2295.3368 | 221.3368 | 60 |  | 113.4259 | 9800
8 | 500 | 530 | 1030 | 0 | 0 | 4 | 1030 | 109 | 9.55 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 84.6 | 8240 | 41.488 | 3203.46 | 720 | 10814 | 10094 | 9.8 | 87.9012 | 10679.9 | 0 | 194.1 | 60 |  | 116.8287 | 10094
9 | 760 | 270 | 1030 | 0 | 0 | 4 | 1030 | 110 | 15.5 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 84.95 | 9080 | 41.98 | 3779.1 | 840 | 12903.1579 | 10300 | 10 | 85.4412 | 12609.6 | 1763.1579 | 293.5579 | 0 |  | 119.213 | 10300
10 | 420 | 340 | 760 | 0 | 0 | 4 | 760 | 110 | 8.3 | 6.5 | 0 | 0 | 1.15 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | ΒΛΑΒΗ ΦΡΕΝΩΝ | 10 | 83.7 | 6080 | 41.63 | 3369.6 | -3000 | 8259.5745 | 7600 | 10 | 88.0024 | 7976.4 | 3659.5745 | 343.1745 | 60 |  | 87.963 | 7600
11 | 565 | 410 | 975 | 0 | 0 | 4 | 975 | 110 | 11.1 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 11 | 84.45 | 7880 | 41.68 | 3428.1 | 1800 | 11647.5 | 9847.5 | 10.1 | 85.5917 | 11598.9 | 0 | 108.6 | 60 |  | 113.9757 | 9847.5
12 | 310 | 245 | 555 | 0 | 0 | 4 | 555 | 110 | 6.3 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 85.1 | 9440 | 41.302 | 2985.84 | 1560 | 11856.9894 | 5605.5 | 10.1 | 84.3008 | 11736.12 | 4691.4894 | 180.8694 | 60 |  | 64.8785 | 5605.5
13 | 330 | 275 | 605 | 0 | 0 | 4 | 605 | 110 | 6.8 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.9 | 8960 | 41.452 | 3161.34 | -480 | 9109.4474 | 6110.5 | 10.1 | 84.6939 | 9125 | 3478.9474 | 44.4474 | 60 |  | 70.7234 | 6110.5
14 | 775 | 605 | 1380 | 0 | 0 | 4 | 1380 | 110 | 15.4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.7 | 8480 | 41.947 | 3740.49 | -480 | 13044 | 13524 | 9.8 | 87.6954 | 12811.5 | 0 | 232.5 | 0 |  | 156.5278 | 13524
15 | 570 | 595 | 1165 | 0 | 0 | 4 | 1165 | 110 | 12.2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 84.8 | 8720 | 41.852 | 3629.34 | 240 | 11831.75 | 11591.75 | 9.95 | 86.1715 | 11689.05 | 0 | 142.7 | 0 |  | 134.1638 | 11591.75
16 | 610 | 485 | 1095 | 0 | 0 | 4 | 1095 | 109 | 12.6 | 11.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 16 | 84.05 | 6920 | 41.611 | 3347.37 | -1800 | 9259.5 | 11059.5 | 10.1 | 86.4059 | 8957.76 | 0 | 361.74 | 60 |  | 128.0035 | 11059.5
17 | 545 | 445 | 990 | 0 | 0 | 4 | 990 | 110 | 9.6 | 6.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 17 | 84.4 | 7760 | 41.4 | 3100.5 | 840 | 10839 | 9999 | 10.1 | 85.6926 | 10855.9 | 0 | 43.1 | 60 |  | 115.7292 | 9999
18 | 545 | 450 | 995 | 0 | 0 | 4 | 995 | 110 | 10.5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.6 | 8240 | 42.02 | 3825.9 | 480 | 10529.5 | 10049.5 | 10.1 | 85.2903 | 10168.9 | 0 | 420.6 | 60 |  | 116.3137 | 10049.5
19 | 650 | 385 | 1035 | 0 | 0 | 4 | 1035 | 110 | 13.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 83 | 4400 | 41.14 | 2796.3 | -3840 | 9478.0851 | 10350 | 10 | 89.5049 | 9562 | 2968.0851 | 16.0851 | 100 |  | 119.7917 | 10350
20 | 885 | 300 | 1185 | 0 | 0 | 4 | 1185 | 110 | 18.3 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 83.6 | 5840 | 42.15 | 3978 | 1440 | 13764 | 12324 | 10.4 | 84.8211 | 13859.2 | 0 | 14.8 | 110 |  | 142.6389 | 12324
21 | 395 | 715 | 1110 | 0 | 0 | 4 | 1110 | 110 | 7.4 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 83.55 | 5720 | 42.1 | 3919.5 | -120 | 11313 | 11433 | 10.3 | 85.7477 | 11343.6 | 0 | 29.4 | 60 |  | 132.3264 | 11433
22 | 515 | 645 | 1160 | 0 | 0 | 4 | 1160 | 110 | 10.1 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84.5 | 8000 | 41.65 | 3393 | 2280 | 13996 | 11716 | 10.1 | 85.491 | 13738.6 | 0 | 317.4 | 60 |  | 135.6019 | 11716
23 | 460 | 530 | 990 | 0 | 0 | 4 | 990 | 110 | 8.3 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 23 | 84.6 | 8240 | 41.25 | 2925 | 240 | 10041 | 9801 | 9.9 | 87.0133 | 9954.2 | 0 | 146.8 | 60 |  | 113.4375 | 9801
24 | 585 | 535 | 1120 | 0 | 0 | 4 | 1120 | 110 | 11.85 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 24 | 85.05 | 9320 | 41.34 | 3030.3 | 1080 | 12280 | 11200 | 10 | 85.2427 | 12293.2 | 0 | 46.8 | 60 |  | 129.6296 | 11200
25 | 460 | 445 | 905 | 0 | 0 | 4 | 905 | 109 | 10.55 | 9.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 25 | 85 | 9200 | 41.8008 | 3569.436 | -120 | 8839.5 | 8959.5 | 9.9 | 86.2039 | 8776.4 | 0 | 123.1 | 60 |  | 103.6979 | 8959.5
26 | 240 | 295 | 535 | 0 | 0 | 4 | 535 | 109 | 3.95 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.1 | 7040 | 40.96 | 2585.7 | -2160 | 6328.2979 | 5350 | 10 | 87.1663 | 6119.8 | 3138.2979 | 268.4979 | 60 |  | 61.9213 | 5350
27 | 355 | 355 | 710 | 0 | 0 | 3 | 710 | 109 | 8.05 | 7.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 27 | 83.9 | 6560 | 40.198 | 1694.16 | -480 | 7046 | 7526 | 10.6 | 82.6248 | 6962.4 | 0 | 143.6 | 60 |  | 87.1065 | 7526
28 | 420 | 175 | 595 | 0 | 0 | 4 | 595 | 110 | 8.2 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84.05 | 6920 | 41.798 | 3566.16 | 360 | 9020.2287 | 6277.25 | 10.55 | 82.7203 | 9037.4 | 2382.9787 | 42.8287 | 60 |  | 72.6534 | 6277.25
29 | 220 | 535 | 755 | 0 | 0 | 4 | 755 | 110 | 3.9 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 29 | 84.3 | 7520 | 41.65 | 3393 | 600 | 9910.6383 | 7550 | 10 | 86.7541 | 9792 | 1760.6383 | 178.6383 | 60 |  | 87.3843 | 7550
30 | 330 | 305 | 635 | 0 | 0 | 4 | 635 | 103 | 7.1 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.95 | 9080 | 40.85 | 2457 | 1560 | 7846.5 | 6286.5 | 9.9 | 86.3043 | 7540.6 | 0 | 365.9 | 60 |  | 72.7604 | 6286.5
| 14940 | 13010 | 27950 | 0 | 0 | 118 | 27832 | 110 | 296.8 | 262.6 | 0 | 0 | 1.15 | 0 | 0 | 0 | 0 | 0 | 52 | 53 |  |  | 84.4133 | 7792 | 41.5229 | 3244.3008 | 960 | 312684.1971 | 280875.625 | 10.0492 | 86.0986 | 309230.88 | 30848.5721 | 5163.3171 | 1710 |  | 108.3625 | 280875.625