## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 340 | 250 | 590 | 0 | 0 | 4 | 590 | 110 | 6.8 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.9 | 8960 | 41.5 | 3217.5 | -120 | 6461.3404 | 5959 | 10.1 | 84.6939 | 6307.2 | 622.3404 | 214.1404 | 60 |  | 68.9699 | 5959
2 | 695 | 350 | 1045 | 0 | 0 | 4 | 1045 | 110 | 14.5 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.5 | 8000 | 42.07 | 3884.4 | -960 | 9281 | 10241 | 9.8 | 88.108 | 9108 | 0 | 233 | 60 |  | 118.5301 | 10241
3 | 340 | 260 | 600 | 0 | 0 | 3 | 600 | 110 | 6.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.35 | 7640 | 42.1499 | 3977.8713 | -360 | 5880 | 6240 | 10.4 | 83.319 | 5850.6 | 0 | 89.4 | 60 |  | 72.2222 | 6240
4 | 60 | 665 | 725 | 0 | 0 | 3 | 725 | 110 | 1.4 | 13.5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ Δ/Κ Ρ10 | 4 | 84.75 | 8600 | 40.79 | 2386.8 | 960 | 8137.5 | 7177.5 | 9.9 | 86.708 | 7866.8 | 0 | 270.7 | 0 |  | 83.0729 | 7177.5
5 | 0 | 805 | 805 | 0 | 0 | 4 | 805 | 55 | 0 | 17.3 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 5 | 84.55 | 8120 | 40.97 | 2597.4 | -480 | 7650.5 | 8130.5 | 10.1 | 85.3905 | 7803.7 | 0 | 46.8 | 200 |  | 94.103 | 8130.5
6 | 0 | 865 | 865 | 0 | 0 | 4 | 865 | 54 | 0 | 16.8 | 0 | 0 | 18.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 6 | 84.4 | 7760 | 40.901 | 2516.67 | -360 | 8376.5 | 8736.5 | 10.1 | 85.6926 | 8006.4 | 0 | 430.1 | 60 |  | 101.1169 | 8736.5
7 | 0 | 665 | 665 | 0 | 0 | 4 | 665 | 55 | 0 | 13.8 | 0 | 0 | 15.75 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ Δ/Κ Ρ10 | 7 | 83.55 | 5720 | 40.589 | 2151.63 | -2040 | 4809.5 | 6849.5 | 10.3 | 85.7477 | 4886 | 0 | 23.5 | 100 |  | 79.2766 | 6849.5
8 | 0 | 360 | 360 | 0 | 0 | 4 | 360 | 55 | 0 | 7.1 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 8 | 84.5 | 8000 | 40.498 | 2045.16 | 2280 | 5808 | 3528 | 9.8 | 88.108 | 5472 | 0 | 396 | 60 |  | 40.8333 | 3528
9 | 0 | 585 | 585 | 0 | 0 | 4 | 585 | 55 | 0 | 12.1 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ Δ/Κ Ρ10 | 9 | 84.85 | 8840 | 41.852 | 3629.34 | 840 | 6748.5 | 5908.5 | 10.1 | 84.7927 | 6600 | 0 | 208.5 | 60 |  | 68.3854 | 5908.5
10 | 85 | 340 | 425 | 0 | 0 | 4 | 425 | 55 | 29.95 | 8.5 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ Δ/Κ Ρ10 | 10 | 84.4 | 7760 | 40.399 | 1929.33 | -1080 | 6338.1545 | 4292.5 | 10.1 | 85.6926 | 6225.45 | 3125.6545 | 172.7045 | 60 |  | 49.6817 | 4292.5
11 | 655 | 20 | 675 | 0 | 0 | 4 | 675 | 100 | 13.75 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.15 | 7160 | 41.08 | 2726.1 | -600 | 6285 | 6885 | 10.2 | 85.3558 | 6329.1 | 0 | 15.9 | 60 |  | 79.6875 | 6885
12 | 350 | 235 | 585 | 0 | 0 | 4 | 585 | 110 | 7.7 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 85.15 | 9560 | 41.638 | 3378.96 | 2400 | 8103.75 | 5703.75 | 9.75 | 87.2258 | 7871.85 | 0 | 231.9 | 0 |  | 66.0156 | 5703.75
13 | 400 | 120 | 520 | 0 | 0 | 0 | 520 | 109 | 8.1 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.75 | 8600 | 40.41 | 1942.2 | -960 | 7846.383 | 5200 | 10 | 85.8409 | 7759.9 | 3606.383 | 146.483 | 60 |  | 60.1852 | 5200
14 | 500 | 0 | 500 | 0 | 0 | 5 | 500 | 55 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 85.25 | 9800 | 40.881 | 2493.27 | 1200 | 7845.2073 | 4925 | 9.85 | 86.1407 | 7776.3 | 1720.2073 | 128.9073 | 60 |  | 57.0023 | 4925
15 | 400 | 195 | 595 | 0 | 0 | 4 | 595 | 110 | 9.1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 84.8 | 8720 | 41.381 | 3078.27 | -1080 | 7689.3351 | 5801.25 | 9.75 | 87.9391 | 7465.8 | 2968.0851 | 223.5351 | 0 |  | 67.1441 | 5801.25
16 | 420 | 115 | 535 | 0 | 0 | 3 | 535 | 110 | 8.6 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.4 | 7760 | 41.88 | 3662.1 | -960 | 5611.0676 | 5403.5 | 10.1 | 85.6926 | 5580.6 | 1167.5676 | 30.4676 | 0 |  | 62.5405 | 5403.5
17 | 250 | 190 | 440 | 0 | 0 | 4 | 440 | 109 | 5.2 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.5 | 8000 | 42.002 | 3804.84 | 240 | 4706 | 4466 | 10.15 | 85.0698 | 4630.5 | 0 | 75.5 | 0 |  | 51.6898 | 4466
18 | 315 | 460 | 775 | 0 | 0 | 4 | 775 | 110 | 6.6 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.1 | 7040 | 42 | 3802.5 | -960 | 6867.5 | 7827.5 | 10.1 | 86.3032 | 6792.5 | 0 | 135 | 60 |  | 90.5961 | 7827.5
19 | 385 | 35 | 420 | 0 | 0 | 3 | 420 | 100 | 8.2 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.15 | 7160 | 41.398 | 3098.16 | 120 | 4573.75 | 4453.75 | 10.6042 | 82.1025 | 4494 | 0 | 79.75 | 0 |  | 51.548 | 4453.75
20 | 230 | 220 | 450 | 0 | 0 | 4 | 450 | 55 | 4.45 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 84.4 | 7760 | 41.702 | 3453.84 | 600 | 4942.5 | 4342.5 | 9.65 | 89.6886 | 4899.95 | 0 | 42.55 | 0 |  | 50.2604 | 4342.5
21 | 340 | 115 | 455 | 0 | 0 | 4 | 455 | 108 | 7.05 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 85.05 | 9320 | 41.8 | 3568.5 | 1560 | 6110 | 4550 | 10 | 85.2427 | 5963.1 | 0 | 146.9 | 0 |  | 52.662 | 4550
22 | 470 | 380 | 850 | 0 | 0 | 3 | 850 | 109 | 9 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 83.8 | 6320 | 41.24 | 2913.3 | -3000 | 5415 | 8415 | 9.9 | 88.6787 | 5340 | 0 | 75 | 0 |  | 97.3958 | 8415
23 | 355 | 115 | 470 | 0 | 0 | 3 | 470 | 110 | 8.2 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.5 | 8000 | 41.75 | 3510 | 1680 | 6215.5 | 4535.5 | 9.65 | 89.4776 | 6205.85 | 0 | 69.65 | 60 |  | 52.4942 | 4535.5
24 | 255 | 145 | 400 | 0 | 0 | 4 | 400 | 108 | 5.1 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83 | 4400 | 41.538 | 3261.96 | -3600 | 3971.3514 | 4220 | 10.55 | 84.8387 | 3990 | 3351.3514 | 41.3514 | 60 |  | 48.8426 | 4220
25 | 50 | 300 | 350 | 0 | 0 | 4 | 350 | 55 | 1 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 83.25 | 5000 | 41.192 | 2857.14 | 600 | 4310 | 3710 | 10.6 | 83.9268 | 4416 | 0 | 14 | 120 |  | 42.9398 | 3710
26 | 0 | 485 | 485 | 0 | 0 | 4 | 485 | 55 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 83.05 | 4520 | 41.499 | 3216.33 | -480 | 4491.25 | 4971.25 | 10.25 | 87.2155 | 4406.4 | 0 | 84.85 | 0 |  | 57.5376 | 4971.25
27 | 370 | 85 | 455 | 0 | 0 | 4 | 455 | 105 | 7.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 83.75 | 6200 | 41.399 | 3099.33 | 1680 | 6116.25 | 4436.25 | 9.75 | 90.1508 | 6066.3 | 0 | 49.95 | 0 |  | 51.3455 | 4436.25
28 | 485 | 0 | 485 | 0 | 0 | 4 | 485 | 55 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.9 | 8960 | 41.662 | 3407.04 | 2760 | 7513 | 4753 | 9.8 | 87.2865 | 7286.1 | 0 | 226.9 | 0 |  | 55.0116 | 4753
29 | 440 | 100 | 540 | 0 | 0 | 4 | 540 | 70 | 9.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.7 | 8480 | 42.05 | 3861 | -480 | 4839 | 5319 | 9.85 | 87.2502 | 4773 | 0 | 126 | 60 |  | 61.5625 | 5319
30 | 365 | 115 | 480 | 0 | 0 | 4 | 480 | 109 | 6.9 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 30 | 85 | 9200 | 42.05 | 3861 | 720 | 5400 | 4680 | 9.75 | 87.5301 | 5357.6 | 0 | 42.4 | 0 |  | 54.1667 | 4680
31 | 0 | 385 | 385 | 0 | 0 | 3 | 385 | 55 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 31 | 85.2 | 9680 | 41.25 | 2925 | 480 | 4195.25 | 3715.25 | 9.65 | 88.0277 | 3572.55 | 0 | 622.7 | 0 |  | 43.0006 | 3715.25
| 8555 | 8960 | 17515 | 0 | 0 | 114 | 17401 | 110 | 204.9 | 188.6 | 0 | 0 | 130.05 | 0 | 0 | 0 | 0 | 0 | 37 | 35 |  |  | 84.4065 | 7775.4839 | 41.4039 | 3105.0626 | 600 | 192538.0891 | 175376.5 | 10.0129 | 86.4246 | 189103.55 | 16561.5891 | 4694.5391 | 1260 |  | 65.4781 | 175376.5