## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 54 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 85.3 | 9920 | 41.3 | 2983.5 | 240 | 4482 | 4242 | 10.1 | 83.9115 | 4097.5 | 0 | 384.5 | 0 |  | 49.0972 | 4242
2 | 460 | 0 | 460 | 0 | 0 | 3 | 460 | 54 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 85.15 | 9560 | 41.448 | 3156.66 | -360 | 4079 | 4439 | 9.65 | 88.1297 | 3775 | 0 | 304 | 0 |  | 51.3773 | 4439
3 | 490 | 0 | 490 | 0 | 0 | 4 | 490 | 54 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 83.9 | 6560 | 41.638 | 3378.96 | -3000 | 4310.7021 | 4949 | 10.1 | 86.7152 | 4125.1 | 2361.7021 | 245.6021 | 60 |  | 57.2801 | 4949
4 | 355 | 145 | 500 | 0 | 0 | 4 | 500 | 90 | 7.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 83.8 | 6320 | 42.0305 | 3838.185 | -240 | 4910 | 5150 | 10.3 | 85.2348 | 4912.9 | 0 | 57.1 | 60 |  | 59.6065 | 5150
5 | 465 | 0 | 465 | 0 | 0 | 4 | 465 | 53 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 83.5 | 5600 | 41.772 | 3535.74 | -720 | 3930 | 4650 | 10 | 88.4265 | 3890.9 | 0 | 39.1 | 0 |  | 53.8194 | 4650
6 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 50 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 83.85 | 6440 | 41.648 | 3390.66 | 840 | 5250 | 4410 | 9.8 | 89.4765 | 5183 | 0 | 127 | 60 |  | 51.0417 | 4410
7 | 400 | 105 | 505 | 0 | 0 | 4 | 505 | 70 | 8.7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.4 | 7760 | 41.83 | 3603.6 | 1320 | 7611.9894 | 5100.5 | 10.1 | 85.6926 | 7368.05 | 1191.4894 | 243.9394 | 0 |  | 59.0336 | 5100.5
8 | 535 | 205 | 740 | 0 | 0 | 3 | 740 | 108 | 12.4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 8 | 84.55 | 8120 | 41.632 | 3371.94 | 360 | 7760 | 7400 | 10 | 86.2444 | 7701.5 | 0 | 58.5 | 0 |  | 85.6481 | 7400
9 | 525 | 10 | 535 | 0 | 0 | 3 | 535 | 100 | 10.9 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.25 | 7400 | 41.649 | 3391.83 | -720 | 4552.25 | 5272.25 | 9.8547 | 88.1377 | 4511.4 | 0 | 40.85 | 0 |  | 61.0214 | 5272.25
10 | 590 | 0 | 590 | 0 | 0 | 3 | 590 | 53 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 41.898 | 3683.16 | 120 | 5843 | 5723 | 9.7 | 89.4373 | 5537 | 0 | 306 | 0 |  | 66.2384 | 5723
11 | 0 | 495 | 495 | 0 | 0 | 3 | 495 | 50 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 84.15 | 7160 | 41.849 | 3625.83 | -360 | 4515.75 | 4875.75 | 9.85 | 88.3887 | 4440.2 | 0 | 75.55 | 0 |  | 56.4323 | 4875.75
12 | 500 | 0 | 500 | 0 | 0 | 3 | 500 | 50 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.05 | 6920 | 41.97 | 3767.4 | -240 | 4760 | 5000 | 10 | 87.2699 | 4684.2 | 0 | 135.8 | 60 |  | 57.8704 | 5000
13 | 105 | 265 | 370 | 0 | 0 | 4 | 370 | 50 | 2 | 5.8 | 0 | 0 | 8.25 | 0 | 0 | 0 | 2.75 | 0 | 1 | 1 | ΒΛΑΒΗ 48V D.C. | 13 | 84.5 | 8000 | 41.13 | 2784.6 | 1080 | 5921.5426 | 3607.5 | 9.75 | 88.5599 | 5747.7 | 1234.0426 | 173.8426 | 0 |  | 41.7535 | 3607.5
14 | 535 | 40 | 575 | 0 | 0 | 4 | 575 | 50 | 10.9 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.45 | 7880 | 41.889 | 3672.63 | -120 | 5634 | 5754 | 10.007 | 86.3875 | 5572.5 | 0 | 61.5 | 0 |  | 66.5972 | 5754
15 | 385 | 215 | 600 | 0 | 0 | 4 | 600 | 110 | 8.15 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 15 | 84.45 | 7880 | 41.598 | 3332.16 | 0 | 6120 | 6120 | 10.2 | 84.7525 | 6130.6 | 0 | 49.4 | 60 |  | 70.8333 | 6120
16 | 500 | 90 | 590 | 0 | 0 | 4 | 590 | 85 | 10.85 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84 | 6800 | 41.901 | 3686.67 | -1080 | 4731.5 | 5811.5 | 9.85 | 88.7044 | 4509.5 | 0 | 222 | 0 |  | 67.2627 | 5811.5
17 | 500 | 0 | 500 | 0 | 0 | 3 | 500 | 49 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.35 | 7640 | 41.601 | 3335.67 | 840 | 5715 | 4875 | 9.75 | 88.8736 | 5594.4 | 0 | 180.6 | 60 |  | 56.4236 | 4875
18 | 215 | 90 | 305 | 0 | 0 | 4 | 305 | 70 | 5.9 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 84.55 | 8120 | 41.602 | 3336.84 | 480 | 3560.5 | 3080.5 | 10.1 | 85.3905 | 3538.75 | 0 | 21.75 | 0 |  | 35.6539 | 3080.5
19 | 0 | 410 | 410 | 0 | 0 | 4 | 410 | 50 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.2 | 7280 | 41.458 | 3168.36 | -840 | 3219 | 4059 | 9.9 | 87.8381 | 3011.8 | 0 | 207.2 | 0 |  | 46.9792 | 4059
20 | 90 | 235 | 325 | 0 | 0 | 3 | 325 | 100 | 2 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.4 | 7760 | 41.001 | 2633.67 | 480 | 3616.25 | 3136.25 | 9.65 | 89.6886 | 3457.9 | 0 | 158.35 | 0 |  | 36.2992 | 3136.25
21 | 0 | 315 | 315 | 0 | 0 | 4 | 315 | 50 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.2 | 7280 | 41.2 | 2866.5 | -480 | 4535.7766 | 3244.5 | 10.3 | 84.4269 | 4401.9 | 1771.2766 | 193.8766 | 60 |  | 37.5521 | 3244.5
22 | 285 | 95 | 380 | 0 | 0 | 3 | 380 | 70 | 6.1 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 83.6 | 5840 | 42.119 | 3941.73 | -1440 | 4720.9362 | 3762 | 9.9 | 89.105 | 4628.2 | 2398.9362 | 92.7362 | 0 |  | 43.5417 | 3762
23 | 225 | 210 | 435 | 0 | 0 | 4 | 435 | 55 | 4.2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.6 | 5840 | 41.4 | 3100.5 | 0 | 4632.75 | 4632.75 | 10.65 | 82.83 | 4571.4 | 0 | 61.35 | 0 |  | 53.6198 | 4632.75
24 | 270 | 190 | 460 | 0 | 0 | 4 | 460 | 110 | 5.65 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83.8 | 6320 | 41.968 | 3765.06 | 480 | 5080 | 4600 | 10 | 87.7919 | 5058.9 | 0 | 81.1 | 60 |  | 53.2407 | 4600
25 | 565 | 0 | 565 | 0 | 0 | 4 | 565 | 50 | 11.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 83.65 | 5960 | 41.649 | 3391.83 | -360 | 5346.5 | 5706.5 | 10.1 | 87.2357 | 5278 | 0 | 128.5 | 60 |  | 66.0475 | 5706.5
26 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 50 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.1 | 7040 | 41.7 | 3451.5 | 1080 | 6180 | 5100 | 10 | 87.1663 | 6149 | 0 | 31 | 0 |  | 59.0278 | 5100
27 | 420 | 0 | 420 | 0 | 0 | 3 | 420 | 50 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 85 | 9200 | 41.15 | 2808 | 2160 | 6255 | 4095 | 9.75 | 87.5301 | 5920.2 | 0 | 334.8 | 0 |  | 47.3958 | 4095
28 | 385 | 40 | 425 | 0 | 0 | 4 | 425 | 95 | 7.95 | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 85.15 | 9560 | 40.75 | 2340 | 360 | 4652.5 | 4292.5 | 10.1 | 84.2032 | 4580.6 | 0 | 131.9 | 60 |  | 49.6817 | 4292.5
29 | 0 | 555 | 555 | 0 | 0 | 4 | 555 | 55 | 0 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.4 | 7760 | 41.65 | 3393 | -1800 | 3805.5 | 5605.5 | 10.1 | 85.6926 | 3817.9 | 0 | 47.6 | 60 |  | 64.8785 | 5605.5
30 | 0 | 500 | 500 | 0 | 0 | 4 | 500 | 50 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.35 | 7640 | 42 | 3802.5 | -120 | 4780 | 4900 | 9.8 | 88.4201 | 4533.3 | 0 | 246.7 | 0 |  | 56.713 | 4900
| 9250 | 5140 | 14390 | 0 | 0 | 110 | 14280 | 110 | 194.05 | 108.9 | 0 | 0 | 8.25 | 0 | 0 | 0 | 2.75 | 0 | 41 | 27 |  |  | 84.265 | 7436 | 41.6144 | 3351.2895 | -2040 | 150511.4468 | 143594 | 9.9787 | 87.011 | 146729.3 | 8957.4468 | 4442.1468 | 660 |  | 55.3989