## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 35 | 455 | 490 | 0 | 0 | 4 | 490 | 85 | 1.05 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.55 | 8120 | 41.951 | 3745.17 | 480 | 5306.5 | 4826.5 | 9.85 | 87.5578 | 5153.8 | 0 | 152.7 | 0 |  | 55.8623 | 4826.5
2 | 280 | 20 | 300 | 0 | 0 | 3 | 300 | 50 | 6.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.6 | 8240 | 41.3315 | 3020.355 | 120 | 3060 | 2940 | 9.8 | 87.9012 | 2946.15 | 0 | 113.85 | 0 |  | 34.0278 | 2940
3 | 335 | 0 | 335 | 0 | 0 | 4 | 335 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.6 | 8240 | 40.85 | 2457 | 0 | 3249.5 | 3249.5 | 9.7 | 88.8074 | 3022.2 | 0 | 227.3 | 0 |  | 37.61 | 3249.5
4 | 395 | 0 | 395 | 0 | 0 | 3 | 395 | 50 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.6 | 8240 | 41.901 | 3686.67 | 0 | 3989.5 | 3989.5 | 10.1 | 85.2903 | 3701.1 | 0 | 288.4 | 0 |  | 46.1748 | 3989.5
5 | 330 | 0 | 330 | 0 | 0 | 3 | 330 | 50 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480 | 41.247 | 2921.49 | 240 | 3573 | 3333 | 10.1 | 85.0905 | 3547.8 | 0 | 85.2 | 60 |  | 38.5764 | 3333
6 | 335 | 125 | 460 | 0 | 0 | 3 | 460 | 100 | 7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 84.95 | 9080 | 41.71 | 3463.2 | 600 | 5039 | 4439 | 9.65 | 88.5401 | 4719.75 | 0 | 319.25 | 0 |  | 51.3773 | 4439
7 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 50 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 84.65 | 8360 | 41.698 | 3449.16 | -720 | 4152 | 4872 | 10.15 | 84.7706 | 4204.8 | 0 | 7.2 | 60 |  | 56.3889 | 4872
8 | 55 | 445 | 500 | 0 | 0 | 4 | 500 | 110 | 1 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.8 | 8720 | 41.611 | 3347.37 | 360 | 5185 | 4825 | 9.65 | 88.8504 | 4920.2 | 0 | 264.8 | 0 |  | 55.8449 | 4825
9 | 160 | 370 | 530 | 0 | 0 | 4 | 530 | 85 | 4.2 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 84.5 | 8000 | 41.689 | 3438.63 | -720 | 4553.5 | 5273.5 | 9.95 | 86.7798 | 4496.8 | 0 | 56.7 | 0 |  | 61.0359 | 5273.5
10 | 425 | 15 | 440 | 0 | 0 | 4 | 440 | 55 | 8.6 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.65 | 8360 | 41.119 | 2771.73 | 360 | 4628 | 4268 | 9.7 | 88.7033 | 4555.2 | 0 | 72.8 | 0 |  | 49.3981 | 4268
11 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 50 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.9 | 8960 | 40.229 | 1730.43 | 600 | 4200 | 3600 | 9.6 | 89.105 | 3978.85 | 0 | 221.15 | 0 |  | 41.6667 | 3600
12 | 10 | 495 | 505 | 0 | 0 | 3 | 505 | 50 | 0.4 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.1 | 7040 | 40.409 | 1941.03 | -1920 | 3180.5 | 5100.5 | 10.1 | 86.3032 | 3080.4 | 0 | 160.1 | 60 |  | 59.0336 | 5100.5
13 | 535 | 50 | 585 | 0 | 0 | 4 | 585 | 50 | 10.6 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.6 | 5840 | 40.9595 | 2585.115 | -1200 | 4620.75 | 5820.75 | 9.95 | 88.6572 | 4632.4 | 0 | 48.35 | 60 |  | 67.3698 | 5820.75
14 | 580 | 0 | 580 | 0 | 0 | 4 | 580 | 54 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 83.55 | 5720 | 41.29 | 2971.8 | -120 | 5535 | 5655 | 9.75 | 90.5847 | 5313 | 0 | 222 | 0 |  | 65.4514 | 5655
15 | 535 | 0 | 535 | 0 | 0 | 4 | 535 | 54 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.55 | 5720 | 41.19 | 2854.8 | 0 | 5457 | 5457 | 10.2 | 86.5883 | 5505.5 | 0 | 11.5 | 60 |  | 63.1597 | 5457
16 | 550 | 0 | 550 | 0 | 0 | 3 | 550 | 50 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.5 | 8000 | 40.848 | 2454.66 | 2280 | 7670 | 5390 | 9.8 | 88.108 | 7550 | 0 | 120 | 0 |  | 62.3843 | 5390
17 | 105 | 555 | 660 | 0 | 0 | 4 | 660 | 70 | 2.2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 17 | 84.2 | 7280 | 41.45 | 3159 | -720 | 5814 | 6534 | 9.9 | 87.8381 | 5852 | 0 | 22 | 60 |  | 75.625 | 6534
18 | 210 | 395 | 605 | 0 | 0 | 4 | 605 | 70 | 4.8 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.35 | 7640 | 41.582 | 3313.44 | 360 | 6652 | 6292 | 10.4 | 83.319 | 6645.2 | 0 | 66.8 | 60 |  | 72.8241 | 6292
19 | 365 | 250 | 615 | 0 | 0 | 3 | 615 | 85 | 8.2 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 85.05 | 9320 | 41.804 | 3573.18 | 1680 | 7719.3 | 6039.3 | 9.82 | 86.8052 | 7649.8 | 0 | 69.5 | 0 |  | 69.8993 | 6039.3
20 | 480 | 130 | 610 | 0 | 0 | 4 | 610 | 70 | 9.8 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 84.85 | 8840 | 41.8 | 3568.5 | -480 | 5559 | 6039 | 9.9 | 86.5057 | 5431.2 | 0 | 127.8 | 0 |  | 69.8958 | 6039
21 | 480 | 365 | 845 | 0 | 0 | 4 | 845 | 110 | 11.3 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 84.8 | 8720 | 42 | 3802.5 | -120 | 8414.5 | 8534.5 | 10.1 | 84.8917 | 8236.2 | 0 | 238.3 | 60 |  | 98.7789 | 8534.5
22 | 565 | 85 | 650 | 0 | 0 | 3 | 650 | 70 | 11.9 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 22 | 84.4 | 7760 | 41.732 | 3488.94 | -960 | 5540 | 6500 | 10 | 86.5495 | 5372.85 | 0 | 167.15 | 0 |  | 75.2315 | 6500
23 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.65 | 8360 | 41.733 | 3490.11 | 600 | 7150.25 | 6550.25 | 9.85 | 87.3525 | 7078.05 | 0 | 72.2 | 0 |  | 75.8131 | 6550.25
24 | 115 | 775 | 890 | 0 | 0 | 3 | 890 | 110 | 2.1 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.6 | 8240 | 41.842 | 3617.64 | -120 | 8557.5 | 8677.5 | 9.75 | 88.352 | 8467.2 | 0 | 90.3 | 0 |  | 100.434 | 8677.5
25 | 0 | 665 | 665 | 0 | 0 | 5 | 665 | 50 | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.45 | 7880 | 41.659 | 3403.53 | -360 | 6356.5 | 6716.5 | 10.1 | 85.5917 | 6278.4 | 0 | 138.1 | 60 |  | 77.7373 | 6716.5
26 | 0 | 540 | 540 | 0 | 0 | 4 | 540 | 50 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.05 | 6920 | 40.983 | 2612.61 | -960 | 4494 | 5454 | 10.1 | 86.4059 | 4477.5 | 0 | 76.5 | 60 |  | 63.125 | 5454
27 | 60 | 690 | 750 | 0 | 0 | 4 | 750 | 70 | 1.7 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 83.7 | 6080 | 42.102 | 3921.84 | -840 | 6847.5 | 7687.5 | 10.25 | 85.856 | 6883.9 | 0 | 23.6 | 60 |  | 88.9757 | 7687.5
28 | 330 | 400 | 730 | 0 | 0 | 4 | 730 | 55 | 6.7 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.4 | 7760 | 41.851 | 3628.17 | 1680 | 9053 | 7373 | 10.1 | 85.6926 | 8971.2 | 0 | 141.8 | 60 |  | 85.3356 | 7373
29 | 275 | 350 | 625 | 0 | 0 | 4 | 625 | 50 | 5.9 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.4 | 7760 | 41.449 | 3157.83 | 0 | 6250 | 6250 | 10 | 86.5495 | 6075.5 | 0 | 174.5 | 0 |  | 72.338 | 6250
30 | 505 | 185 | 690 | 0 | 0 | 4 | 690 | 100 | 11.5 | 3.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 30 | 84.25 | 7400 | 41.982 | 3781.44 | -360 | 6540 | 6900 | 10 | 86.8568 | 6452.5 | 0 | 147.5 | 60 |  | 79.8611 | 6900
31 | 0 | 625 | 625 | 0 | 0 | 4 | 625 | 50 | 0 | 13.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.4 | 7760 | 41.001 | 2633.67 | 360 | 6610 | 6250 | 10 | 86.5495 | 6475.1 | 0 | 134.9 | 0 |  | 72.338 | 6250
| 9090 | 8465 | 17555 | 0 | 0 | 115 | 17440 | 110 | 191.95 | 179.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 32 |  |  | 84.4306 | 7833.5484 | 41.4517 | 3161.0003 | 120 | 174956.8 | 174836.8 | 9.9594 | 86.8398 | 171674.55 | 0 | 4062.25 | 780 |  | 65.2766 | 174836.8