## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 415 | 330 | 745 | 0 | 0 | 4 | 745 | 110 | 8.3 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 |  | 1 | 84.2 | 7280 | 41.968 | 3765.06 | -1440 | 6084.5 | 7524.5 | 10.1 | 86.0987 | 6174 | 0 | 10.5 | 100 |  | 87.0891 | 7524.5
2 | 145 | 660 | 805 | 0 | 0 | 4 | 805 | 110 | 3 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 84.4 | 7760 | 41.599 | 3333.33 | 480 | 8570.25 | 8090.25 | 10.05 | 86.1189 | 8551.4 | 0 | 18.85 | 0 |  | 93.6372 | 8090.25
3 | 335 | 515 | 850 | 0 | 0 | 0 | 850 | 110 | 7 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.75 | 8600 | 41.651 | 3394.17 | 840 | 9255 | 8415 | 9.9 | 86.708 | 9216.9 | 0 | 38.1 | 0 |  | 97.3958 | 8415
4 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 50 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.2 | 7280 | 41.699 | 3450.33 | -1320 | 3831 | 5151 | 10.1 | 86.0987 | 3814.65 | 0 | 16.35 | 0 |  | 59.6181 | 5151
5 | 425 | 125 | 550 | 0 | 0 | 5 | 550 | 110 | 8.15 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 83.9 | 6560 | 41.848 | 3624.66 | -720 | 4835 | 5555 | 10.1 | 86.7152 | 4832.6 | 0 | 62.4 | 60 |  | 64.294 | 5555
6 | 0 | 375 | 375 | 0 | 0 | 4 | 375 | 55 | 0 | 7.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.55 | 8120 | 41.383 | 3080.61 | 1560 | 5347.5 | 3787.5 | 10.1 | 85.3905 | 5032.8 | 0 | 314.7 | 0 |  | 43.8368 | 3787.5
7 | 615 | 735 | 1350 | 0 | 0 | 4 | 1350 | 110 | 13.75 | 15.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.15 | 7160 | 41.622 | 3360.24 | -960 | 12540 | 13500 | 10 | 87.0629 | 12519.5 | 0 | 20.5 | 0 |  | 156.25 | 13500
8 | 65 | 515 | 580 | 0 | 0 | 4 | 580 | 70 | 1.7 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.6 | 8240 | 41.891 | 3674.97 | 1080 | 6793 | 5713 | 9.85 | 87.455 | 6621.1 | 0 | 171.9 | 0 |  | 66.1227 | 5713
9 | 0 | 405 | 405 | 0 | 0 | 4 | 405 | 55 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.7 | 8480 | 41.2 | 2866.5 | 240 | 4553.25 | 4313.25 | 10.65 | 80.6962 | 4622.4 | 0 | 130.85 | 200 |  | 49.9219 | 4313.25
10 | 490 | 0 | 490 | 0 | 0 | 5 | 490 | 45 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 41.848 | 3624.66 | -960 | 3768.5 | 4728.5 | 9.65 | 89.9007 | 3522.4 | 0 | 246.1 | 0 |  | 54.728 | 4728.5
11 | 670 | 80 | 750 | 0 | 0 | 4 | 750 | 110 | 13.3 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.5 | 8000 | 42.099 | 3918.33 | 480 | 7980 | 7500 | 10 | 86.3459 | 7867.2 | 0 | 112.8 | 0 |  | 86.8056 | 7500
12 | 210 | 95 | 305 | 0 | 0 | 3 | 305 | 80 | 5.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.3 | 7520 | 41.165 | 2825.55 | -480 | 2600.5 | 3080.5 | 10.1 | 85.8952 | 2460.1 | 0 | 140.4 | 0 |  | 35.6539 | 3080.5
13 | 0 | 190 | 190 | 0 | 0 | 4 | 190 | 55 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 84.4 | 7760 | 40.402 | 1932.84 | 240 | 2235 | 1995 | 10.5 | 82.4281 | 2071.1 | 0 | 163.9 | 0 |  | 23.0903 | 1995
14 | 225 | 45 | 270 | 0 | 0 | 3 | 270 | 110 | 5.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84 | 6800 | 41.019 | 2654.73 | -960 | 3393.4468 | 2646 | 9.8 | 89.1569 | 3268.8 | 1707.4468 | 124.6468 | 0 |  | 30.625 | 2646
15 | 0 | 450 | 450 | 0 | 0 | 4 | 450 | 55 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.2 | 7280 | 40.9315 | 2552.355 | 480 | 5025 | 4545 | 10.1 | 86.0987 | 5082 | 0 | 13 | 70 |  | 52.6042 | 4545
16 | 485 | 75 | 560 | 0 | 0 | 4 | 560 | 110 | 10.8 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.35 | 7640 | 41.372 | 3067.74 | 360 | 5960 | 5600 | 10 | 86.6517 | 5792.75 | 0 | 167.25 | 0 |  | 64.8148 | 5600
17 | 385 | 130 | 515 | 0 | 0 | 3 | 515 | 110 | 8.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 85.1 | 9440 | 41.65 | 3393 | 1800 | 6924.25 | 5124.25 | 9.95 | 85.5717 | 6869.3 | 0 | 114.95 | 60 |  | 59.3084 | 5124.25
18 | 395 | 0 | 395 | 0 | 0 | 4 | 395 | 55 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.55 | 8120 | 40.87 | 2480.4 | -1320 | 2827.5 | 4147.5 | 10.5 | 82.1375 | 2847 | 0 | 40.5 | 60 |  | 48.0035 | 4147.5
19 | 220 | 95 | 315 | 0 | 0 | 4 | 315 | 100 | 5.9 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.6 | 8240 | 41.019 | 2654.73 | 120 | 3270 | 3150 | 10 | 86.1432 | 3212 | 0 | 118 | 60 |  | 36.4583 | 3150
20 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 40 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.55 | 8120 | 40.821 | 2423.07 | -120 | 2455.5 | 2575.5 | 10.1 | 85.3905 | 2445.5 | 0 | 70 | 60 |  | 29.809 | 2575.5
21 | 470 | 70 | 540 | 0 | 0 | 3 | 540 | 70 | 9.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.6 | 8240 | 41.45 | 3159 | 120 | 5574 | 5454 | 10.1 | 85.2903 | 5307.1 | 0 | 326.9 | 60 |  | 63.125 | 5454
22 | 590 | 205 | 795 | 0 | 0 | 3 | 795 | 110 | 11.3 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 83.9 | 6560 | 40.86 | 2468.7 | -1680 | 6270 | 7950 | 10 | 87.5823 | 6153.9 | 0 | 116.1 | 0 |  | 92.0139 | 7950
23 | 335 | 60 | 395 | 0 | 0 | 3 | 395 | 110 | 7.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.15 | 7160 | 41.3 | 2983.5 | 600 | 4589.5 | 3989.5 | 10.1 | 86.2009 | 4526 | 0 | 123.5 | 60 |  | 46.1748 | 3989.5
24 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 40 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 24 | 84 | 6800 | 40.57 | 2129.4 | -360 | 1876.5 | 2236.5 | 10.65 | 82.0411 | 1657.6 | 0 | 218.9 | 0 |  | 25.8854 | 2236.5
25 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 35 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84 | 6800 | 40.078 | 1553.76 | 0 | 1683 | 1683 | 10.2 | 85.6606 | 1540.3 | 0 | 142.7 | 0 |  | 19.4792 | 1683
26 | 310 | 30 | 340 | 0 | 0 | 3 | 340 | 110 | 7 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84.05 | 6920 | 41.138 | 2793.96 | 120 | 3554 | 3434 | 10.1 | 86.4059 | 3598.9 | 0 | 15.1 | 60 |  | 39.7454 | 3434
27 | 150 | 0 | 150 | 0 | 0 | 3 | 150 | 54 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.55 | 8120 | 40.572 | 2131.74 | 1200 | 2797.5 | 1597.5 | 10.65 | 80.9807 | 2628 | 0 | 169.5 | 0 |  | 18.4896 | 1597.5
28 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 55 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.4 | 7760 | 40.749 | 2338.83 | -360 | 1660 | 2020 | 10.1 | 85.6926 | 1627.9 | 0 | 32.1 | 0 |  | 23.3796 | 2020
29 | 430 | 75 | 505 | 0 | 0 | 4 | 505 | 90 | 9.95 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.4 | 7760 | 41.702 | 3453.84 | 0 | 4923.75 | 4923.75 | 9.75 | 88.7687 | 4935 | 0 | 48.75 | 60 |  | 56.9878 | 4923.75
30 | 300 | 0 | 300 | 0 | 0 | 3 | 300 | 40 | 7.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.65 | 8360 | 40.925 | 2544.75 | 600 | 3495 | 2895 | 9.65 | 89.1629 | 3204.6 | 0 | 290.4 | 0 |  | 33.5069 | 2895
| 8495 | 5770 | 14265 | 0 | 0 | 109 | 14156 | 110 | 188.7 | 123.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 30 |  |  | 84.3667 | 7680 | 41.2467 | 2921.1585 | -360 | 144672.4468 | 143325 | 10.0473 | 86.2097 | 142002.8 | 1707.4468 | 3579.6468 | 910 |  | 55.2951 | 143325