## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 230 | 230 | 0 | 0 | 4 | 230 | 50 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 84.3 | 7520 | 40.395 | 1924.65 | 360 | 2809.5 | 2449.5 | 10.65 | 81.4593 | 2592.6 | 0 | 216.9 | 0 |  | 28.3507 | 2449.5
2 | 475 | 0 | 475 | 0 | 0 | 4 | 475 | 55 | 9.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.65 | 8360 | 41.932 | 3722.94 | 840 | 5518.75 | 4678.75 | 9.85 | 87.3525 | 5482.3 | 0 | 36.45 | 0 |  | 54.1522 | 4678.75
3 | 520 | 65 | 585 | 0 | 0 | 4 | 585 | 110 | 11.3 | 1.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 3 | 84.3 | 7520 | 41.318 | 3004.56 | -840 | 4980.75 | 5820.75 | 9.95 | 87.1901 | 4955.8 | 0 | 24.95 | 0 |  | 67.3698 | 5820.75
4 | 315 | 0 | 315 | 0 | 0 | 3 | 315 | 50 | 7.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.1 | 7040 | 41.2415 | 2915.055 | -480 | 2717.25 | 3197.25 | 10.15 | 85.8781 | 2685.15 | 0 | 32.1 | 0 |  | 37.0052 | 3197.25
5 | 275 | 0 | 275 | 0 | 0 | 3 | 275 | 55 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.1 | 7040 | 41.208 | 2875.86 | 0 | 2777.5 | 2777.5 | 10.1 | 86.3032 | 2671.8 | 0 | 165.7 | 60 |  | 32.147 | 2777.5
6 | 405 | 120 | 525 | 0 | 0 | 3 | 525 | 110 | 8.8 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 84 | 6800 | 41.13 | 2784.6 | -240 | 5062.5 | 5302.5 | 10.1 | 86.5087 | 4968 | 0 | 94.5 | 0 |  | 61.3715 | 5302.5
7 | 480 | 0 | 480 | 0 | 0 | 4 | 480 | 55 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.2 | 7280 | 41.5 | 3217.5 | 480 | 5472 | 4992 | 10.4 | 83.6151 | 5572.2 | 0 | 4.8 | 105 |  | 57.7778 | 4992
8 | 410 | 240 | 650 | 0 | 0 | 3 | 650 | 110 | 8.4 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 8 | 84.2 | 7280 | 41.81 | 3580.2 | 0 | 6370 | 6370 | 9.8 | 88.7344 | 6230.8 | 0 | 139.2 | 0 |  | 73.7269 | 6370
9 | 0 | 270 | 270 | 0 | 0 | 4 | 270 | 55 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.2 | 7280 | 40.1445 | 1631.565 | 0 | 2700 | 2700 | 10 | 86.9597 | 2592 | 0 | 168 | 60 |  | 31.25 | 2700
10 | 455 | 0 | 455 | 0 | 0 | 3 | 455 | 55 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 84.35 | 7640 | 41.42 | 3123.9 | 360 | 4910 | 4550 | 10 | 86.6517 | 4847.2 | 0 | 62.8 | 0 |  | 52.662 | 4550
11 | 325 | 0 | 325 | 0 | 0 | 4 | 325 | 50 | 7.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 83.95 | 6680 | 41.6 | 3334.5 | -960 | 2290 | 3250 | 10 | 87.4779 | 2138.9 | 0 | 151.1 | 0 |  | 37.6157 | 3250
12 | 265 | 0 | 265 | 0 | 0 | 4 | 265 | 50 | 6.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 83.8 | 6320 | 41.27 | 2948.4 | -360 | 2290 | 2650 | 10 | 87.7919 | 2211.9 | 0 | 78.1 | 0 |  | 30.6713 | 2650
13 | 375 | 0 | 375 | 0 | 0 | 4 | 375 | 50 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.9 | 6560 | 41.55 | 3276 | 240 | 3952.5 | 3712.5 | 9.9 | 88.467 | 3744.4 | 0 | 208.1 | 0 |  | 42.9688 | 3712.5
14 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 50 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.3 | 7520 | 41.112 | 2763.54 | 960 | 3010 | 2050 | 10 | 86.7541 | 2890.8 | 0 | 119.2 | 0 |  | 23.7269 | 2050
15 | 0 | 245 | 245 | 0 | 0 | 3 | 245 | 50 | 0 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 83.8 | 6320 | 40.68 | 2258.1 | -1200 | 3276.5957 | 2450 | 10 | 87.7919 | 3255.8 | 2026.5957 | 80.7957 | 60 |  | 28.3565 | 2450
16 | 450 | 115 | 565 | 0 | 0 | 4 | 565 | 70 | 9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.3 | 7520 | 40.43 | 1965.6 | 1200 | 8071.3936 | 5706.5 | 10.1 | 85.8952 | 8042.4 | 1164.8936 | 88.9936 | 60 |  | 66.0475 | 5706.5
17 | 425 | 0 | 425 | 0 | 0 | 4 | 425 | 50 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.05 | 6920 | 40.079 | 1554.93 | -600 | 4747.4359 | 4250 | 10 | 87.2699 | 4620.3 | 1097.4359 | 127.1359 | 0 |  | 49.1898 | 4250
18 | 380 | 120 | 500 | 0 | 0 | 4 | 500 | 110 | 7.4 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 18 | 84.1 | 7040 | 40.603 | 2168.01 | 120 | 5070 | 4950 | 9.9 | 88.0467 | 5015.1 | 0 | 54.9 | 0 |  | 57.2917 | 4950
19 | 395 | 200 | 595 | 0 | 0 | 2 | 595 | 110 | 7.4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 83.75 | 6200 | 40.483 | 2027.61 | -840 | 5169.5 | 6009.5 | 10.1 | 87.0267 | 5112.25 | 0 | 117.25 | 60 |  | 69.5544 | 6009.5
20 | 160 | 85 | 245 | 0 | 0 | 4 | 245 | 70 | 4.6 | 2.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 84 | 6800 | 40.581 | 2142.27 | 600 | 3050 | 2450 | 10 | 87.3738 | 3002.35 | 0 | 47.65 | 0 |  | 28.3565 | 2450
21 | 230 | 0 | 230 | 0 | 0 | 4 | 230 | 50 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.35 | 7640 | 40.322 | 1839.24 | 840 | 3094 | 2254 | 9.8 | 88.4201 | 2912.7 | 0 | 181.3 | 0 |  | 26.088 | 2254
22 | 325 | 0 | 325 | 0 | 0 | 4 | 325 | 50 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.35 | 7640 | 40.34 | 1860.3 | 0 | 3185 | 3185 | 9.8 | 88.4201 | 3095.2 | 0 | 89.8 | 0 |  | 36.8634 | 3185
23 | 470 | 185 | 655 | 0 | 0 | 2 | 655 | 100 | 9.1 | 4.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 83.75 | 6200 | 40.45 | 1989 | -1440 | 4979 | 6419 | 9.8 | 89.6908 | 4949 | 0 | 30 | 0 |  | 74.294 | 6419
24 | 0 | 365 | 365 | 0 | 0 | 3 | 365 | 55 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.2 | 7280 | 40.752 | 2342.34 | 1080 | 4730 | 3650 | 10 | 86.9597 | 4584.4 | 0 | 145.6 | 0 |  | 42.2454 | 3650
25 | 515 | 445 | 960 | 0 | 0 | 4 | 960 | 110 | 11.4 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 83.7 | 6080 | 40.638 | 2208.96 | -1200 | 8736 | 9936 | 10.35 | 85.0265 | 8811.1 | 0 | 24.9 | 100 |  | 115 | 9936
26 | 355 | 165 | 520 | 0 | 0 | 0 | 520 | 110 | 6.9 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 83.85 | 6440 | 40.539 | 2093.13 | 360 | 7304.3077 | 5252 | 10.1 | 86.8188 | 7263.5 | 1692.3077 | 40.8077 | 0 |  | 60.787 | 5252
27 | 0 | 155 | 155 | 0 | 0 | 7 | 155 | 50 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.2 | 7280 | 40.628 | 2197.26 | 840 | 2359 | 1519 | 9.8 | 88.7344 | 2080.5 | 0 | 278.5 | 0 |  | 17.581 | 1519
28 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 35 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.4 | 7760 | 40.562 | 2120.04 | 480 | 2212.5 | 1732.5 | 9.9 | 87.4238 | 2153.55 | 0 | 118.95 | 60 |  | 20.0521 | 1732.5
29 | 395 | 120 | 515 | 0 | 0 | 3 | 515 | 110 | 7.6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 83.6 | 5840 | 40.37 | 1895.4 | -1920 | 3146.75 | 5066.75 | 9.8383 | 89.6634 | 3007.6 | 0 | 139.15 | 0 |  | 58.6429 | 5066.75
30 | 200 | 0 | 200 | 0 | 0 | 4 | 200 | 55 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.2 | 7280 | 40.5 | 2047.5 | 1440 | 3460 | 2020 | 10.1 | 86.0987 | 3394.5 | 0 | 125.5 | 60 |  | 23.3796 | 2020
| 8775 | 3330 | 12105 | 0 | 0 | 105 | 12000 | 110 | 184.8 | 72.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 19 |  |  | 84.0983 | 7036 | 40.8529 | 2460.432 | 120 | 127452.233 | 121351 | 10.0249 | 86.9535 | 124884.1 | 5981.233 | 3193.133 | 625 |  | 46.8175 | 121351