## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 430 | 0 | 430 | 0 | 0 | 4 | 430 | 55 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.15 | 7160 | 40.69 | 2269.8 | -120 | 4094 | 4214 | 9.8 | 88.8397 | 4052.8 | 0 | 41.2 | 0 |  | 48.7731 | 4214
2 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 35 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.3 | 7520 | 40.27 | 1778.4 | 360 | 1910 | 1550 | 10 | 86.7541 | 1861.5 | 0 | 78.5 | 30 |  | 17.9398 | 1550
3 | 0 | 220 | 220 | 0 | 0 | 3 | 220 | 55 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 84.65 | 8360 | 41.401 | 3101.67 | 840 | 3051 | 2211 | 10.05 | 85.6141 | 2831.25 | 0 | 219.75 | 0 |  | 25.5903 | 2211
4 | 330 | 0 | 330 | 0 | 0 | 4 | 330 | 55 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.4 | 7760 | 39.819 | 1250.73 | -600 | 2601 | 3201 | 9.7 | 89.2263 | 2430.9 | 0 | 170.1 | 0 |  | 37.0486 | 3201
5 | 440 | 180 | 620 | 0 | 0 | 4 | 620 | 110 | 8.5 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 83.75 | 6200 | 41.239 | 2912.13 | -1560 | 4578 | 6138 | 9.9 | 88.7849 | 4537.55 | 0 | 40.45 | 0 |  | 71.0417 | 6138
6 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.05 | 6920 | 40.711 | 2294.37 | 720 | 1518.75 | 798.75 | 10.65 | 81.9436 | 1461.6 | 0 | 77.15 | 20 |  | 9.2448 | 798.75
7 | 105 | 135 | 240 | 0 | 0 | 4 | 240 | 55 | 1.9 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.1 | 7040 | 41.426 | 3130.92 | 120 | 2472 | 2352 | 9.8 | 88.9452 | 2454.8 | 0 | 17.2 | 0 |  | 27.2222 | 2352
8 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.2 | 7280 | 40.649 | 2221.83 | 240 | 975 | 735 | 9.8 | 88.7344 | 934.4 | 0 | 40.6 | 0 |  | 8.5069 | 735
9 | 230 | 0 | 230 | 0 | 0 | 4 | 230 | 35 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.05 | 6920 | 41.89 | 3673.8 | -360 | 2055 | 2415 | 10.5 | 83.1142 | 1953.6 | 0 | 101.4 | 0 |  | 27.9514 | 2415
10 | 420 | 0 | 420 | 0 | 0 | 4 | 420 | 55 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 10 | 83.8 | 6320 | 41.499 | 3216.33 | -600 | 3642 | 4242 | 10.1 | 86.9226 | 3585.6 | 0 | 56.4 | 0 |  | 49.0972 | 4242
11 | 275 | 0 | 275 | 0 | 0 | 3 | 275 | 55 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 11 | 83.55 | 5720 | 41.65 | 3393 | -600 | 2177.5 | 2777.5 | 10.1 | 87.4456 | 2124.3 | 0 | 113.2 | 60 |  | 32.147 | 2777.5
12 | 130 | 0 | 130 | 0 | 0 | 5 | 130 | 35 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 12 | 83.9 | 6560 | 41.8345 | 3608.865 | 840 | 2114 | 1274 | 9.8 | 89.3697 | 1990.6 | 0 | 123.4 | 0 |  | 14.7454 | 1274
13 | 155 | 0 | 155 | 0 | 0 | 5 | 155 | 55 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | Εγκατάσταση νέων Μ/Σ τάσεως & εντάσεως στον Υ/Σ 150KV | 13 | 84.45 | 7880 | 41.698 | 3449.16 | 1320 | 2831.25 | 1511.25 | 9.75 | 88.6642 | 2744.8 | 0 | 86.45 | 0 |  | 17.4913 | 1511.25
14 | 175 | 380 | 555 | 0 | 0 | 4 | 555 | 110 | 3.3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.3 | 7520 | 41.47 | 3182.4 | -360 | 5245.5 | 5605.5 | 10.1 | 85.8952 | 5217 | 0 | 88.5 | 60 |  | 64.8785 | 5605.5
15 | 180 | 365 | 545 | 0 | 0 | 5 | 545 | 110 | 4.9 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84 | 6800 | 41.5 | 3217.5 | -720 | 4730 | 5450 | 10 | 87.3738 | 4773 | 0 | 17 | 60 |  | 63.0787 | 5450
16 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 55 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.15 | 7160 | 40.428 | 1963.26 | 360 | 1152 | 792 | 9.9 | 87.9423 | 984.2 | 0 | 227.8 | 60 |  | 9.1667 | 792
17 | 470 | 235 | 705 | 0 | 0 | 4 | 705 | 110 | 10.2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.05 | 6920 | 41.54 | 3264.3 | -240 | 6739.5 | 6979.5 | 9.9 | 88.1514 | 6719.2 | 0 | 80.3 | 60 |  | 80.7812 | 6979.5
18 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 55 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.15 | 7160 | 40.415 | 1948.05 | 240 | 864 | 624 | 9.6 | 90.6905 | 775.2 | 0 | 148.8 | 60 |  | 7.2222 | 624
19 | 115 | 285 | 400 | 0 | 0 | 5 | 400 | 100 | 3 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 83.95 | 6680 | 41.77 | 3533.4 | -480 | 3480 | 3960 | 9.9 | 88.3616 | 3394.5 | 0 | 145.5 | 60 |  | 45.8333 | 3960
20 | 0 | 305 | 305 | 0 | 0 | 5 | 305 | 55 | 0 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.65 | 5960 | 41.31 | 2995.2 | -720 | 2360.5 | 3080.5 | 10.1 | 87.2357 | 2237.95 | 0 | 182.55 | 60 |  | 35.6539 | 3080.5
21 | 115 | 360 | 475 | 0 | 0 | 4 | 475 | 110 | 2.5 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 83.7 | 6080 | 41.6 | 3334.5 | 120 | 4775 | 4655 | 9.8 | 89.7984 | 4562.5 | 0 | 272.5 | 60 |  | 53.8773 | 4655
22 | 0 | 170 | 170 | 0 | 0 | 4 | 170 | 36 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.95 | 6680 | 41.329 | 3017.43 | 600 | 2317 | 1717 | 10.1 | 86.6118 | 2360.6 | 0 | 16.4 | 60 |  | 19.8727 | 1717
23 | 140 | 55 | 195 | 0 | 0 | 4 | 195 | 70 | 3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.85 | 6440 | 41.266 | 2943.72 | -240 | 1671 | 1911 | 9.8 | 89.4765 | 1496.5 | 0 | 234.5 | 60 |  | 22.1181 | 1911
24 | 275 | 0 | 275 | 0 | 0 | 5 | 275 | 55 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 24 | 84.35 | 7640 | 41.75 | 3510 | 1200 | 3977.5 | 2777.5 | 10.1 | 85.7938 | 3890.9 | 0 | 146.6 | 60 |  | 32.147 | 2777.5
25 | 0 | 150 | 150 | 0 | 0 | 4 | 150 | 36 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 84.05 | 6920 | 41.348 | 3039.66 | -720 | 1107.8723 | 1530 | 10.2 | 85.5587 | 922.5 | 297.8723 | 245.3723 | 60 |  | 17.7083 | 1530
26 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.1 | 7040 | 40.292 | 1804.14 | 120 | 2427.9362 | 909 | 10.1 | 86.3032 | 2430.9 | 1398.9362 | 57.0362 | 60 |  | 10.5208 | 909
27 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.15 | 7160 | 39.2995 | 642.915 | 120 | 877.5 | 757.5 | 10.1 | 86.2009 | 759.2 | 0 | 178.3 | 60 |  | 8.7674 | 757.5
28 | 235 | 165 | 400 | 0 | 0 | 5 | 400 | 70 | 6.2 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 28 | 84 | 6800 | 41.402 | 3102.84 | -360 | 3720 | 4080 | 10.2 | 85.6606 | 3502.5 | 0 | 277.5 | 60 |  | 47.2222 | 4080
29 | 0 | 185 | 185 | 0 | 0 | 5 | 185 | 35 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.05 | 6920 | 41.031 | 2668.77 | 120 | 1988.5 | 1868.5 | 10.1 | 86.4059 | 1949.1 | 0 | 99.4 | 60 |  | 21.6262 | 1868.5
30 | 200 | 230 | 430 | 0 | 0 | 4 | 430 | 55 | 3.8 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84 | 6800 | 41.559 | 3286.53 | -120 | 4180 | 4300 | 10 | 87.3738 | 4212.25 | 0 | 27.75 | 60 |  | 49.7685 | 4300
31 | 70 | 275 | 345 | 0 | 0 | 4 | 345 | 110 | 1.3 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 31 | 83.6 | 5840 | 41.3 | 2983.5 | -960 | 2524.5 | 3484.5 | 10.1 | 87.3405 | 2423.6 | 0 | 160.9 | 60 |  | 40.3299 | 3484.5
| 4795 | 4005 | 8800 | 0 | 0 | 128 | 8672 | 110 | 107.5 | 92.6 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 29 | 26 |  |  | 84.0452 | 6908.3871 | 41.1415 | 2798.0361 | -1440 | 88157.8085 | 87901 | 9.9887 | 87.3783 | 85575.3 | 1696.8085 | 3772.5085 | 1190 |  | 32.8185 | 87901