## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 35 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84 | 6800 | 41.53 | 3252.6 | -240 | 1160 | 1400 | 10 | 87.3738 | 1000.1 | 0 | 159.9 | 0 |  | 16.2037 | 1400
2 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 35 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.35 | 7640 | 41.25 | 2925 | 840 | 2246.5 | 1406.5 | 9.7 | 89.3317 | 2168.2 | 0 | 78.3 | 0 |  | 16.2789 | 1406.5
3 | 110 | 0 | 110 | 0 | 0 | 3 | 110 | 35 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84 | 6800 | 41.35 | 3042 | -840 | 1202.1053 | 1100 | 10 | 87.3738 | 1196.25 | 942.1053 | 5.8553 | 0 |  | 12.7315 | 1100
4 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.3 | 7520 | 40.83 | 2433.6 | 720 | 1427 | 707 | 10.1 | 85.8952 | 1197.2 | 0 | 229.8 | 0 |  | 8.1829 | 707
5 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 55 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.3 | 7520 | 41.299 | 2982.33 | 0 | 2211.7447 | 1616 | 10.1 | 85.8952 | 2153.5 | 595.7447 | 58.2447 | 0 |  | 18.7037 | 1616
6 | 60 | 170 | 230 | 0 | 0 | 4 | 230 | 109 | 1.2 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 83.85 | 6440 | 41.728 | 3484.26 | -1080 | 1243 | 2323 | 10.1 | 86.8188 | 1239 | 0 | 24 | 20 |  | 26.8866 | 2323
7 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 55 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.1 | 7040 | 41.284 | 2964.78 | 600 | 2050 | 1450 | 10 | 87.1663 | 1868.8 | 0 | 181.2 | 0 |  | 16.7824 | 1450
8 | 190 | 0 | 190 | 0 | 0 | 4 | 190 | 50 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.35 | 7640 | 41.64 | 3381.3 | 600 | 2500 | 1900 | 10 | 86.6517 | 2438.2 | 0 | 91.8 | 30 |  | 21.9907 | 1900
9 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.3 | 7520 | 41.05 | 2691 | -120 | 839.5 | 959.5 | 10.1 | 85.8952 | 854.1 | 0 | 45.4 | 60 |  | 11.1053 | 959.5
10 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 54 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.05 | 6920 | 41.04 | 2679.3 | -600 | 1050 | 1650 | 10 | 87.2699 | 1036.75 | 0 | 73.25 | 60 |  | 19.0972 | 1650
11 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 35 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.25 | 7400 | 40.44 | 1977.3 | 480 | 1641.5 | 1161.5 | 10.1 | 85.9968 | 1401.6 | 0 | 239.9 | 0 |  | 13.4433 | 1161.5
12 | 150 | 0 | 150 | 0 | 0 | 4 | 150 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84 | 6800 | 40.279 | 1788.93 | -600 | 885 | 1485 | 9.9 | 88.2564 | 813.2 | 0 | 71.8 | 0 |  | 17.1875 | 1485
13 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 35 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.25 | 7400 | 41.12 | 2772.9 | 600 | 1761.5 | 1161.5 | 10.1 | 85.9968 | 1759.3 | 0 | 32.2 | 30 |  | 13.4433 | 1161.5
14 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 83.8 | 6320 | 40.7 | 2281.5 | -1080 | 1801.7798 | 959.5 | 10.1 | 86.9226 | 1657.1 | 1922.2798 | 144.6798 | 0 |  | 11.1053 | 959.5
15 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 83.8 | 6320 | 40.6 | 2164.5 | 0 | 3441.0691 | 685.75 | 10.55 | 83.215 | 3423.7 | 2755.3191 | 77.3691 | 60 |  | 7.9369 | 685.75
16 | 135 | 0 | 135 | 0 | 0 | 3 | 135 | 55 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 83.5 | 5600 | 41.117 | 2769.39 | -720 | 2542.4923 | 1437.75 | 10.65 | 83.0296 | 2569.6 | 1824.7423 | 32.8923 | 60 |  | 16.6406 | 1437.75
17 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 35 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.85 | 6440 | 40.89 | 2503.8 | 840 | 2034 | 1194 | 9.95 | 88.1276 | 1876.1 | 0 | 157.9 | 0 |  | 13.8194 | 1194
18 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 55 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 84.15 | 7160 | 40.81 | 2410.2 | 720 | 2134 | 1414 | 10.1 | 86.2009 | 2077.5 | 0 | 56.5 | 0 |  | 16.3657 | 1414
19 | 170 | 0 | 170 | 0 | 0 | 4 | 170 | 50 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 83.95 | 6680 | 40.808 | 2407.86 | -480 | 1237 | 1717 | 10.1 | 86.6118 | 1123.2 | 0 | 113.8 | 0 |  | 19.8727 | 1717
20 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 55 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.55 | 8120 | 40.532 | 2084.94 | 1440 | 2551 | 1111 | 10.1 | 85.3905 | 2547.7 | 0 | 63.3 | 60 |  | 12.8588 | 1111
21 | 55 | 0 | 55 | 0 | 0 | 3 | 55 | 36 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.3 | 7520 | 40.95 | 2574 | -600 | 2386.2692 | 555.5 | 10.1 | 85.8952 | 2343.3 | 2430.7692 | 42.9692 | 0 |  | 6.4294 | 555.5
22 | 65 | 35 | 100 | 0 | 0 | 4 | 100 | 70 | 1.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.25 | 7400 | 41.15 | 2808 | -120 | 880 | 1000 | 10 | 86.8568 | 803 | 0 | 77 | 0 |  | 11.5741 | 1000
23 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.3 | 7520 | 40.7 | 2281.5 | 120 | 928 | 808 | 10.1 | 85.8952 | 978.2 | 0 | 9.8 | 60 |  | 9.3519 | 808
24 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 35 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.5 | 8000 | 41 | 2632.5 | 480 | 1519.5 | 1039.5 | 9.9 | 87.2181 | 1330.35 | 0 | 189.15 | 0 |  | 12.0312 | 1039.5
25 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.8 | 8720 | 40.6508 | 2223.936 | 720 | 1512 | 792 | 9.9 | 86.6067 | 1394.3 | 0 | 117.7 | 0 |  | 9.1667 | 792
26 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 35 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.8 | 8720 | 40.707 | 2289.69 | 0 | 1399.25 | 1399.25 | 9.65 | 88.8504 | 1275.95 | 0 | 123.3 | 0 |  | 16.195 | 1399.25
27 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 55 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.5 | 8000 | 41.2 | 2866.5 | -720 | 1152 | 1872 | 9.6 | 89.9436 | 1041.9 | 0 | 110.1 | 0 |  | 21.6667 | 1872
28 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 83.75 | 6200 | 40.89 | 2503.8 | -1800 | 1236.7872 | 707 | 10.1 | 87.0267 | 1109.6 | 2329.7872 | 187.1872 | 60 |  | 8.1829 | 707
29 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 83.9 | 6560 | 40.521 | 2072.07 | 360 | 1010 | 650 | 10 | 87.5823 | 934.4 | 0 | 75.6 | 0 |  | 7.5231 | 650
| 3190 | 370 | 3560 | 0 | 0 | 106 | 3454 | 109 | 80.8 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 5 |  |  | 84.1655 | 7197.2414 | 40.9678 | 2594.8099 | -480 | 47982.9976 | 35662.25 | 10.0175 | 86.8789 | 45612.1 | 12800.7476 | 2870.8976 | 500 |  | 14.233 | 35662.25