## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 180 | 0 | 180 | 0 | 0 | 4 | 180 | 35 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.3 | 7520 | 41.05 | 2691 | 240 | 2013 | 1773 | 9.85 | 88.0753 | 1912.6 | 0 | 100.4 | 0 |  | 20.5208 | 1773
2 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 55 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.6 | 8240 | 41.24 | 2913.3 | 720 | 2670 | 1950 | 10 | 86.1432 | 2535.75 | 0 | 134.25 | 0 |  | 22.5694 | 1950
3 | 200 | 65 | 265 | 0 | 0 | 4 | 265 | 75 | 5.4 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 84.7 | 8480 | 41.801 | 3569.67 | 240 | 2890 | 2650 | 10 | 85.9415 | 2760 | 0 | 130 | 0 |  | 30.6713 | 2650
4 | 180 | 220 | 400 | 0 | 0 | 4 | 400 | 110 | 4 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84.3 | 7520 | 40.922 | 2541.24 | -960 | 2980 | 3940 | 9.85 | 88.0753 | 2832.4 | 0 | 147.6 | 0 |  | 45.6019 | 3940
5 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 55 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 83.8 | 6320 | 39.182 | 505.44 | -1200 | 1350 | 2550 | 10 | 87.7919 | 1343.2 | 0 | 6.8 | 0 |  | 29.5139 | 2550
6 | 195 | 35 | 230 | 0 | 0 | 4 | 230 | 110 | 5.1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 83.7 | 6080 | 40.611 | 2177.37 | -240 | 2083 | 2323 | 10.1 | 87.1311 | 2044 | 0 | 39 | 0 |  | 26.8866 | 2323
7 | 90 | 0 | 90 | 0 | 0 | 5 | 90 | 52 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84 | 6800 | 40.692 | 2272.14 | 720 | 1606.5 | 886.5 | 9.85 | 88.7044 | 1387 | 0 | 219.5 | 0 |  | 10.2604 | 886.5
8 | 150 | 0 | 150 | 0 | 0 | 4 | 150 | 35 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.4 | 7760 | 41.227 | 2898.09 | 960 | 2557.5 | 1597.5 | 10.65 | 81.2672 | 2533.1 | 0 | 84.4 | 60 |  | 18.4896 | 1597.5
9 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.65 | 8360 | 40.9 | 2515.5 | 600 | 1243.5 | 643.5 | 9.9 | 86.9113 | 1005.75 | 0 | 237.75 | 0 |  | 7.4479 | 643.5
10 | 105 | 0 | 105 | 0 | 0 | 5 | 105 | 35 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 40.92 | 2538.9 | -840 | 914.7145 | 1023.75 | 9.75 | 88.9786 | 645 | 730.9645 | 269.7145 | 0 |  | 11.849 | 1023.75
11 | 180 | 60 | 240 | 0 | 0 | 4 | 240 | 110 | 4.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.15 | 7160 | 41.547 | 3272.49 | -360 | 2016 | 2376 | 9.9 | 87.9423 | 1795.8 | 0 | 220.2 | 0 |  | 27.5 | 2376
12 | 150 | 55 | 205 | 0 | 0 | 4 | 205 | 110 | 3.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.2 | 7280 | 41.399 | 3099.33 | 120 | 2129 | 2009 | 9.8 | 88.7344 | 2107.5 | 0 | 21.5 | 0 |  | 23.2523 | 2009
13 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 55 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.8 | 6320 | 41.282 | 2962.44 | -960 | 1612.5 | 2572.5 | 10.5 | 83.6113 | 1512.3 | 0 | 160.2 | 60 |  | 29.7743 | 2572.5
14 | 45 | 60 | 105 | 0 | 0 | 4 | 105 | 70 | 1.2 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 83.85 | 6440 | 40.69 | 2269.8 | 120 | 1180.5 | 1060.5 | 10.1 | 86.8188 | 1065.8 | 0 | 144.7 | 30 |  | 12.2743 | 1060.5
15 | 165 | 0 | 165 | 0 | 0 | 5 | 165 | 35 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84 | 6800 | 41.17 | 2831.4 | 360 | 1977 | 1617 | 9.8 | 89.1569 | 1785 | 0 | 192 | 0 |  | 18.7153 | 1617
16 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.4 | 7760 | 40.88 | 2492.1 | 960 | 1869 | 909 | 10.1 | 85.6926 | 1591.4 | 0 | 277.6 | 0 |  | 10.5208 | 909
17 | 110 | 0 | 110 | 0 | 0 | 4 | 110 | 55 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480 | 40.703 | 2285.01 | 720 | 2406.6957 | 1078 | 9.8 | 87.6954 | 2058 | 608.6957 | 348.6957 | 0 |  | 12.4769 | 1078
18 | 110 | 130 | 240 | 0 | 0 | 4 | 240 | 70 | 2.5 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.5 | 8000 | 41.369 | 3064.23 | -480 | 2028 | 2508 | 10.45 | 82.6276 | 1773.9 | 0 | 314.1 | 60 |  | 29.0278 | 2508
19 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 40 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.5 | 8000 | 41.09 | 2737.8 | 0 | 2110 | 2110 | 10.55 | 81.8444 | 1785 | 0 | 425 | 100 |  | 24.4213 | 2110
20 | 210 | 0 | 210 | 0 | 0 | 5 | 210 | 40 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.5 | 8000 | 41.171 | 2832.57 | 0 | 2236.5 | 2236.5 | 10.65 | 81.0759 | 1825 | 0 | 471.5 | 60 |  | 25.8854 | 2236.5
21 | 195 | 0 | 195 | 0 | 0 | 4 | 195 | 88 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.4 | 7760 | 41.37 | 3065.4 | -240 | 1729.5 | 1969.5 | 10.1 | 85.6926 | 1531.8 | 0 | 197.7 | 0 |  | 22.7951 | 1969.5
22 | 220 | 0 | 220 | 0 | 0 | 4 | 220 | 55 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.3 | 7520 | 41.252 | 2927.34 | -240 | 1982 | 2222 | 10.1 | 85.8952 | 1832.3 | 0 | 209.7 | 60 |  | 25.7176 | 2222
23 | 235 | 95 | 330 | 0 | 0 | 4 | 330 | 70 | 5.7 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.3 | 7520 | 41.834 | 3608.28 | 0 | 3333 | 3333 | 10.1 | 85.8952 | 3328.8 | 0 | 64.2 | 60 |  | 38.5764 | 3333
24 | 205 | 95 | 300 | 0 | 0 | 4 | 300 | 70 | 5.4 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 24 | 84.4 | 7760 | 41.821 | 3593.07 | 240 | 3270 | 3030 | 10.1 | 85.6926 | 3022.2 | 0 | 307.8 | 60 |  | 35.0694 | 3030
25 | 0 | 285 | 285 | 0 | 0 | 4 | 285 | 55 | 0 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.6 | 8240 | 41.012 | 2646.54 | 480 | 3321.45 | 2841.45 | 9.97 | 86.4024 | 3225 | 0 | 96.45 | 0 |  | 32.8872 | 2841.45
26 | 420 | 50 | 470 | 0 | 0 | 3 | 470 | 110 | 9.8 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84.25 | 7400 | 41.389 | 3087.63 | -840 | 5105.7051 | 4817.5 | 10.25 | 84.7383 | 5137.65 | 1128.2051 | 28.0551 | 60 |  | 55.7581 | 4817.5
27 | 230 | 260 | 490 | 0 | 0 | 4 | 490 | 110 | 4.8 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 84.3 | 7520 | 41.782 | 3547.44 | 120 | 5069 | 4949 | 10.1 | 85.8952 | 4993.2 | 0 | 135.8 | 60 |  | 57.2801 | 4949
28 | 320 | 0 | 320 | 0 | 0 | 3 | 320 | 55 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.35 | 7640 | 40.937 | 2558.79 | 120 | 3352 | 3232 | 10.1 | 85.7938 | 3285 | 0 | 127 | 60 |  | 37.4074 | 3232
29 | 280 | 0 | 280 | 0 | 0 | 5 | 280 | 45 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.05 | 6920 | 40.449 | 1987.83 | -720 | 2108 | 2828 | 10.1 | 86.4059 | 1971 | 0 | 137 | 0 |  | 32.7315 | 2828
30 | 245 | 0 | 245 | 0 | 0 | 4 | 245 | 40 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 84.55 | 8120 | 40.12 | 1602.9 | 1200 | 3674.5 | 2474.5 | 10.1 | 85.3905 | 3445.6 | 0 | 228.9 | 0 |  | 28.64 | 2474.5
| 5380 | 1500 | 6880 | 0 | 0 | 122 | 6758 | 110 | 129.3 | 36.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 17 |  |  | 84.295 | 7508 | 41.0604 | 2703.168 | 840 | 72818.5652 | 69510.7 | 10.1033 | 85.8773 | 68071.05 | 2467.8652 | 5477.5152 | 730 |  | 26.8174 | 69510.7