## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 840 | 840 | 0 | 0 | 2 | 840 | 55 | 0 | 19.33 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 85 | 9200 | 41.569 | 3298.23 | 0 | 8274 | 8274 | 9.85 | 86.6415 | 7965.25 | 0 | 308.75 | 0 |  | 95.7639 | 8274
2 | 0 | 760 | 760 | 0 | 0 | 2 | 760 | 40 | 0 | 20.22 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 83.6 | 5840 | 41.421 | 3125.07 | -3360 | 4506 | 7866 | 10.35 | 85.2309 | 4416.5 | 0 | 149.5 | 60 |  | 91.0417 | 7866
3 | 0 | 780 | 780 | 0 | 0 | 3 | 780 | 40 | 0 | 19.1 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 3 | 83.7 | 6080 | 41.652 | 3395.34 | 240 | 8469 | 8229 | 10.55 | 83.4146 | 8560.05 | 0 | 58.95 | 150 |  | 95.2431 | 8229
4 | 610 | 195 | 805 | 0 | 0 | 4 | 805 | 80 | 14.2 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 83.5 | 5600 | 41.542 | 3266.64 | -480 | 7650.5 | 8130.5 | 10.1 | 87.551 | 7613.9 | 0 | 36.6 | 0 |  | 94.103 | 8130.5
5 | 155 | 570 | 725 | 0 | 0 | 5 | 725 | 90 | 3.7 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 5 | 84.85 | 8840 | 40.92 | 2538.9 | 3240 | 10562.5 | 7322.5 | 10.1 | 84.7927 | 10575 | 0 | 47.5 | 60 |  | 84.7512 | 7322.5
6 | 60 | 805 | 865 | 0 | 0 | 5 | 865 | 80 | 1.5 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.8 | 8720 | 41.501 | 3218.67 | -120 | 8616.5 | 8736.5 | 10.1 | 84.8917 | 8614 | 0 | 12.5 | 10 |  | 101.1169 | 8736.5
7 | 165 | 800 | 965 | 0 | 0 | 4 | 965 | 80 | 4.2 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84 | 6800 | 41.7515 | 3511.755 | -1920 | 7585.25 | 9505.25 | 9.85 | 88.7044 | 7469.5 | 0 | 115.75 | 0 |  | 110.0145 | 9505.25
8 | 0 | 760 | 760 | 0 | 0 | 4 | 760 | 55 | 0 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 84.5 | 8000 | 41.5 | 3217.5 | 1200 | 8952 | 7752 | 10.2 | 84.6528 | 9000 | 0 | 12 | 60 |  | 89.7222 | 7752
9 | 180 | 670 | 850 | 0 | 0 | 5 | 850 | 90 | 4.55 | 15.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 83.75 | 6200 | 41.45 | 3159 | -1800 | 6700 | 8500 | 10 | 87.897 | 6645 | 0 | 55 | 0 |  | 98.3796 | 8500
10 | 70 | 755 | 825 | 0 | 0 | 4 | 825 | 70 | 1.4 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84 | 6800 | 41.75 | 3510 | 600 | 8932.5 | 8332.5 | 10.1 | 86.5087 | 8760 | 0 | 172.5 | 0 |  | 96.441 | 8332.5
11 | 605 | 15 | 620 | 0 | 0 | 4 | 620 | 80 | 13.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.4 | 7760 | 41.35 | 3042 | 960 | 7222 | 6262 | 10.1 | 85.6926 | 7080 | 0 | 142 | 0 |  | 72.4769 | 6262
12 | 645 | 120 | 765 | 0 | 0 | 4 | 765 | 80 | 14.25 | 3.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.4 | 7760 | 41.98 | 3779.1 | 0 | 7650 | 7650 | 10 | 86.5495 | 7530 | 0 | 120 | 0 |  | 88.5417 | 7650
13 | 570 | 165 | 735 | 0 | 0 | 4 | 735 | 80 | 13.4 | 3.899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.05 | 6920 | 42.031 | 3838.77 | -840 | 6510 | 7350 | 10 | 87.2699 | 6453.2 | 0 | 116.8 | 60 |  | 85.0694 | 7350
14 | 540 | 135 | 675 | 0 | 0 | 4 | 675 | 80 | 12.7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84 | 6800 | 42.001 | 3803.67 | -120 | 6697.5 | 6817.5 | 10.1 | 86.5087 | 6475.1 | 0 | 222.4 | 0 |  | 78.9062 | 6817.5
15 | 180 | 520 | 700 | 0 | 0 | 3 | 700 | 85 | 4.6 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 15 | 84.05 | 6920 | 41.9 | 3685.5 | 120 | 7295 | 7175 | 10.25 | 85.1414 | 7345.7 | 0 | 9.3 | 60 |  | 83.044 | 7175
16 | 580 | 155 | 735 | 0 | 0 | 3 | 735 | 110 | 12.7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 16 | 84.4 | 7760 | 41.967 | 3763.89 | 840 | 8116.5 | 7276.5 | 9.9 | 87.4238 | 8002.5 | 0 | 114 | 0 |  | 84.2188 | 7276.5
17 | 235 | 895 | 1130 | 0 | 0 | 3 | 1130 | 100 | 4.9 | 18.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 85 | 9200 | 42.151 | 3979.17 | 1440 | 12853 | 11413 | 10.1 | 84.4969 | 12949.09 | 0 | 3.91 | 100 |  | 132.0949 | 11413
18 | 620 | 105 | 725 | 0 | 0 | 3 | 725 | 100 | 12.5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.35 | 7640 | 41.399 | 3099.33 | -1560 | 5762.5 | 7322.5 | 10.1 | 85.7938 | 5606.4 | 0 | 156.1 | 0 |  | 84.7512 | 7322.5
19 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 55 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.45 | 7880 | 41.52 | 3240.9 | 240 | 5635.5 | 5395.5 | 9.9 | 87.3208 | 5572.5 | 0 | 63 | 0 |  | 62.4479 | 5395.5
20 | 520 | 155 | 675 | 0 | 0 | 2 | 675 | 80 | 12.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 20 | 84.1 | 7040 | 41.981 | 3780.27 | -840 | 5977.5 | 6817.5 | 10.1 | 86.3032 | 5937.65 | 0 | 39.85 | 0 |  | 78.9062 | 6817.5
21 | 135 | 465 | 600 | 0 | 0 | 4 | 600 | 90 | 2.8 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 83.9 | 6560 | 42.051 | 3862.17 | -480 | 5520 | 6000 | 10 | 87.5823 | 5438.5 | 0 | 81.5 | 0 |  | 69.4444 | 6000
22 | 80 | 525 | 605 | 0 | 0 | 4 | 605 | 90 | 1.75 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 83.8 | 6320 | 42.061 | 3873.87 | -240 | 5870.5 | 6110.5 | 10.1 | 86.9226 | 5897.51 | 0 | 32.99 | 60 |  | 70.7234 | 6110.5
23 | 105 | 535 | 640 | 0 | 0 | 4 | 640 | 90 | 2.45 | 12.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 23 | 84 | 6800 | 42.0715 | 3886.155 | 480 | 6816 | 6336 | 9.9 | 88.2564 | 6786.95 | 0 | 29.05 | 0 |  | 73.3333 | 6336
24 | 80 | 505 | 585 | 0 | 0 | 4 | 585 | 90 | 1.7 | 10.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.05 | 6920 | 41.811 | 3581.37 | 120 | 6028.5 | 5908.5 | 10.1 | 86.4059 | 5956.9 | 0 | 71.6 | 0 |  | 68.3854 | 5908.5
25 | 535 | 165 | 700 | 0 | 0 | 3 | 700 | 90 | 12.1 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.5 | 8000 | 42.029 | 3836.43 | 1080 | 8010 | 6930 | 9.9 | 87.2181 | 7972.8 | 0 | 37.2 | 0 |  | 80.2083 | 6930
26 | 450 | 220 | 670 | 0 | 0 | 4 | 670 | 90 | 9.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 26 | 84 | 6800 | 41.998 | 3800.16 | -1200 | 5600.5 | 6800.5 | 10.15 | 86.0826 | 5641.35 | 0 | 19.15 | 60 |  | 78.7095 | 6800.5
27 | 560 | 145 | 705 | 0 | 0 | 3 | 705 | 110 | 11.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 83.75 | 6200 | 42.04 | 3849.3 | -600 | 6450 | 7050 | 10 | 87.897 | 6153.9 | 0 | 296.1 | 0 |  | 81.5972 | 7050
28 | 515 | 70 | 585 | 0 | 0 | 3 | 585 | 55 | 10.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.1 | 7040 | 41.143 | 2799.81 | 840 | 6800 | 5960 | 10.188 | 85.5575 | 6840 | 0 | 20 | 60 |  | 68.9815 | 5960
29 | 525 | 145 | 670 | 0 | 0 | 3 | 670 | 100 | 11.3 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.05 | 6920 | 41.881 | 3663.27 | -120 | 6446 | 6566 | 9.8 | 89.0509 | 6256.1 | 0 | 189.9 | 0 |  | 75.9954 | 6566
30 | 120 | 515 | 635 | 0 | 0 | 3 | 635 | 90 | 2.9 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.4 | 7760 | 42.03 | 3837.6 | 840 | 7190 | 6350 | 10 | 86.5495 | 7021.5 | 0 | 168.5 | 0 |  | 73.4954 | 6350
| 9385 | 12490 | 21875 | 0 | 0 | 107 | 21768 | 110 | 208.9 | 287.25 | 58.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 36 |  |  | 84.1817 | 7236 | 41.7484 | 3508.128 | -1440 | 218699.25 | 220139.25 | 10.0635 | 86.4485 | 216536.85 | 0 | 2902.4 | 740 |  | 84.9303 | 220139.25