## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 345 | 255 | 600 | 0 | 0 | 3 | 600 | 90 | 7.7 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.2 | 7280 | 41.1 | 2749.5 | -480 | 5640 | 6120 | 10.2 | 85.2546 | 5663 | 0 | 37 | 60 |  | 70.8333 | 6120
2 | 615 | 0 | 615 | 0 | 0 | 4 | 615 | 50 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.45 | 7880 | 41.603 | 3338.01 | 600 | 6627 | 6027 | 9.8 | 88.2118 | 6349.2 | 0 | 307.8 | 30 |  | 69.7569 | 6027
3 | 0 | 535 | 535 | 0 | 0 | 3 | 535 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 3 | 83.9 | 6560 | 41.449 | 3157.83 | -1320 | 4083.5 | 5403.5 | 10.1 | 86.7152 | 4073.4 | 0 | 40.1 | 30 |  | 62.5405 | 5403.5
4 | 640 | 10 | 650 | 0 | 0 | 4 | 650 | 50 | 12.75 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.3 | 7520 | 41.621 | 3359.07 | 960 | 7330 | 6370 | 9.8 | 88.5246 | 7081.8 | 0 | 248.2 | 0 |  | 73.7269 | 6370
5 | 660 | 0 | 660 | 0 | 0 | 4 | 660 | 50 | 13.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.05 | 6920 | 41.799 | 3567.33 | -600 | 5934 | 6534 | 9.9 | 88.1514 | 5950 | 0 | 14 | 30 |  | 75.625 | 6534
6 | 660 | 0 | 660 | 0 | 0 | 3 | 660 | 50 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.25 | 7400 | 41.48 | 3194.1 | 480 | 7014 | 6534 | 9.9 | 87.7341 | 6759.8 | 0 | 284.2 | 30 |  | 75.625 | 6534
7 | 690 | 0 | 690 | 0 | 0 | 2 | 690 | 50 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.2 | 7280 | 41.44 | 3147.3 | -120 | 6711 | 6831 | 9.9 | 87.8381 | 6465.6 | 0 | 275.4 | 30 |  | 79.0625 | 6831
8 | 0 | 695 | 695 | 0 | 0 | 4 | 695 | 50 | 0 | 13.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.15 | 7160 | 41.55 | 3276 | -120 | 6760.5 | 6880.5 | 9.9 | 87.9423 | 6759.8 | 0 | 30.7 | 30 |  | 79.6354 | 6880.5
9 | 650 | 5 | 655 | 0 | 0 | 3 | 655 | 50 | 13.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.25 | 7400 | 41.848 | 3624.66 | 240 | 6659 | 6419 | 9.8 | 88.6294 | 6423.2 | 0 | 235.8 | 0 |  | 74.294 | 6419
10 | 55 | 610 | 665 | 0 | 0 | 4 | 665 | 50 | 1.3 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.5 | 8000 | 41.889 | 3672.63 | 600 | 7316.5 | 6716.5 | 10.1 | 85.491 | 7300 | 0 | 76.5 | 60 |  | 77.7373 | 6716.5
11 | 615 | 40 | 655 | 0 | 0 | 4 | 655 | 100 | 12.3 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.8 | 8720 | 42.086 | 3903.12 | 720 | 7139 | 6419 | 9.8 | 87.4905 | 6748.8 | 0 | 390.2 | 0 |  | 74.294 | 6419
12 | 15 | 650 | 665 | 0 | 0 | 4 | 665 | 50 | 0.4 | 12.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.6 | 8240 | 41.651 | 3394.17 | -480 | 6236.5 | 6716.5 | 10.1 | 85.2903 | 6180 | 0 | 56.5 | 0 |  | 77.7373 | 6716.5
13 | 640 | 120 | 760 | 0 | 0 | 0 | 760 | 85 | 13.38 | 2.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.5 | 8000 | 41.85 | 3627 | -240 | 7132 | 7372 | 9.7 | 89.0164 | 6710.4 | 0 | 421.6 | 0 |  | 85.3241 | 7372
14 | 105 | 635 | 740 | 0 | 0 | 8 | 740 | 85 | 3.02 | 14.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.5 | 8000 | 41.7 | 3451.5 | 0 | 7622 | 7622 | 10.3 | 83.831 | 7657.5 | 0 | 4.5 | 40 |  | 88.2176 | 7622
15 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 13.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.3 | 7520 | 41.23 | 2901.6 | -480 | 6388 | 6868 | 10.1 | 85.8952 | 6205 | 0 | 183 | 0 |  | 79.4907 | 6868
16 | 760 | 0 | 760 | 0 | 0 | 4 | 760 | 50 | 15.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 83.65 | 5960 | 41.8 | 3568.5 | -1560 | 5888 | 7448 | 9.8 | 89.9062 | 5853.4 | 0 | 94.6 | 60 |  | 86.2037 | 7448
17 | 295 | 385 | 680 | 0 | 0 | 4 | 680 | 50 | 5.75 | 8.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.15 | 7160 | 41.9 | 3685.5 | 1200 | 8000 | 6800 | 10 | 87.0629 | 7972.5 | 0 | 27.5 | 0 |  | 78.7037 | 6800
18 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 13.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4 | 0 | 2 | 0 | ΒΛΑΒΗ ΣΤΟ ΣΥΣΤΗΜΑ ΦΡΕΝΩΝ | 18 | 84.4 | 7760 | 41.6 | 3334.5 | 600 | 7332 | 6732 | 9.9 | 87.4238 | 7241.6 | 0 | 90.4 | 0 |  | 77.9167 | 6732
19 | 665 | 0 | 665 | 0 | 0 | 4 | 665 | 50 | 13.1 | 0 | 0 | 0 | 3.7 | 0 | 0 | 0 | 24 | 0 | 3 | 0 | ΒΛΑΒΗ ΣΤΟ ΣΥΣΤΗΜΑ ΦΡΕΝΩΝ | 19 | 84.75 | 8600 | 41.18 | 2843.1 | 840 | 7290.5 | 6450.5 | 9.7 | 88.4958 | 7137.45 | 0 | 153.05 | 0 |  | 74.6586 | 6450.5
20 | 695 | 0 | 695 | 0 | 0 | 2 | 695 | 50 | 13.8 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 0 | ΒΛΑΒΗ ΣΤΟ ΣΥΣΤΗΜΑ ΦΡΕΝΩΝ | 20 | 85 | 9200 | 41.15 | 2808 | 600 | 7272 | 6672 | 9.6 | 88.8978 | 6976.8 | 0 | 295.2 | 0 |  | 77.2222 | 6672
21 | 0 | 650 | 650 | 0 | 0 | 2 | 650 | 50 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 83.8 | 6320 | 40.8 | 2398.5 | -2880 | 3685 | 6565 | 10.1 | 86.9226 | 3693.6 | 0 | 51.4 | 60 |  | 75.9838 | 6565
22 | 0 | 795 | 795 | 0 | 0 | 3 | 795 | 50 | 0 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.4 | 7760 | 41.8 | 3568.5 | 1440 | 9231 | 7791 | 9.8 | 88.3158 | 9212.6 | 0 | 18.4 | 0 |  | 90.1736 | 7791
23 | 0 | 695 | 695 | 0 | 0 | 3 | 695 | 50 | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 84.4 | 7760 | 41.75 | 3510 | 0 | 6741.5 | 6741.5 | 9.7 | 89.2263 | 6745.2 | 0 | 11.3 | 15 |  | 78.0266 | 6741.5
24 | 0 | 735 | 735 | 0 | 0 | 4 | 735 | 55 | 0 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 24 | 84.7 | 8480 | 42 | 3802.5 | 720 | 7776 | 7056 | 9.6 | 89.5223 | 7676 | 0 | 100 | 0 |  | 81.6667 | 7056
25 | 120 | 590 | 710 | 0 | 0 | 4 | 710 | 105 | 2.6 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 25 | 85 | 9200 | 42 | 3802.5 | 720 | 7678 | 6958 | 9.8 | 87.0835 | 7365.7 | 0 | 312.3 | 0 |  | 80.5324 | 6958
26 | 10 | 705 | 715 | 0 | 0 | 3 | 715 | 50 | 0.2 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.75 | 8600 | 42.001 | 3803.67 | -600 | 6478.5 | 7078.5 | 9.9 | 86.708 | 6278 | 0 | 260.5 | 60 |  | 81.9271 | 7078.5
27 | 0 | 690 | 690 | 0 | 0 | 4 | 690 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.1 | 7040 | 41.87 | 3650.4 | -1560 | 5271 | 6831 | 9.9 | 88.0467 | 5175.9 | 0 | 125.1 | 30 |  | 79.0625 | 6831
28 | 0 | 705 | 705 | 0 | 0 | 4 | 705 | 50 | 0 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.3 | 7520 | 41.97 | 3767.4 | 480 | 7600.5 | 7120.5 | 10.1 | 85.8952 | 7597.5 | 0 | 63 | 60 |  | 82.4132 | 7120.5
29 | 0 | 725 | 725 | 0 | 0 | 3 | 725 | 50 | 0 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.75 | 8600 | 41.681 | 3429.27 | 1080 | 8330 | 7250 | 10 | 85.8409 | 8205 | 0 | 125 | 0 |  | 83.912 | 7250
30 | 0 | 740 | 740 | 0 | 0 | 5 | 740 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 83.95 | 6680 | 42.102 | 3921.84 | -1920 | 5517 | 7437 | 10.05 | 87.0427 | 5371.45 | 0 | 145.55 | 0 |  | 86.0764 | 7437
31 | 555 | 115 | 670 | 0 | 0 | 4 | 670 | 100 | 12 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 84.1 | 7040 | 42.102 | 3921.84 | 360 | 7227.5 | 6867.5 | 10.25 | 85.0403 | 7156.8 | 0 | 70.7 | 0 |  | 79.485 | 6867.5
| 10150 | 11085 | 21235 | 0 | 0 | 111 | 21124 | 105 | 206.6 | 226.2 | 2 | 0 | 3.7 | 0 | 0 | 0 | 47.4 | 0 | 33 | 36 |  |  | 84.3597 | 7663.2258 | 41.6775 | 3425.1561 | -720 | 209911.5 | 210631.5 | 9.9191 | 87.3387 | 205987 | 0 | 4549.5 | 625 |  | 78.6408 | 210631.5