## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 685 | 25 | 710 | 0 | 0 | 3 | 710 | 50 | 13.3 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.1 | 7040 | 41.788 | 3554.46 | 0 | 6958 | 6958 | 9.8 | 88.9452 | 6855.2 | 0 | 102.8 | 0 |  | 80.5324 | 6958
2 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 50 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 84.5 | 8000 | 41.492 | 3208.14 | 960 | 7477 | 6517 | 9.8 | 88.108 | 7175.7 | 0 | 301.3 | 0 |  | 75.4282 | 6517
3 | 0 | 685 | 685 | 0 | 0 | 4 | 685 | 50 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 3 | 84.5 | 8000 | 41.778 | 3542.76 | 0 | 7055.5 | 7055.5 | 10.3 | 83.831 | 6847.4 | 0 | 208.1 | 0 |  | 81.6609 | 7055.5
4 | 700 | 0 | 700 | 0 | 0 | 4 | 700 | 50 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.85 | 8840 | 41.961 | 3756.87 | 840 | 7665 | 6825 | 9.75 | 87.8365 | 7422.8 | 0 | 242.2 | 0 |  | 78.9931 | 6825
5 | 715 | 0 | 715 | 0 | 0 | 4 | 715 | 50 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.95 | 9080 | 41.752 | 3512.34 | 240 | 7211.25 | 6971.25 | 9.75 | 87.632 | 7117.5 | 0 | 93.75 | 0 |  | 80.6858 | 6971.25
6 | 680 | 55 | 735 | 0 | 0 | 3 | 735 | 50 | 13.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 6 | 85.1 | 9440 | 41.552 | 3278.34 | 360 | 7545.5 | 7185.5 | 9.7762 | 87.0931 | 7185 | 0 | 360.5 | 0 |  | 83.1655 | 7185.5
7 | 695 | 0 | 695 | 0 | 0 | 4 | 695 | 50 | 14.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.6 | 8240 | 41.648 | 3390.66 | -1200 | 5680.5 | 6880.5 | 9.9 | 87.0133 | 5632.5 | 0 | 48 | 0 |  | 79.6354 | 6880.5
8 | 25 | 640 | 665 | 0 | 0 | 3 | 665 | 50 | 0.3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 83.8 | 6320 | 41.37 | 3065.4 | -1920 | 4796.5 | 6716.5 | 10.1 | 86.9226 | 4605 | 0 | 191.5 | 0 |  | 77.7373 | 6716.5
9 | 690 | 0 | 690 | 0 | 0 | 4 | 690 | 50 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.15 | 7160 | 41.951 | 3745.17 | 840 | 7740 | 6900 | 10 | 87.0629 | 7584.7 | 0 | 155.3 | 0 |  | 79.8611 | 6900
10 | 730 | 0 | 730 | 0 | 0 | 3 | 730 | 50 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.75 | 8600 | 41.888 | 3671.46 | 1440 | 8594 | 7154 | 9.8 | 87.5928 | 8252.15 | 0 | 341.85 | 0 |  | 82.8009 | 7154
11 | 720 | 220 | 940 | 0 | 0 | 4 | 940 | 85 | 16.2 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.25 | 7400 | 41.801 | 3569.67 | -1200 | 8059 | 9259 | 9.85 | 88.1795 | 7897.3 | 0 | 161.7 | 0 |  | 107.1644 | 9259
12 | 725 | 0 | 725 | 0 | 0 | 4 | 725 | 50 | 14.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.4 | 7760 | 41.7915 | 3558.555 | 360 | 7537.5 | 7177.5 | 9.9 | 87.4238 | 7350.48 | 0 | 187.02 | 0 |  | 83.0729 | 7177.5
13 | 575 | 0 | 575 | 0 | 0 | 4 | 575 | 50 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.7 | 6080 | 41.369 | 3064.23 | -1680 | 5464.2876 | 5807.5 | 10.1 | 87.1311 | 5320.6 | 1336.7876 | 143.6876 | 0 |  | 67.2164 | 5807.5
14 | 630 | 0 | 630 | 0 | 0 | 3 | 630 | 50 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.05 | 6920 | 41.67 | 3416.4 | 840 | 8632.228 | 6300 | 10 | 87.2699 | 8364.3 | 1492.228 | 267.928 | 0 |  | 72.9167 | 6300
15 | 370 | 250 | 620 | 0 | 0 | 4 | 620 | 50 | 7.5 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 15 | 84.3 | 7520 | 41.6815 | 3429.855 | 600 | 6707 | 6107 | 9.85 | 88.0753 | 6420.6 | 0 | 286.4 | 0 |  | 70.6829 | 6107
16 | 0 | 725 | 725 | 0 | 0 | 4 | 725 | 55 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.1 | 7040 | 42 | 3802.5 | -480 | 6842.5 | 7322.5 | 10.1 | 86.3032 | 6793.25 | 0 | 49.25 | 0 |  | 84.7512 | 7322.5
17 | 335 | 440 | 775 | 0 | 0 | 3 | 775 | 54 | 6.4 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.3 | 7520 | 41.688 | 3437.46 | 480 | 8307.5 | 7827.5 | 10.1 | 85.8952 | 8158.15 | 0 | 209.35 | 60 |  | 90.5961 | 7827.5
18 | 565 | 0 | 565 | 0 | 0 | 4 | 565 | 50 | 11.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.75 | 8600 | 41.3 | 2983.5 | 1080 | 6730 | 5650 | 10 | 85.8409 | 6421.9 | 0 | 308.1 | 0 |  | 65.3935 | 5650
19 | 620 | 0 | 620 | 0 | 0 | 4 | 620 | 50 | 12.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.8 | 8720 | 41.351 | 3043.17 | 120 | 6320 | 6200 | 10 | 85.7407 | 6175.8 | 0 | 144.2 | 0 |  | 71.7593 | 6200
20 | 10 | 580 | 590 | 0 | 0 | 4 | 590 | 50 | 0.25 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.7 | 8480 | 41.449 | 3157.83 | -240 | 5660 | 5900 | 10 | 85.9415 | 5564.8 | 0 | 95.2 | 0 |  | 68.287 | 5900
21 | 515 | 60 | 575 | 0 | 0 | 4 | 575 | 90 | 11 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 83.7 | 6080 | 41.848 | 3624.66 | -2400 | 6810.733 | 5750 | 10 | 88.0024 | 6697 | 3460.733 | 113.733 | 0 |  | 66.5509 | 5750
22 | 600 | 0 | 600 | 0 | 0 | 4 | 600 | 50 | 12.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 2 | 0 | Αποκ. Βλ. κυκλ. Ρ.Σ. Μον. ΝοΙΙ | 22 | 83.65 | 5960 | 41.65 | 3393 | -120 | 5880 | 6000 | 10 | 88.108 | 5788.9 | 0 | 91.1 | 0 |  | 69.4444 | 6000
23 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 50 | 12.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 83.8 | 6320 | 42.001 | 3803.67 | 360 | 5973.5 | 5613.5 | 10.3 | 85.2348 | 5837.4 | 0 | 136.1 | 0 |  | 64.9711 | 5613.5
24 | 200 | 0 | 200 | 0 | 0 | 3 | 200 | 45 | 4.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 24 | 84.5 | 8000 | 40.1 | 1579.5 | 1680 | 8159.3814 | 2000 | 10 | 86.3459 | 8095.86 | 4479.3814 | 63.5214 | 0 |  | 23.1481 | 2000
25 | 555 | 0 | 555 | 0 | 0 | 4 | 555 | 54 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.8 | 8720 | 41 | 2632.5 | 720 | 6186.75 | 5466.75 | 9.85 | 87.0463 | 5985 | 0 | 201.75 | 0 |  | 63.2726 | 5466.75
26 | 0 | 545 | 545 | 0 | 0 | 3 | 545 | 50 | 0 | 12.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.7 | 8480 | 41.75 | 3510 | -240 | 5369.5745 | 5450 | 10 | 85.9415 | 5312.45 | 159.5745 | 57.1245 | 0 |  | 63.0787 | 5450
27 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 50 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.55 | 8120 | 42 | 3802.5 | -360 | 4736 | 5096 | 9.8 | 88.0045 | 4492.25 | 0 | 243.75 | 0 |  | 58.9815 | 5096
28 | 0 | 535 | 535 | 0 | 0 | 4 | 535 | 50 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.9 | 8960 | 41.8 | 3568.5 | 840 | 6190 | 5350 | 10 | 85.5408 | 6134.6 | 0 | 55.4 | 0 |  | 61.9213 | 5350
29 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 50 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.75 | 8600 | 41.758 | 3519.36 | -360 | 4791 | 5151 | 10.1 | 84.991 | 4730.4 | 0 | 60.6 | 0 |  | 59.6181 | 5151
30 | 0 | 430 | 430 | 0 | 0 | 3 | 430 | 45 | 0 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85 | 9200 | 41.733 | 3490.11 | 600 | 4814 | 4214 | 9.8 | 87.0835 | 4552.65 | 0 | 261.35 | 0 |  | 48.7731 | 4214
31 | 0 | 445 | 445 | 0 | 0 | 4 | 445 | 45 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.85 | 8840 | 41.615 | 3352.05 | -360 | 4134.5 | 4494.5 | 10.1 | 84.7927 | 4060.25 | 0 | 74.25 | 0 |  | 52.0197 | 4494.5
| 12550 | 6665 | 19215 | 0 | 0 | 114 | 19101 | 90 | 257.7 | 142.4 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 37 | 24 |  |  | 84.4468 | 7872.2581 | 41.6302 | 3369.8265 | 1800 | 204028.7044 | 191300 | 9.9558 | 86.8383 | 198831.89 | 10928.7044 | 5256.8144 | 60 |  | 71.4232 | 191300