## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 395 | 250 | 645 | 0 | 0 | 4 | 645 | 108 | 9.5 | 5.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.6 | 8240 | 41.68 | 3428.1 | 1080 | 7465.5 | 6385.5 | 9.9 | 87.0133 | 7416.15 | 0 | 49.35 | 0 |  | 73.9062 | 6385.5
2 | 0 | 570 | 570 | 0 | 0 | 5 | 570 | 55 | 0 | 12.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.5 | 8000 | 41.349 | 3040.83 | -240 | 5517 | 5757 | 10.1 | 85.491 | 5423.9 | 0 | 153.1 | 60 |  | 66.6319 | 5757
3 | 620 | 285 | 905 | 0 | 0 | 5 | 905 | 100 | 13.8 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 3 | 84.1 | 7040 | 41.65 | 3393 | -960 | 8180.5 | 9140.5 | 10.1 | 86.3032 | 8128.8 | 0 | 111.7 | 60 |  | 105.7928 | 9140.5
4 | 425 | 305 | 730 | 0 | 0 | 4 | 730 | 80 | 9.7 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 4 | 84.5 | 8000 | 42 | 3802.5 | 960 | 8187 | 7227 | 9.9 | 87.2181 | 8028 | 0 | 159 | 0 |  | 83.6458 | 7227
5 | 275 | 170 | 445 | 0 | 0 | 4 | 445 | 40 | 7.8 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.7 | 8480 | 40.7 | 2281.5 | 480 | 4885.5 | 4405.5 | 9.9 | 86.8095 | 4845.6 | 0 | 39.9 | 0 |  | 50.9896 | 4405.5
6 | 290 | 0 | 290 | 0 | 0 | 4 | 290 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.65 | 8360 | 41.007 | 2640.69 | -120 | 3378.6596 | 2871 | 9.9 | 86.9113 | 3255.8 | 627.6596 | 122.8596 | 0 |  | 33.2292 | 2871
7 | 455 | 0 | 455 | 0 | 0 | 6 | 455 | 40 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 85.1 | 9440 | 41.081 | 2727.27 | 1080 | 5539 | 4459 | 9.8 | 86.8815 | 5415 | 0 | 124 | 0 |  | 51.6088 | 4459
8 | 485 | 0 | 485 | 0 | 0 | 5 | 485 | 55 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.8 | 8720 | 41.6 | 3334.5 | -720 | 8395.3298 | 4801.5 | 9.9 | 86.6067 | 8305.5 | 4313.8298 | 89.8298 | 0 |  | 55.5729 | 4801.5
9 | 0 | 515 | 515 | 0 | 0 | 4 | 515 | 45 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 9 | 84.85 | 8840 | 41.3 | 2983.5 | 120 | 6241.4681 | 5047 | 9.8 | 87.3884 | 6232.5 | 1074.4681 | 8.9681 | 0 |  | 58.4144 | 5047
10 | 475 | 0 | 475 | 0 | 0 | 4 | 475 | 45 | 11.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 10 | 84.3 | 7520 | 41.5 | 3217.5 | -1320 | 3382.5 | 4702.5 | 9.9 | 87.6304 | 3344.8 | 0 | 37.7 | 0 |  | 54.4271 | 4702.5
11 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 45 | 9.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.3 | 7520 | 41.297 | 2979.99 | 0 | 4150 | 4150 | 10 | 86.7541 | 3929.4 | 0 | 220.6 | 0 |  | 48.0324 | 4150
12 | 270 | 0 | 270 | 0 | 0 | 5 | 270 | 40 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.85 | 8840 | 40.15 | 1638 | 1320 | 4020 | 2700 | 10 | 85.6406 | 3774 | 0 | 246 | 0 |  | 31.25 | 2700
13 | 230 | 0 | 230 | 0 | 0 | 5 | 230 | 45 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.4 | 7760 | 41.2 | 2866.5 | -1080 | 4696.125 | 2323 | 10.1 | 85.6926 | 4662 | 3453.125 | 34.125 | 0 |  | 26.8866 | 2323
14 | 440 | 0 | 440 | 0 | 0 | 5 | 440 | 45 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.05 | 6920 | 41.589 | 3321.63 | -840 | 3604 | 4444 | 10.1 | 86.4059 | 3336.1 | 0 | 327.9 | 60 |  | 51.4352 | 4444
15 | 190 | 250 | 440 | 0 | 0 | 4 | 440 | 85 | 4.4 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 15 | 84.25 | 7400 | 41.201 | 2867.67 | 480 | 4880 | 4400 | 10 | 86.8568 | 4837.5 | 0 | 42.5 | 0 |  | 50.9259 | 4400
16 | 160 | 275 | 435 | 0 | 0 | 5 | 435 | 45 | 3.9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 84.5 | 8000 | 41.563 | 3291.21 | 600 | 4884.75 | 4284.75 | 9.85 | 87.6608 | 4758.2 | 0 | 126.55 | 0 |  | 49.592 | 4284.75
17 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 54 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.15 | 7160 | 41.36 | 3053.7 | -840 | 3705 | 4545 | 10.1 | 86.2009 | 3592.8 | 0 | 112.2 | 0 |  | 52.6042 | 4545
18 | 400 | 0 | 400 | 0 | 0 | 4 | 400 | 45 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 18 | 84.5 | 8000 | 41.602 | 3336.84 | 840 | 4840 | 4000 | 10 | 86.3459 | 4845 | 0 | 55 | 60 |  | 46.2963 | 4000
19 | 570 | 250 | 820 | 0 | 0 | 4 | 820 | 110 | 12.7 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.8 | 8720 | 41.779 | 3543.93 | 720 | 8920 | 8200 | 10 | 85.7407 | 8842.5 | 0 | 77.5 | 0 |  | 94.9074 | 8200
20 | 440 | 0 | 440 | 0 | 0 | 4 | 440 | 45 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.5 | 8000 | 41.219 | 2888.73 | -720 | 3724 | 4444 | 10.1 | 85.491 | 3598.9 | 0 | 125.1 | 0 |  | 51.4352 | 4444
21 | 190 | 465 | 655 | 0 | 0 | 5 | 655 | 70 | 4.9 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 84.4 | 7760 | 41.15 | 2808 | -240 | 6244.5 | 6484.5 | 9.9 | 87.4238 | 6234.2 | 0 | 10.3 | 0 |  | 75.0521 | 6484.5
22 | 705 | 220 | 925 | 0 | 0 | 4 | 925 | 70 | 15.85 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 84.55 | 8120 | 41.62 | 3357.9 | 360 | 9702.5 | 9342.5 | 10.1 | 85.3905 | 9614.1 | 0 | 88.4 | 0 |  | 108.1308 | 9342.5
23 | 155 | 770 | 925 | 0 | 0 | 5 | 925 | 95 | 4.15 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.45 | 7880 | 41.78 | 3545.1 | -240 | 8825 | 9065 | 9.8 | 88.2118 | 8752.7 | 0 | 132.3 | 60 |  | 104.919 | 9065
24 | 640 | 140 | 780 | 0 | 0 | 5 | 780 | 70 | 14.1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.4 | 7760 | 41.316 | 3002.22 | -120 | 7563 | 7683 | 9.85 | 87.8675 | 7554.4 | 0 | 8.6 | 0 |  | 88.9236 | 7683
25 | 790 | 190 | 980 | 0 | 0 | 4 | 980 | 110 | 16.2 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 83.95 | 6680 | 41.8 | 3568.5 | -1080 | 8622 | 9702 | 9.9 | 88.3616 | 8424.5 | 0 | 197.5 | 0 |  | 112.2917 | 9702
26 | 765 | 0 | 765 | 0 | 0 | 5 | 765 | 45 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 83.8 | 6320 | 41.372 | 3067.74 | -360 | 7366.5 | 7726.5 | 10.1 | 86.9226 | 7402.2 | 0 | 24.3 | 60 |  | 89.4271 | 7726.5
27 | 390 | 390 | 780 | 0 | 0 | 4 | 780 | 90 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 83.45 | 5480 | 41.03 | 2667.6 | -840 | 7155 | 7995 | 10.25 | 86.3738 | 7182 | 0 | 33 | 60 |  | 92.5347 | 7995
28 | 730 | 250 | 980 | 0 | 0 | 4 | 980 | 90 | 16 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 83.45 | 5480 | 41.802 | 3570.84 | 0 | 9898 | 9898 | 10.1 | 87.6566 | 9778.15 | 0 | 119.85 | 0 |  | 114.5602 | 9898
29 | 785 | 120 | 905 | 0 | 0 | 4 | 905 | 100 | 17 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 83.5 | 5600 | 41.7 | 3451.5 | 120 | 9848.75 | 9728.75 | 10.75 | 82.2572 | 9841.8 | 0 | 36.95 | 30 |  | 112.6013 | 9728.75
30 | 660 | 0 | 660 | 0 | 0 | 4 | 660 | 55 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 83.95 | 6680 | 40.851 | 2458.17 | 1080 | 7482 | 6402 | 9.7 | 90.1835 | 7270.65 | 0 | 211.35 | 0 |  | 74.0972 | 6402
| 12795 | 5415 | 18210 | 0 | 0 | 133 | 18077 | 110 | 290.8 | 123.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 22 |  |  | 84.3433 | 7624 | 41.3749 | 3071.172 | -480 | 191303.5824 | 182314.5 | 10.0118 | 86.5634 | 188627.15 | 9469.0824 | 3126.4324 | 450 |  | 70.3374