## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 715 | 250 | 965 | 0 | 0 | 5 | 965 | 100 | 15.85 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 84.2 | 7280 | 41.83 | 3603.6 | 600 | 10105.25 | 9505.25 | 9.85 | 88.284 | 9900 | 0 | 205.25 | 0 |  | 110.0145 | 9505.25
2 | 510 | 260 | 770 | 0 | 0 | 5 | 770 | 100 | 11.55 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 2 | 84.4 | 7760 | 41.562 | 3290.04 | 480 | 8180 | 7700 | 10 | 86.5495 | 8038.55 | 0 | 141.45 | 0 |  | 89.1204 | 7700
3 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 55 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.55 | 8120 | 41.141 | 2797.47 | 360 | 4905 | 4545 | 10.1 | 85.3905 | 4777.5 | 0 | 127.5 | 0 |  | 52.6042 | 4545
4 | 450 | 0 | 450 | 0 | 0 | 4 | 450 | 55 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 84.3 | 7520 | 41.29 | 2971.8 | -600 | 3945 | 4545 | 10.1 | 85.8952 | 3832.5 | 0 | 112.5 | 0 |  | 52.6042 | 4545
5 | 470 | 520 | 990 | 0 | 0 | 4 | 990 | 110 | 11.8 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 83.2 | 4880 | 41.349 | 3040.83 | -2640 | 7507.5 | 10147.5 | 10.25 | 86.8979 | 7540.9 | 0 | 26.6 | 60 |  | 117.4479 | 10147.5
6 | 250 | 530 | 780 | 0 | 0 | 4 | 780 | 110 | 6.3 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 83.5 | 5600 | 41.86 | 3638.7 | 720 | 8855.4 | 8135.4 | 10.43 | 84.7809 | 8892 | 0 | 23.4 | 60 |  | 94.1597 | 8135.4
7 | 255 | 160 | 415 | 0 | 0 | 4 | 415 | 110 | 5.3 | 3.5 | 0 | 5.2 | 0 | 0 | 0 | 5.2 | 0 | 0 | 2 | 2 | Συντήρηση Ρ60 Υ/Σ Ραχιάς από ΑΔΜΗΕ | 7 | 83.65 | 5960 | 40.802 | 2400.84 | 360 | 4551.5 | 4191.5 | 10.1 | 87.2357 | 4489.5 | 0 | 62 | 0 |  | 48.5127 | 4191.5
8 | 435 | 0 | 435 | 0 | 0 | 5 | 435 | 40 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.2 | 7280 | 40.973 | 2600.91 | 1320 | 6795.1327 | 4393.5 | 10.1 | 86.0987 | 6795 | 1081.6327 | 5.1327 | 5 |  | 50.8507 | 4393.5
9 | 445 | 80 | 525 | 0 | 0 | 4 | 525 | 70 | 10.35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 9 | 83.75 | 6200 | 41.4 | 3100.5 | -1080 | 4117.5 | 5197.5 | 9.9 | 88.7849 | 4080.7 | 0 | 36.8 | 0 |  | 60.1562 | 5197.5
10 | 145 | 215 | 360 | 0 | 0 | 4 | 360 | 55 | 3.65 | 4.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 84.8 | 8720 | 41.9865 | 3786.705 | 2520 | 6062.5 | 3542.5 | 9.8403 | 87.1324 | 5869.2 | 0 | 193.3 | 0 |  | 41.0012 | 3542.5
11 | 470 | 0 | 470 | 0 | 0 | 4 | 470 | 45 | 10.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11 | 84 | 6800 | 41.3 | 2983.5 | -1920 | 2827 | 4747 | 10.1 | 86.5087 | 2759.4 | 0 | 127.6 | 60 |  | 54.9421 | 4747
12 | 760 | 325 | 1085 | 0 | 0 | 6 | 1085 | 90 | 15.85 | 7.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.25 | 7400 | 41.6 | 3334.5 | 600 | 11450 | 10850 | 10 | 86.8568 | 11527.5 | 0 | 12.5 | 90 |  | 125.5787 | 10850
13 | 150 | 570 | 720 | 0 | 0 | 6 | 720 | 90 | 3.2 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 13 | 83.7 | 6080 | 40.82 | 2421.9 | -1320 | 5952 | 7272 | 10.1 | 87.1311 | 5803.5 | 0 | 208.5 | 60 |  | 84.1667 | 7272
14 | 270 | 875 | 1145 | 0 | 0 | 4 | 1145 | 100 | 5.3 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.4 | 7760 | 41.76 | 3521.7 | 1680 | 13244.5 | 11564.5 | 10.1 | 85.6926 | 13223.8 | 0 | 20.7 | 0 |  | 133.8484 | 11564.5
15 | 600 | 665 | 1265 | 0 | 0 | 4 | 1265 | 110 | 11.9 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | ΒΛΑΒΗ ΔΙΕΓΕΡΣΗΣ ΜΟΝ. ΝοΙ | 15 | 83.4 | 5360 | 41.58 | 3311.1 | -2400 | 10503 | 12903 | 10.2 | 86.9021 | 10574.6 | 0 | 28.4 | 100 |  | 149.3403 | 12903
16 | 625 | 715 | 1340 | 0 | 0 | 4 | 1340 | 110 | 11.6 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 83.65 | 5960 | 41.098 | 2747.16 | 600 | 14134 | 13534 | 10.1 | 87.2357 | 14222.05 | 0 | 11.95 | 100 |  | 156.6435 | 13534
17 | 480 | 165 | 645 | 0 | 0 | 5 | 645 | 110 | 9.8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 17 | 83.9 | 6560 | 41.4 | 3100.5 | 600 | 6985.5 | 6385.5 | 9.9 | 88.467 | 6824.2 | 0 | 161.3 | 0 |  | 73.9062 | 6385.5
18 | 330 | 390 | 720 | 0 | 0 | 5 | 720 | 110 | 6.4 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84 | 6800 | 41.75 | 3510 | 240 | 7512 | 7272 | 10.1 | 86.5087 | 7467.9 | 0 | 104.1 | 60 |  | 84.1667 | 7272
19 | 890 | 520 | 1410 | 0 | 0 | 5 | 1410 | 110 | 18.7 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 84.55 | 8120 | 41.69 | 3439.8 | 1320 | 15843 | 14523 | 10.3 | 83.7324 | 15836 | 0 | 67 | 60 |  | 168.0903 | 14523
20 | 780 | 505 | 1285 | 0 | 0 | 5 | 1285 | 110 | 16.2 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 83.55 | 5720 | 41.7 | 3451.5 | -2400 | 10707 | 13107 | 10.2 | 86.5883 | 10744.8 | 0 | 22.2 | 60 |  | 151.7014 | 13107
21 | 350 | 265 | 615 | 0 | 0 | 5 | 615 | 95 | 7.3 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 21 | 82.8 | 3960 | 41.16 | 2819.7 | -1760 | 4789.75 | 6549.75 | 10.65 | 84.4541 | 4556 | 0 | 333.75 | 100 |  | 75.8073 | 6549.75
22 | 775 | 280 | 1055 | 0 | 0 | 5 | 1055 | 108 | 17 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.5 | 8000 | 41.78 | 3545.1 | 4040 | 14801 | 10761 | 10.2 | 84.6528 | 14843.4 | 0 | 17.6 | 60 |  | 124.5486 | 10761
23 | 810 | 550 | 1360 | 0 | 0 | 4 | 1360 | 109 | 15.55 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 83.7 | 6080 | 41.32 | 3006.9 | -1920 | 11544 | 13464 | 9.9 | 88.8913 | 11380.7 | 0 | 163.3 | 0 |  | 155.8333 | 13464
24 | 325 | 280 | 605 | 0 | 0 | 4 | 605 | 110 | 6.25 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.4 | 7760 | 41.6 | 3334.5 | 1680 | 7669.5 | 5989.5 | 9.9 | 87.4238 | 7636.65 | 0 | 32.85 | 0 |  | 69.3229 | 5989.5
25 | 280 | 0 | 280 | 0 | 0 | 4 | 280 | 55 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.4 | 7760 | 40.497 | 2043.99 | 0 | 2828 | 2828 | 10.1 | 85.6926 | 2804.5 | 0 | 83.5 | 60 |  | 32.7315 | 2828
26 | 220 | 0 | 220 | 0 | 0 | 4 | 220 | 45 | 5.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 84.1 | 7040 | 41.47 | 3182.4 | -720 | 1414 | 2134 | 9.7 | 89.8621 | 1265.4 | 0 | 148.6 | 0 |  | 24.6991 | 2134
27 | 610 | 570 | 1180 | 0 | 0 | 4 | 1180 | 110 | 14 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 83 | 4400 | 41.3485 | 3040.245 | -2640 | 9278 | 11918 | 10.1 | 88.6187 | 9303 | 0 | 35 | 60 |  | 137.9398 | 11918
28 | 730 | 660 | 1390 | 0 | 0 | 6 | 1390 | 110 | 13.85 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.4 | 7760 | 41.6985 | 3449.745 | 3360 | 17607.5 | 14247.5 | 10.25 | 84.4386 | 17640 | 0 | 27.5 | 60 |  | 164.9016 | 14247.5
29 | 520 | 140 | 660 | 0 | 0 | 5 | 660 | 70 | 12.4 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.7 | 8480 | 41.269 | 2947.23 | 720 | 8362.5532 | 6600 | 10 | 85.9415 | 8209.14 | 1042.5532 | 153.4132 | 0 |  | 76.3889 | 6600
30 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.6 | 8240 | 41.03 | 2667.6 | -240 | 3684.5106 | 1616 | 10.1 | 85.2903 | 3690.96 | 2308.5106 | 53.5506 | 60 |  | 18.7037 | 1616
31 | 510 | 510 | 1020 | 0 | 0 | 5 | 1020 | 110 | 10.8 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 31 | 84 | 6800 | 41.33 | 3018.6 | -1440 | 8964 | 10404 | 10.2 | 85.6606 | 8967.3 | 0 | 56.7 | 60 |  | 120.4167 | 10404
| 14610 | 10160 | 24770 | 0 | 0 | 141 | 24629 | 110 | 314 | 216.4 | 0 | 5.2 | 0 | 0 | 0 | 5.2 | 0 | 0 | 35 | 32 |  |  | 84.0177 | 6843.871 | 41.3998 | 3100.2924 | 120 | 255125.5965 | 250572.9 | 10.116 | 86.3356 | 253496.65 | 4432.6965 | 2803.9465 | 1175 |  | 93.5532 | 250572.9