## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 55 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.9 | 6560 | 41.241 | 2914.47 | -240 | 2942.4487 | 1464.5 | 10.1 | 86.7152 | 2816.1 | 1717.9487 | 126.3487 | 0 |  | 16.9502 | 1464.5
2 | 80 | 0 | 80 | 0 | 0 | 7 | 80 | 55 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 83.85 | 6440 | 41.051 | 2692.17 | -120 | 2360.9697 | 784 | 9.8 | 89.4765 | 2347.5 | 1696.9697 | 13.4697 | 0 |  | 9.0741 | 784
3 | 60 | 0 | 60 | 0 | 0 | 3 | 60 | 35 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 83 | 4400 | 40.74 | 2328.3 | -2040 | 796.0851 | 618 | 10.3 | 86.8979 | 880.4 | 2218.0851 | 35.6851 | 120 |  | 7.1528 | 618
4 | 55 | 0 | 55 | 0 | 0 | 7 | 55 | 37 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 4 | 83.35 | 5240 | 40.43 | 1965.6 | 840 | 1379 | 539 | 9.8 | 90.5584 | 1147.5 | 0 | 231.5 | 0 |  | 6.2384 | 539
5 | 65 | 0 | 65 | 0 | 0 | 10 | 65 | 35 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 83.4 | 5360 | 40.21 | 1708.2 | 120 | 2481.7759 | 646.75 | 9.95 | 89.0855 | 2388.75 | 1715.0259 | 93.0259 | 0 |  | 7.4855 | 646.75
6 | 65 | 0 | 65 | 0 | 0 | 5 | 65 | 36 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 6 | 83.8 | 6320 | 39.998 | 1460.16 | 960 | 1610 | 650 | 10 | 87.7919 | 1428.2 | 0 | 181.8 | 0 |  | 7.5231 | 650
7 | 185 | 0 | 185 | 0 | 0 | 5 | 185 | 55 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.4 | 7760 | 40.802 | 2400.84 | 1440 | 4981.6378 | 1822.25 | 9.85 | 87.8675 | 4780.4 | 1719.3878 | 201.2378 | 0 |  | 21.0909 | 1822.25
8 | 85 | 0 | 85 | 0 | 0 | 7 | 85 | 55 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 8 | 85.1 | 9440 | 40.754 | 2344.68 | 1680 | 2517.25 | 837.25 | 9.85 | 86.4405 | 2443.6 | 0 | 73.65 | 0 |  | 9.6904 | 837.25
9 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85.1 | 9440 | 40.801 | 2399.67 | 0 | 950 | 950 | 10 | 85.1439 | 788.4 | 0 | 161.6 | 0 |  | 10.9954 | 950
10 | 70 | 0 | 70 | 0 | 0 | 7 | 70 | 55 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 10 | 85 | 9200 | 40.7 | 2281.5 | -240 | 2760.3808 | 689.5 | 9.85 | 86.6415 | 2501.2 | 2310.8808 | 259.1808 | 0 |  | 7.9803 | 689.5
11 | 85 | 0 | 85 | 0 | 0 | 6 | 85 | 55 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85 | 9200 | 40.713 | 2296.71 | 0 | 2563.9645 | 833 | 9.8 | 87.0835 | 2506.6 | 1730.9645 | 57.3645 | 0 |  | 9.6412 | 833
12 | 90 | 0 | 90 | 0 | 0 | 6 | 90 | 55 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.35 | 7640 | 40.523 | 2074.41 | -1560 | 1726.6596 | 909 | 10.1 | 85.7938 | 1701 | 2377.6596 | 85.6596 | 60 |  | 10.5208 | 909
13 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.25 | 7400 | 40.518 | 2068.56 | -240 | 3028.7884 | 909 | 10.1 | 85.9968 | 2914.5 | 2359.7884 | 174.2884 | 60 |  | 10.5208 | 909
14 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 14 | 84.25 | 7400 | 40.421 | 1955.07 | 0 | 2639.7959 | 650 | 10 | 86.8568 | 2405 | 1989.7959 | 234.7959 | 0 |  | 7.5231 | 650
15 | 90 | 0 | 90 | 0 | 0 | 7 | 90 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84 | 6800 | 40.5 | 2047.5 | -600 | 2681.3404 | 909 | 10.1 | 86.5087 | 2445.5 | 2372.3404 | 295.8404 | 60 |  | 10.5208 | 909
16 | 65 | 0 | 65 | 0 | 0 | 7 | 65 | 36 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 83.7 | 6080 | 40.352 | 1874.34 | -720 | 3458.4974 | 650 | 10 | 88.0024 | 3498.6 | 3528.4974 | 19.8974 | 60 |  | 7.5231 | 650
17 | 65 | 0 | 65 | 0 | 0 | 5 | 65 | 37 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.75 | 6200 | 40.271 | 1779.57 | 120 | 2965.2755 | 656.5 | 10.1 | 87.0267 | 2912.7 | 2188.7755 | 112.5755 | 60 |  | 7.5984 | 656.5
18 | 60 | 0 | 60 | 0 | 0 | 4 | 60 | 40 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 18 | 83.85 | 6440 | 40.25 | 1755 | 240 | 876 | 636 | 10.6 | 82.7236 | 751.9 | 0 | 124.1 | 0 |  | 7.3611 | 636
19 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.8 | 6320 | 40.35 | 1872 | -120 | 970.2005 | 643.5 | 9.9 | 88.6787 | 847.5 | 446.7005 | 122.7005 | 0 |  | 7.4479 | 643.5
20 | 0 | 50 | 50 | 0 | 0 | 8 | 50 | 40 | 0 | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 83.85 | 6440 | 40.112 | 1593.54 | 120 | 637.5 | 517.5 | 10.35 | 84.7217 | 700.8 | 0 | 16.7 | 80 |  | 5.9896 | 517.5
21 | 65 | 0 | 65 | 0 | 0 | 6 | 65 | 35 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.1 | 7040 | 40.019 | 1484.73 | 600 | 1243.5 | 643.5 | 9.9 | 88.0467 | 877.5 | 0 | 366 | 0 |  | 7.4479 | 643.5
22 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 22 | 84.3 | 7520 | 40.28 | 1790.1 | 480 | 1110.5 | 630.5 | 9.7 | 89.4373 | 772.65 | 0 | 337.85 | 0 |  | 7.2975 | 630.5
23 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.3 | 7520 | 40.42 | 1953.9 | 0 | 707 | 707 | 10.1 | 85.8952 | 744.6 | 0 | 22.4 | 60 |  | 8.1829 | 707
24 | 0 | 80 | 80 | 0 | 0 | 6 | 80 | 35 | 0 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.5 | 8000 | 40.47 | 2012.4 | 480 | 1264 | 784 | 9.8 | 88.108 | 1050 | 0 | 214 | 0 |  | 9.0741 | 784
25 | 0 | 60 | 60 | 0 | 0 | 7 | 60 | 55 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 84.6 | 8240 | 40.351 | 1873.17 | 240 | 846 | 606 | 10.1 | 85.2903 | 781.1 | 0 | 64.9 | 0 |  | 7.0139 | 606
26 | 0 | 70 | 70 | 0 | 0 | 5 | 70 | 36 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.75 | 8600 | 40.302 | 1815.84 | 360 | 1046 | 686 | 9.8 | 87.5928 | 825 | 0 | 221 | 0 |  | 7.9398 | 686
27 | 0 | 130 | 130 | 0 | 0 | 5 | 130 | 55 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.95 | 9080 | 40.762 | 2354.04 | 480 | 1760.5 | 1280.5 | 9.85 | 86.7423 | 1545.3 | 0 | 215.2 | 0 |  | 14.8206 | 1280.5
28 | 0 | 80 | 80 | 0 | 0 | 6 | 80 | 36 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85 | 9200 | 40.771 | 2364.57 | 120 | 904 | 784 | 9.8 | 87.0835 | 755 | 0 | 149 | 0 |  | 9.0741 | 784
| 1780 | 470 | 2250 | 0 | 0 | 158 | 2092 | 55 | 41.4 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 6 |  |  | 84.2214 | 7331.4286 | 40.504 | 2052.18 | 2400 | 53209.0702 | 22436.25 | 9.9717 | 87.1625 | 49557.3 | 28372.8202 | 4211.7702 | 560 |  | 9.2742 | 22436.25