## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 75 | 75 | 0 | 0 | 5 | 75 | 36 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 85 | 9200 | 40.749 | 2338.83 | 0 | 735 | 735 | 9.8 | 87.0835 | 604 | 0 | 131 | 0 |  | 8.5069 | 735
2 | 0 | 100 | 100 | 0 | 0 | 5 | 100 | 54 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.75 | 6200 | 40.921 | 2540.07 | -3000 | 2763.1579 | 1000 | 10 | 87.897 | 2606.4 | 4763.1579 | 156.7579 | 0 |  | 11.5741 | 1000
3 | 0 | 130 | 130 | 0 | 0 | 8 | 130 | 55 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 3 | 83.95 | 6680 | 41.019 | 2654.73 | 480 | 1780 | 1300 | 10 | 87.4779 | 1813 | 0 | 27 | 60 |  | 15.0463 | 1300
4 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 55 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84 | 6800 | 41.002 | 2634.84 | 120 | 851.25 | 731.25 | 9.75 | 89.6142 | 714.4 | 0 | 136.85 | 0 |  | 8.4635 | 731.25
5 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 55 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 5 | 84.35 | 7640 | 40.979 | 2607.93 | 840 | 1624 | 784 | 9.8 | 88.4201 | 1260 | 0 | 364 | 0 |  | 9.0741 | 784
6 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 54 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 84.4 | 7760 | 41.189 | 2853.63 | 120 | 1424.8673 | 886.5 | 9.85 | 87.8675 | 1411.85 | 418.3673 | 13.0173 | 0 |  | 10.2604 | 886.5
7 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 55 | 0 | 1.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 84.6 | 8240 | 41.082 | 2728.44 | 480 | 1123.5 | 643.5 | 9.9 | 87.0133 | 764.4 | 0 | 359.1 | 0 |  | 7.4479 | 643.5
8 | 0 | 195 | 195 | 0 | 0 | 6 | 195 | 55 | 0 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.55 | 8120 | 41.842 | 3617.64 | -120 | 1849.5 | 1969.5 | 10.1 | 85.3905 | 1518.4 | 0 | 391.1 | 60 |  | 22.7951 | 1969.5
9 | 0 | 140 | 140 | 0 | 0 | 6 | 140 | 55 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 84.8 | 8720 | 41.783 | 3548.61 | 600 | 1965 | 1365 | 9.75 | 87.9391 | 1406 | 0 | 559 | 0 |  | 15.7986 | 1365
10 | 0 | 85 | 85 | 0 | 0 | 5 | 85 | 35 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.9 | 8960 | 40.6945 | 2275.065 | 240 | 1098.5 | 858.5 | 10.1 | 84.6939 | 717.1 | 0 | 441.4 | 60 |  | 9.9363 | 858.5
11 | 0 | 85 | 85 | 0 | 0 | 5 | 85 | 55 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 11 | 85 | 9200 | 40.585 | 2146.95 | 240 | 1081.5 | 841.5 | 9.9 | 86.2039 | 1021.65 | 0 | 119.85 | 60 |  | 9.7396 | 841.5
12 | 0 | 145 | 145 | 0 | 0 | 5 | 145 | 54 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85.05 | 9320 | 40.92 | 2538.9 | 120 | 2016.6399 | 1435.5 | 9.9 | 86.1038 | 1494.8 | 461.1399 | 521.8399 | 0 |  | 16.6146 | 1435.5
13 | 0 | 70 | 70 | 0 | 0 | 6 | 70 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 85.1 | 9440 | 40.752 | 2342.34 | 120 | 827 | 707 | 10.1 | 84.3008 | 737.3 | 0 | 149.7 | 60 |  | 8.1829 | 707
14 | 60 | 185 | 245 | 0 | 0 | 5 | 245 | 110 | 1.2 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.9 | 8960 | 41.652 | 3395.34 | -480 | 1921 | 2401 | 9.8 | 87.2865 | 1383.2 | 0 | 537.8 | 0 |  | 27.7894 | 2401
15 | 0 | 145 | 145 | 0 | 0 | 4 | 145 | 55 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 84.9 | 8960 | 41.55 | 3276 | 0 | 1479 | 1479 | 10.2 | 83.8635 | 1499.4 | 0 | 39.6 | 60 |  | 17.1181 | 1479
16 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85.1 | 9440 | 41.151 | 2809.17 | 480 | 1123.5 | 643.5 | 9.9 | 86.0039 | 815.85 | 0 | 307.65 | 0 |  | 7.4479 | 643.5
17 | 0 | 65 | 65 | 0 | 0 | 6 | 65 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 17 | 85.2 | 9680 | 41.13 | 2784.6 | 240 | 877 | 637 | 9.8 | 86.6804 | 727.5 | 0 | 149.5 | 0 |  | 7.3727 | 637
18 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 55 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 85 | 9200 | 41.553 | 3279.51 | -480 | 1272.4921 | 1386 | 9.9 | 86.2039 | 1102.5 | 366.4921 | 169.9921 | 0 |  | 16.0417 | 1386
19 | 0 | 70 | 70 | 0 | 0 | 8 | 70 | 55 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 84.9 | 8960 | 40.958 | 2583.36 | -240 | 956.2041 | 686 | 9.8 | 87.2865 | 772.5 | 510.2041 | 183.7041 | 0 |  | 7.9398 | 686
20 | 0 | 110 | 110 | 0 | 0 | 5 | 110 | 55 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.8 | 8720 | 41.12 | 2772.9 | -240 | 849 | 1089 | 9.9 | 86.6067 | 637.5 | 0 | 211.5 | 0 |  | 12.6042 | 1089
21 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 21 | 84.85 | 8840 | 40.99 | 2620.8 | 120 | 799 | 679 | 9.7 | 88.2893 | 729.6 | 0 | 69.4 | 0 |  | 7.8588 | 679
22 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 54 | 0 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85.1 | 9440 | 40.848 | 2454.66 | 600 | 1376 | 776 | 9.7 | 87.7772 | 1004.15 | 0 | 371.85 | 0 |  | 8.9815 | 776
23 | 0 | 65 | 65 | 0 | 0 | 6 | 65 | 36 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 85.15 | 9560 | 40.752 | 2342.34 | 120 | 770 | 650 | 10 | 85.0452 | 786.45 | 0 | 43.55 | 60 |  | 7.5231 | 650
24 | 70 | 105 | 175 | 0 | 0 | 4 | 175 | 110 | 1.7 | 2.4 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.6 | 8240 | 41.402 | 3102.84 | -1320 | 491.25 | 1811.25 | 10.35 | 83.2301 | 540.2 | 0 | 11.05 | 60 |  | 20.9635 | 1811.25
25 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 25 | 84.15 | 7160 | 41.263 | 2940.21 | -1080 | 1043.0918 | 643.5 | 9.9 | 87.9423 | 747.4 | 1479.5918 | 295.6918 | 0 |  | 7.4479 | 643.5
26 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.4 | 7760 | 41.103 | 2753.01 | 600 | 1286 | 686 | 9.8 | 88.3158 | 1095 | 0 | 191 | 0 |  | 7.9398 | 686
27 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 27 | 84.4 | 7760 | 41.14 | 2796.3 | 0 | 909 | 909 | 10.1 | 85.6926 | 912.5 | 0 | 56.5 | 60 |  | 10.5208 | 909
28 | 0 | 95 | 95 | 0 | 0 | 5 | 95 | 55 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.45 | 7880 | 41.2 | 2866.5 | 120 | 1582.0907 | 959.5 | 10.1 | 85.5917 | 1561.4 | 502.5907 | 50.6907 | 30 |  | 11.1053 | 959.5
29 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 55 | 1.8 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 0 |  | 29 | 84.45 | 7880 | 40.637 | 2207.79 | 0 | 1649.75 | 931 | 9.8 | 88.2118 | 1423.96 | 718.75 | 225.79 | 0 |  | 10.7755 | 931
30 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 55 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 30 | 84.75 | 8600 | 40.403 | 1934.01 | 720 | 1602 | 882 | 9.8 | 87.5928 | 1178.1 | 0 | 423.9 | 0 |  | 10.2083 | 882
31 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 35 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 31 | 85 | 9200 | 40.207 | 1704.69 | 600 | 1477.5 | 877.5 | 9.75 | 87.5301 | 1154.75 | 0 | 382.75 | 60 |  | 10.1562 | 877.5
| 315 | 2845 | 3160 | 0 | 0 | 149 | 3011 | 110 | 6.4 | 62.1 | 1 | 7 | 0 | 0 | 1 | 7 | 0 | 0 | 3 | 29 |  |  | 84.6952 | 8468.3871 | 41.0509 | 2692.0002 | 0 | 40603.7939 | 31383.5 | 9.9315 | 86.5441 | 34141.26 | 9220.2939 | 7092.5339 | 630 |  | 11.7173 | 31383.5