## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 35 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 85.15 | 9560 | 40.143 | 1629.81 | 360 | 1370 | 1010 | 10.1 | 84.2032 | 1381.65 | 0 | 8.35 | 20 |  | 11.6898 | 1010
2 | 0 | 100 | 100 | 0 | 0 | 4 | 100 | 36 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.2 | 9680 | 40.236 | 1738.62 | 120 | 1100 | 980 | 9.8 | 86.6804 | 821.4 | 0 | 278.6 | 0 |  | 11.3426 | 980
3 | 190 | 0 | 190 | 0 | 0 | 4 | 190 | 41 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85 | 9200 | 40.842 | 2447.64 | -480 | 1439 | 1919 | 10.1 | 84.4969 | 1447.5 | 0 | 11.5 | 20 |  | 22.2106 | 1919
4 | 0 | 120 | 120 | 0 | 0 | 3 | 120 | 40 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 85.15 | 9560 | 40.7925 | 2389.725 | 360 | 1536 | 1176 | 9.8 | 86.7808 | 1307.2 | 0 | 228.8 | 0 |  | 13.6111 | 1176
5 | 0 | 225 | 225 | 0 | 0 | 4 | 225 | 40 | 0 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 5 | 84.9 | 8960 | 41.42 | 3123.9 | -600 | 1672.5 | 2272.5 | 10.1 | 84.6939 | 1533 | 0 | 169.5 | 30 |  | 26.3021 | 2272.5
6 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 55 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.9 | 8960 | 41.681 | 3429.27 | 0 | 1691.25 | 1691.25 | 10.25 | 83.4544 | 1606.5 | 0 | 84.75 | 0 |  | 19.5747 | 1691.25
7 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 55 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 7 | 85.05 | 9320 | 41.639 | 3380.13 | 360 | 1634 | 1274 | 9.8 | 86.9824 | 1387.5 | 0 | 246.5 | 0 |  | 14.7454 | 1274
8 | 65 | 95 | 160 | 0 | 0 | 4 | 160 | 55 | 1.25 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85 | 9200 | 41.543 | 3267.81 | -120 | 1456 | 1576 | 9.85 | 86.6415 | 1155.2 | 0 | 300.8 | 0 |  | 18.2407 | 1576
9 | 125 | 0 | 125 | 0 | 0 | 4 | 125 | 55 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85 | 9200 | 41.382 | 3079.44 | 0 | 2135.9948 | 1225 | 9.8 | 87.0835 | 1795.45 | 910.9948 | 340.5448 | 0 |  | 14.1782 | 1225
10 | 0 | 165 | 165 | 0 | 0 | 4 | 165 | 55 | 0 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 85 | 9200 | 41.558 | 3285.36 | 0 | 1650 | 1650 | 10 | 85.3419 | 1569.5 | 0 | 80.5 | 0 |  | 19.0972 | 1650
11 | 0 | 205 | 205 | 0 | 0 | 4 | 205 | 55 | 0 | 4.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 85 | 9200 | 41.928 | 3718.26 | 0 | 2029.5 | 2029.5 | 9.9 | 86.2039 | 1781.8 | 0 | 247.7 | 0 |  | 23.4896 | 2029.5
12 | 0 | 160 | 160 | 0 | 0 | 2 | 160 | 55 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.9 | 8960 | 41.5635 | 3291.795 | -240 | 1376 | 1616 | 10.1 | 84.6939 | 1365 | 0 | 71 | 60 |  | 18.7037 | 1616
13 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 35 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 13 | 85 | 9200 | 41.523 | 3244.41 | 240 | 1501 | 1261 | 9.7 | 87.9813 | 1321.25 | 0 | 179.75 | 0 |  | 14.5949 | 1261
14 | 0 | 40 | 40 | 0 | 0 | 4 | 40 | 35 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.85 | 8840 | 40.746 | 2335.32 | -360 | 1801.658 | 400 | 10 | 85.6406 | 1610 | 1761.658 | 191.658 | 0 |  | 4.6296 | 400
15 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 35 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 85.2 | 9680 | 40.306 | 1820.52 | 840 | 1624 | 784 | 9.8 | 86.6804 | 1411.85 | 0 | 212.15 | 0 |  | 9.0741 | 784
16 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 55 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.75 | 8600 | 40 | 1462.5 | -1080 | 4704.0957 | 757.5 | 10.1 | 84.991 | 4657.4 | 5026.5957 | 106.6957 | 60 |  | 8.7674 | 757.5
17 | 0 | 260 | 260 | 0 | 0 | 4 | 260 | 55 | 0 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.85 | 8840 | 40.9 | 2515.5 | 240 | 3190.7853 | 2600 | 10 | 85.6406 | 2962.5 | 350.7853 | 228.2853 | 0 |  | 30.0926 | 2600
18 | 0 | 185 | 185 | 0 | 0 | 4 | 185 | 55 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.85 | 8840 | 40.964 | 2590.38 | 0 | 1868.5 | 1868.5 | 10.1 | 84.7927 | 1817.7 | 0 | 80.8 | 30 |  | 21.6262 | 1868.5
19 | 0 | 180 | 180 | 0 | 0 | 4 | 180 | 55 | 0 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 19 | 84.9 | 8960 | 40.902 | 2517.84 | 120 | 1938 | 1818 | 10.1 | 84.6939 | 2073.2 | 0 | 14.8 | 150 |  | 21.0417 | 1818
20 | 0 | 185 | 185 | 0 | 0 | 4 | 185 | 40 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 84.9 | 8960 | 40.85 | 2457 | 0 | 1813 | 1813 | 9.8 | 87.2865 | 1584.1 | 0 | 288.9 | 60 |  | 20.9838 | 1813
21 | 0 | 235 | 235 | 0 | 0 | 3 | 235 | 55 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.7 | 8480 | 41.052 | 2693.34 | -480 | 1823 | 2303 | 9.8 | 87.6954 | 1613.3 | 0 | 269.7 | 60 |  | 26.6551 | 2303
22 | 55 | 275 | 330 | 0 | 0 | 4 | 330 | 110 | 1.1 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 22 | 85.25 | 9800 | 41.44 | 3147.3 | 1320 | 4554 | 3234 | 9.8 | 86.5802 | 4474.9 | 0 | 139.1 | 60 |  | 37.4306 | 3234
23 | 0 | 150 | 150 | 0 | 0 | 4 | 150 | 55 | 0 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 85.3 | 9920 | 40.834 | 2438.28 | 120 | 1575 | 1455 | 9.7 | 87.3717 | 913.55 | 0 | 721.45 | 60 |  | 16.8403 | 1455
24 | 5 | 160 | 165 | 0 | 0 | 4 | 165 | 85 | 0.1 | 3.15 | 0 | 0 | 2.75 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 24 | 85 | 9200 | 40.0438 | 1513.746 | -720 | 1012.5 | 1732.5 | 10.5 | 81.278 | 1267.5 | 0 | 195 | 60 |  | 20.0521 | 1732.5
25 | 0 | 220 | 220 | 0 | 0 | 4 | 220 | 45 | 0 | 5.3 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 25 | 85.25 | 9800 | 39.6908 | 1100.736 | 600 | 2756 | 2156 | 9.8 | 86.5802 | 2394.4 | 0 | 421.6 | 60 |  | 24.9537 | 2156
26 | 0 | 270 | 270 | 0 | 0 | 3 | 270 | 55 | 0 | 5.6 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 26 | 85.2 | 9680 | 39.524 | 905.58 | -120 | 2499 | 2619 | 9.7 | 87.574 | 2055 | 0 | 504 | 60 |  | 30.3125 | 2619
27 | 0 | 180 | 180 | 0 | 0 | 3 | 180 | 55 | 0 | 4.4 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 27 | 84.9 | 8960 | 38.7775 | 32.175 | -720 | 1188 | 1908 | 10.6 | 80.6989 | 1349 | 0 | 101 | 60 |  | 22.0833 | 1908
28 | 0 | 210 | 210 | 0 | 0 | 4 | 210 | 45 | 0 | 5.2 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 28 | 84.9 | 8960 | 40.25 | 1755 | 0 | 2121 | 2121 | 10.1 | 84.6939 | 1876.1 | 0 | 304.9 | 60 |  | 24.5486 | 2121
29 | 0 | 300 | 300 | 0 | 0 | 5 | 300 | 40 | 0 | 7.2 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 29 | 84.5 | 8000 | 40.552 | 2108.34 | -960 | 2070 | 3030 | 10.1 | 85.491 | 2058.6 | 0 | 71.4 | 60 |  | 35.0694 | 3030
30 | 0 | 275 | 275 | 0 | 0 | 4 | 275 | 55 | 0 | 6.5 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ ΜΟΝΑΔΟΣ ΝοΙ | 30 | 84.75 | 8600 | 40.378 | 1904.76 | 600 | 3281.25 | 2681.25 | 9.75 | 88.042 | 3124.4 | 0 | 216.85 | 60 |  | 31.033 | 2681.25
| 440 | 4875 | 5315 | 0 | 0 | 114 | 5201 | 110 | 9.9 | 110.7 | 0 | 0 | 146.75 | 0 | 0 | 0 | 0 | 0 | 6 | 40 |  |  | 84.9767 | 9144 | 40.782 | 2377.4829 | -600 | 60411.0339 | 52961 | 9.9644 | 85.6929 | 55716.45 | 8050.0339 | 5724.5839 | 1030 |  | 20.4325 | 52961