## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 285 | 285 | 0 | 0 | 1 | 285 | 40 | 0 | 6.2 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 1 | 84.65 | 8360 | 40.74 | 2328.3 | -240 | 3351.266 | 2878.5 | 10.1 | 85.1903 | 3321.5 | 712.766 | 89.766 | 60 |  | 33.316 | 2878.5
2 | 0 | 440 | 440 | 0 | 0 | 1 | 440 | 55 | 0 | 9.1 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 2 | 84 | 6800 | 41.901 | 3686.67 | -1560 | 2928 | 4488 | 10.2 | 85.6606 | 2934.6 | 0 | 53.4 | 60 |  | 51.9444 | 4488
3 | 0 | 435 | 435 | 0 | 0 | 4 | 435 | 55 | 0 | 8.9 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 3 | 84.1 | 7040 | 42.05 | 3861 | 240 | 4785.75 | 4545.75 | 10.45 | 83.4127 | 4732 | 0 | 113.75 | 60 |  | 52.6128 | 4545.75
4 | 0 | 315 | 315 | 0 | 0 | 4 | 315 | 55 | 0 | 7.9 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 4 | 84.1 | 7040 | 40.44 | 1977.3 | 0 | 3260.25 | 3260.25 | 10.35 | 84.2186 | 3255 | 0 | 65.25 | 60 |  | 37.7344 | 3260.25
5 | 0 | 300 | 300 | 0 | 0 | 2 | 300 | 55 | 0 | 7.8 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 5 | 84.4 | 7760 | 40.024 | 1490.58 | 720 | 3630 | 2910 | 9.7 | 89.2263 | 3420.15 | 0 | 209.85 | 0 |  | 33.6806 | 2910
6 | 0 | 390 | 390 | 0 | 0 | 2 | 390 | 45 | 0 | 8.9 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 6 | 84.65 | 8360 | 39.897 | 1341.99 | 600 | 4422 | 3822 | 9.8 | 87.7982 | 4379 | 0 | 43 | 0 |  | 44.2361 | 3822
7 | 0 | 440 | 440 | 0 | 0 | 2 | 440 | 55 | 0 | 8.8 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 7 | 84.9 | 8960 | 40.63 | 2199.6 | 600 | 6892.3478 | 4488 | 10.2 | 83.8635 | 6702.4 | 1804.3478 | 249.9478 | 60 |  | 51.9444 | 4488
8 | 220 | 245 | 465 | 0 | 0 | 4 | 465 | 55 | 4.5 | 4.9 | 0 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 8 | 84.75 | 8600 | 41.053 | 2694.51 | -360 | 4336.5 | 4696.5 | 10.1 | 84.991 | 4283.3 | 0 | 53.2 | 0 |  | 54.3576 | 4696.5
9 | 175 | 185 | 360 | 0 | 0 | 4 | 360 | 55 | 3.4 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 85 | 9200 | 40.79 | 2386.8 | 600 | 4146 | 3546 | 9.85 | 86.6415 | 4015.55 | 0 | 130.45 | 0 |  | 41.0417 | 3546
10 | 190 | 290 | 480 | 0 | 0 | 4 | 480 | 99 | 4.4 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.75 | 8600 | 41.101 | 2750.67 | -600 | 4200 | 4800 | 10 | 85.8409 | 4084.55 | 0 | 115.45 | 0 |  | 55.5556 | 4800
11 | 0 | 510 | 510 | 0 | 0 | 3 | 510 | 55 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 84.5 | 8000 | 41.311 | 2996.37 | -600 | 4551 | 5151 | 10.1 | 85.491 | 4514.9 | 0 | 66.1 | 30 |  | 59.6181 | 5151
12 | 335 | 100 | 435 | 0 | 0 | 4 | 435 | 70 | 8 | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84.45 | 7880 | 41.5 | 3217.5 | -120 | 6965.5579 | 4452.05 | 10.2346 | 84.466 | 6840.1 | 2633.5079 | 185.4579 | 60 |  | 51.5284 | 4452.05
13 | 480 | 0 | 480 | 0 | 0 | 3 | 480 | 45 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 84.5 | 8000 | 41.89 | 3673.8 | 120 | 5160 | 5040 | 10.5 | 82.2342 | 4973.5 | 0 | 186.5 | 0 |  | 58.3333 | 5040
14 | 415 | 0 | 415 | 0 | 0 | 4 | 415 | 45 | 8.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 14 | 84.2 | 7280 | 41.65 | 3393 | -720 | 3430 | 4150 | 10 | 86.9597 | 3270.75 | 0 | 159.25 | 0 |  | 48.0324 | 4150
15 | 0 | 465 | 465 | 0 | 0 | 4 | 465 | 55 | 0 | 9.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84 | 6800 | 41.5 | 3217.5 | -480 | 4216.5 | 4696.5 | 10.1 | 86.5087 | 4139.1 | 0 | 137.4 | 60 |  | 54.3576 | 4696.5
16 | 0 | 440 | 440 | 0 | 0 | 4 | 440 | 55 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.15 | 7160 | 41.602 | 3336.84 | 360 | 4804 | 4444 | 10.1 | 86.2009 | 4493.3 | 0 | 310.7 | 0 |  | 51.4352 | 4444
17 | 0 | 435 | 435 | 0 | 0 | 3 | 435 | 45 | 0 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.5 | 8000 | 41.81 | 3580.2 | 840 | 5233.5 | 4393.5 | 10.1 | 85.491 | 5161.1 | 0 | 132.4 | 60 |  | 50.8507 | 4393.5
18 | 0 | 380 | 380 | 0 | 0 | 3 | 380 | 55 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.5 | 8000 | 41.172 | 2833.74 | 0 | 3800 | 3800 | 10 | 86.3459 | 3720 | 0 | 80 | 0 |  | 43.9815 | 3800
19 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 45 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.6 | 8240 | 41.411 | 3113.37 | 240 | 3757.5 | 3517.5 | 10.5 | 82.0411 | 3525.9 | 0 | 231.6 | 0 |  | 40.7118 | 3517.5
20 | 0 | 290 | 290 | 0 | 0 | 3 | 290 | 45 | 0 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.3 | 7520 | 41.642 | 3383.64 | -720 | 2209 | 2929 | 10.1 | 85.8952 | 2146.2 | 0 | 62.8 | 0 |  | 33.9005 | 2929
21 | 25 | 245 | 270 | 0 | 0 | 4 | 270 | 85 | 0.75 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 84.4 | 7760 | 41.58 | 3311.1 | 240 | 2967 | 2727 | 10.1 | 85.6926 | 2788.6 | 0 | 178.4 | 0 |  | 31.5625 | 2727
22 | 0 | 360 | 360 | 0 | 0 | 3 | 360 | 55 | 0 | 8.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 83.5 | 5600 | 41.401 | 3101.67 | -2160 | 3308.4324 | 3636 | 10.1 | 87.551 | 3262 | 1832.4324 | 106.4324 | 60 |  | 42.0833 | 3636
23 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 45 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 83.8 | 6320 | 40.899 | 2514.33 | 720 | 2336 | 1616 | 10.1 | 86.9226 | 2065.9 | 0 | 330.1 | 60 |  | 18.7037 | 1616
24 | 80 | 100 | 180 | 0 | 0 | 4 | 180 | 55 | 1.65 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.3 | 7520 | 40.7 | 2281.5 | 1200 | 3018 | 1818 | 10.1 | 85.8952 | 2766.7 | 0 | 311.3 | 60 |  | 21.0417 | 1818
25 | 215 | 0 | 215 | 0 | 0 | 4 | 215 | 45 | 4.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.2 | 7280 | 40.75 | 2340 | -240 | 2017.5 | 2257.5 | 10.5 | 82.8188 | 1946 | 0 | 131.5 | 60 |  | 26.1285 | 2257.5
26 | 305 | 0 | 305 | 0 | 0 | 3 | 305 | 45 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 26 | 84.1 | 7040 | 41.469 | 3181.23 | -240 | 2810 | 3050 | 10 | 87.1663 | 2657.2 | 0 | 152.8 | 0 |  | 35.3009 | 3050
27 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 45 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.2 | 7280 | 41.471 | 3183.57 | 240 | 2411.5 | 2171.5 | 10.1 | 86.0987 | 2263 | 0 | 148.5 | 0 |  | 25.1331 | 2171.5
28 | 0 | 230 | 230 | 0 | 0 | 4 | 230 | 45 | 0 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.15 | 7160 | 41.493 | 3209.31 | -120 | 2203 | 2323 | 10.1 | 86.2009 | 2065.9 | 0 | 197.1 | 60 |  | 26.8866 | 2323
29 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 45 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.05 | 6920 | 41.128 | 2782.26 | -240 | 4096.4574 | 2070.5 | 10.1 | 86.4059 | 4018 | 2265.9574 | 138.4574 | 60 |  | 23.9641 | 2070.5
30 | 280 | 0 | 280 | 0 | 0 | 4 | 280 | 45 | 6.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 30 | 83.7 | 6080 | 41.102 | 2751.84 | -840 | 2016 | 2856 | 10.2 | 86.2769 | 2029.4 | 0 | 46.6 | 60 |  | 33.0556 | 2856
31 | 370 | 0 | 370 | 0 | 0 | 2 | 370 | 55 | 8.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84 | 6800 | 41.776 | 3540.42 | 720 | 4457 | 3737 | 10.1 | 86.5087 | 4234 | 0 | 223 | 0 |  | 43.2523 | 3737
| 3295 | 7590 | 10885 | 0 | 0 | 101 | 10784 | 99 | 73.4 | 167.8 | 0 | 0 | 182.6 | 0 | 0 | 0 | 0 | 0 | 21 | 42 |  |  | 84.3032 | 7527.7419 | 41.222 | 2892.2777 | -1800 | 117720.0615 | 110271.05 | 10.1306 | 85.6296 | 114009.6 | 9249.0115 | 4640.4615 | 930 |  | 41.1705 | 110271.05