## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 85 | 660 | 745 | 0 | 0 | 4 | 745 | 80 | 2.3 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 84.4 | 7760 | 41.95 | 3744 | -1320 | 6130 | 7450 | 10 | 86.5495 | 5978.7 | 0 | 151.3 | 0 |  | 86.2269 | 7450
2 | 55 | 865 | 920 | 0 | 0 | 4 | 920 | 105 | 0.95 | 15.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 84.8 | 8720 | 41.9 | 3685.5 | 960 | 10068 | 9108 | 9.9 | 86.6067 | 9971.8 | 0 | 126.2 | 30 |  | 105.4167 | 9108
3 | 685 | 50 | 735 | 0 | 0 | 4 | 735 | 50 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.1 | 7040 | 41.918 | 3706.56 | -1680 | 5780.25 | 7460.25 | 10.15 | 85.8781 | 5813.5 | 0 | 26.75 | 60 |  | 86.3455 | 7460.25
4 | 670 | 0 | 670 | 0 | 0 | 4 | 670 | 50 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.55 | 8120 | 41.691 | 3440.97 | 1080 | 7646 | 6566 | 9.8 | 88.0045 | 7555.5 | 0 | 90.5 | 0 |  | 75.9954 | 6566
5 | 710 | 0 | 710 | 0 | 0 | 2 | 710 | 50 | 15.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.75 | 8600 | 41.549 | 3274.83 | 480 | 7402.5 | 6922.5 | 9.75 | 88.042 | 7305.75 | 0 | 96.75 | 0 |  | 80.1215 | 6922.5
6 | 635 | 0 | 635 | 0 | 0 | 2 | 635 | 50 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 6 | 84.4 | 7760 | 41.049 | 2689.83 | -840 | 7713.1667 | 6286.5 | 9.9 | 87.4238 | 7385.2 | 2266.6667 | 327.9667 | 0 |  | 72.7604 | 6286.5
7 | 410 | 360 | 770 | 0 | 0 | 3 | 770 | 80 | 8.3 | 9.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.1 | 7040 | 41.902 | 3687.84 | -720 | 7057 | 7777 | 10.1 | 86.3032 | 7034.4 | 0 | 22.6 | 0 |  | 90.0116 | 7777
8 | 445 | 290 | 735 | 0 | 0 | 3 | 735 | 55 | 8.7 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.55 | 8120 | 41.829 | 3602.43 | 1080 | 8577 | 7497 | 10.2 | 84.5534 | 8568 | 0 | 69 | 60 |  | 86.7708 | 7497
9 | 710 | 0 | 710 | 0 | 0 | 3 | 710 | 55 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85.15 | 9560 | 42.05 | 3861 | 1440 | 8540 | 7100 | 10 | 85.0452 | 8423.1 | 0 | 116.9 | 0 |  | 82.1759 | 7100
10 | 470 | 820 | 1290 | 0 | 0 | 4 | 1290 | 108 | 8.9 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 10 | 85.05 | 9320 | 41.9 | 3685.5 | -240 | 12789 | 13029 | 10.1 | 84.3988 | 12572 | 0 | 217 | 0 |  | 150.7986 | 13029
11 | 845 | 0 | 845 | 0 | 0 | 4 | 845 | 55 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.9 | 8960 | 41.751 | 3511.17 | -360 | 8005.5 | 8365.5 | 9.9 | 86.4048 | 7926.35 | 0 | 79.15 | 0 |  | 96.8229 | 8365.5
12 | 895 | 0 | 895 | 0 | 0 | 4 | 895 | 55 | 16.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 12 | 84.7 | 8480 | 42.019 | 3824.73 | -480 | 8380.5 | 8860.5 | 9.9 | 86.8095 | 8139.5 | 0 | 241 | 0 |  | 102.5521 | 8860.5
13 | 430 | 385 | 815 | 0 | 0 | 4 | 815 | 55 | 8.3 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 85.3 | 9920 | 41.901 | 3686.67 | 1440 | 9508.5 | 8068.5 | 9.9 | 85.6066 | 9390.6 | 0 | 117.9 | 0 |  | 93.3854 | 8068.5
14 | 385 | 425 | 810 | 0 | 0 | 4 | 810 | 55 | 7.8 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.9 | 8960 | 41.94 | 3732.3 | -960 | 7059 | 8019 | 9.9 | 86.4048 | 6969.72 | 0 | 89.28 | 0 |  | 92.8125 | 8019
15 | 0 | 705 | 705 | 0 | 0 | 4 | 705 | 50 | 0 | 14.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 84.35 | 7640 | 42.06 | 3872.7 | -1320 | 5730 | 7050 | 10 | 86.6517 | 5519.85 | 0 | 210.15 | 0 |  | 81.5972 | 7050
16 | 625 | 10 | 635 | 0 | 0 | 4 | 635 | 50 | 12.85 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.15 | 7160 | 41.78 | 3545.1 | -480 | 5808.5 | 6288.5 | 9.9031 | 87.9143 | 5483.1 | 0 | 325.4 | 0 |  | 72.7836 | 6288.5
17 | 0 | 665 | 665 | 0 | 0 | 1 | 665 | 50 | 0 | 13.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.45 | 7880 | 41.91 | 3697.2 | 720 | 9787.5638 | 6716.5 | 10.1 | 85.5917 | 9738.2 | 2351.0638 | 49.3638 | 0 |  | 77.7373 | 6716.5
18 | 305 | 230 | 535 | 0 | 0 | 2 | 535 | 50 | 6.25 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.6 | 8240 | 41.792 | 3559.14 | 360 | 5763.5 | 5403.5 | 10.1 | 85.2903 | 5698 | 0 | 65.5 | 0 |  | 62.5405 | 5403.5
19 | 0 | 575 | 575 | 0 | 0 | 3 | 575 | 50 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.95 | 9080 | 41.82 | 3591.9 | 840 | 7905.0518 | 5635 | 9.8 | 87.1849 | 7642.5 | 1430.0518 | 262.5518 | 0 |  | 65.2199 | 5635
20 | 0 | 555 | 555 | 0 | 0 | 4 | 555 | 50 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.05 | 9320 | 41.73 | 3486.6 | 240 | 5679 | 5439 | 9.8 | 86.9824 | 5607.45 | 0 | 71.55 | 0 |  | 62.9514 | 5439
21 | 560 | 0 | 560 | 0 | 0 | 4 | 560 | 50 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.5 | 8000 | 41.87 | 3650.4 | -1320 | 4280 | 5600 | 10 | 86.3459 | 4039.9 | 0 | 240.1 | 0 |  | 64.8148 | 5600
22 | 445 | 0 | 445 | 0 | 0 | 4 | 445 | 50 | 9.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.1 | 7040 | 41.902 | 3687.84 | -960 | 3490 | 4450 | 10 | 87.1663 | 3248.5 | 0 | 241.5 | 0 |  | 51.5046 | 4450
23 | 275 | 250 | 525 | 0 | 0 | 4 | 525 | 54 | 5.45 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84 | 6800 | 41.94 | 3732.3 | -240 | 4957.5 | 5197.5 | 9.9 | 88.2564 | 4704 | 0 | 253.5 | 0 |  | 60.1562 | 5197.5
24 | 295 | 405 | 700 | 0 | 0 | 4 | 700 | 108 | 5.35 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 84.45 | 7880 | 41.899 | 3684.33 | 1080 | 8150 | 7070 | 10.1 | 85.5917 | 8023 | 0 | 127 | 0 |  | 81.8287 | 7070
25 | 335 | 240 | 575 | 0 | 0 | 4 | 575 | 54 | 7.5 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.3 | 7520 | 41.703 | 3455.01 | -360 | 5390 | 5750 | 10 | 86.7541 | 5225.85 | 0 | 164.15 | 0 |  | 66.5509 | 5750
26 | 275 | 185 | 460 | 0 | 0 | 1 | 460 | 45 | 5.95 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.15 | 7160 | 41.241 | 2914.47 | -360 | 4332 | 4692 | 10.2 | 85.3558 | 4347.2 | 0 | 44.8 | 60 |  | 54.3056 | 4692
27 | 0 | 480 | 480 | 0 | 0 | 2 | 480 | 45 | 0 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 27 | 84.45 | 7880 | 40.909 | 2526.03 | 720 | 5568 | 4848 | 10.1 | 85.5917 | 5365.5 | 0 | 202.5 | 0 |  | 56.1111 | 4848
28 | 575 | 0 | 575 | 0 | 0 | 3 | 575 | 55 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 28 | 84.3 | 7520 | 41.03 | 2667.6 | -360 | 5332.5 | 5692.5 | 9.9 | 87.6304 | 5186.85 | 0 | 145.65 | 0 |  | 65.8854 | 5692.5
29 | 440 | 245 | 685 | 0 | 0 | 4 | 685 | 55 | 9.05 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 29 | 84.6 | 8240 | 41.648 | 3390.66 | 720 | 7707 | 6987 | 10.2 | 84.4541 | 7740 | 0 | 27 | 60 |  | 80.8681 | 6987
30 | 255 | 425 | 680 | 0 | 0 | 3 | 680 | 80 | 5.65 | 9.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 30 | 84.65 | 8360 | 41.9599 | 3755.583 | 120 | 6886 | 6766 | 9.95 | 86.4746 | 6795 | 0 | 91 | 0 |  | 78.3102 | 6766
31 | 0 | 625 | 625 | 0 | 0 | 3 | 625 | 50 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 31 | 84.85 | 8840 | 41.7 | 3451.5 | 480 | 6792.5 | 6312.5 | 10.1 | 84.7927 | 6624.3 | 0 | 168.2 | 0 |  | 73.0613 | 6312.5
| 11815 | 9450 | 21265 | 0 | 0 | 103 | 21162 | 108 | 239.75 | 192.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 27 |  |  | 84.5661 | 8158.7097 | 41.7498 | 3509.732 | -240 | 218215.5323 | 212407.75 | 9.9886 | 86.3101 | 214023.32 | 6047.7823 | 4462.2123 | 270 |  | 79.304 | 212407.75