## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 325 | 355 | 680 | 0 | 0 | 3 | 680 | 55 | 6.4 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 85 | 9200 | 41.7 | 3451.5 | 360 | 7160 | 6800 | 10 | 85.3419 | 6697 | 0 | 463 | 0 |  | 78.7037 | 6800
2 | 680 | 0 | 680 | 0 | 0 | 4 | 680 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 2 | 85.2 | 9680 | 41.549 | 3274.83 | 480 | 10785.5 | 6868 | 10.1 | 84.1057 | 10672.2 | 3437.5 | 113.3 | 0 |  | 79.4907 | 6868
3 | 355 | 370 | 725 | 0 | 0 | 4 | 725 | 55 | 7.4 | 6.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 85.1 | 9440 | 41.752 | 3512.34 | -240 | 7010 | 7250 | 10 | 85.1439 | 6891.2 | 0 | 118.8 | 0 |  | 83.912 | 7250
4 | 75 | 730 | 805 | 0 | 0 | 4 | 805 | 109 | 1.4 | 13.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 4 | 84.3 | 7520 | 41.9 | 3685.5 | -1920 | 6250.75 | 8170.75 | 10.15 | 85.4721 | 6248 | 0 | 62.75 | 60 |  | 94.5689 | 8170.75
5 | 0 | 750 | 750 | 0 | 0 | 4 | 750 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 5 | 84.6 | 8240 | 42 | 3802.5 | 720 | 8220 | 7500 | 10 | 86.1432 | 8179.6 | 0 | 40.4 | 0 |  | 86.8056 | 7500
6 | 0 | 840 | 840 | 0 | 0 | 4 | 840 | 55 | 0 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.1 | 7040 | 42.002 | 3804.84 | -1200 | 7284 | 8484 | 10.1 | 86.3032 | 7241.6 | 0 | 42.4 | 0 |  | 98.1944 | 8484
7 | 670 | 145 | 815 | 0 | 0 | 4 | 815 | 110 | 12.92 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.55 | 8120 | 42.002 | 3804.84 | 1080 | 9311.5 | 8231.5 | 10.1 | 85.3905 | 9297.52 | 0 | 73.98 | 60 |  | 95.272 | 8231.5
8 | 765 | 0 | 765 | 0 | 0 | 4 | 765 | 55 | 15.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 8 | 84.8 | 8720 | 42.01 | 3814.2 | 600 | 8250 | 7650 | 10 | 85.7407 | 8178.75 | 0 | 71.25 | 0 |  | 88.5417 | 7650
9 | 780 | 0 | 780 | 0 | 0 | 1 | 780 | 55 | 15.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.7 | 8480 | 42.05 | 3861 | -240 | 7560 | 7800 | 10 | 85.9415 | 7423.5 | 0 | 136.5 | 0 |  | 90.2778 | 7800
10 | 0 | 765 | 765 | 0 | 0 | 2 | 765 | 50 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 85.1 | 9440 | 42.003 | 3806.01 | 960 | 8610 | 7650 | 10 | 85.1439 | 8453.4 | 0 | 156.6 | 0 |  | 88.5417 | 7650
11 | 0 | 770 | 770 | 0 | 0 | 4 | 770 | 50 | 0 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 11 | 85 | 9200 | 42.15 | 3978 | -240 | 7460 | 7700 | 10 | 85.3419 | 7377.8 | 0 | 82.2 | 0 |  | 89.1204 | 7700
12 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 55 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.25 | 9800 | 41.552 | 3278.34 | 600 | 7035 | 6435 | 9.9 | 85.7056 | 6852.4 | 0 | 182.6 | 0 |  | 74.4792 | 6435
13 | 415 | 305 | 720 | 0 | 0 | 3 | 720 | 70 | 9 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 85.3 | 9920 | 41.852 | 3629.34 | 120 | 7320 | 7200 | 10 | 84.7506 | 7088.3 | 0 | 231.7 | 0 |  | 83.3333 | 7200
14 | 350 | 250 | 600 | 0 | 0 | 4 | 600 | 50 | 7.1 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 85.3 | 9920 | 41.471 | 3183.57 | 0 | 6060 | 6060 | 10.1 | 83.9115 | 5669.45 | 0 | 390.55 | 0 |  | 70.1389 | 6060
15 | 0 | 660 | 660 | 0 | 0 | 4 | 660 | 50 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 15 | 85.1 | 9440 | 41.693 | 3443.31 | -480 | 6120 | 6600 | 10 | 85.1439 | 5752.4 | 0 | 367.6 | 0 |  | 76.3889 | 6600
16 | 345 | 325 | 670 | 0 | 0 | 4 | 670 | 55 | 7.3 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 84.9 | 8960 | 41.8 | 3568.5 | -480 | 6421 | 6901 | 10.3 | 83.0493 | 6188 | 0 | 233 | 0 |  | 79.8727 | 6901
17 | 360 | 275 | 635 | 0 | 0 | 4 | 635 | 55 | 6.95 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.75 | 8600 | 41.663 | 3408.21 | -360 | 6053.5 | 6413.5 | 10.1 | 84.991 | 5883.8 | 0 | 169.7 | 0 |  | 74.2303 | 6413.5
18 | 305 | 270 | 575 | 0 | 0 | 4 | 575 | 50 | 6.15 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.85 | 8840 | 41.22 | 2889.9 | 240 | 6162.5 | 5922.5 | 10.3 | 83.1462 | 6117.4 | 0 | 45.1 | 0 |  | 68.5475 | 5922.5
19 | 10 | 620 | 630 | 0 | 0 | 4 | 630 | 50 | 0.253 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 19 | 84.95 | 9080 | 41.321 | 3008.07 | 240 | 6760.5 | 6520.5 | 10.35 | 82.5519 | 6570.9 | 0 | 189.6 | 0 |  | 75.4688 | 6520.5
20 | 630 | 0 | 630 | 0 | 0 | 4 | 630 | 50 | 13.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 20 | 84.45 | 7880 | 41.4 | 3100.5 | -1200 | 5037 | 6237 | 9.9 | 87.3208 | 5103 | 0 | 4 | 70 |  | 72.1875 | 6237
21 | 0 | 625 | 625 | 0 | 0 | 1 | 625 | 50 | 0 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 21 | 84.65 | 8360 | 41.782 | 3547.44 | 480 | 6605 | 6125 | 9.8 | 87.7982 | 6420 | 0 | 185 | 0 |  | 70.8912 | 6125
22 | 0 | 520 | 520 | 0 | 0 | 3 | 520 | 45 | 0 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.7 | 8480 | 41.818 | 3589.56 | 120 | 5320 | 5200 | 10 | 85.9415 | 5274.4 | 0 | 45.6 | 0 |  | 60.1852 | 5200
23 | 0 | 515 | 515 | 0 | 0 | 3 | 515 | 45 | 0 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 23 | 84.75 | 8600 | 41.74 | 3498.3 | 120 | 5321.5 | 5201.5 | 10.1 | 84.991 | 5176.5 | 0 | 145 | 0 |  | 60.2025 | 5201.5
24 | 0 | 500 | 500 | 0 | 0 | 4 | 500 | 45 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85 | 9200 | 41.748 | 3507.66 | 600 | 5600 | 5000 | 10 | 85.3419 | 5356.55 | 0 | 243.45 | 0 |  | 57.8704 | 5000
25 | 110 | 465 | 575 | 0 | 0 | 3 | 575 | 50 | 2.05 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 84.95 | 9080 | 41.96 | 3755.7 | -120 | 5630 | 5750 | 10 | 85.4412 | 5542.8 | 0 | 87.2 | 0 |  | 66.5509 | 5750
26 | 285 | 265 | 550 | 0 | 0 | 4 | 550 | 45 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 85.05 | 9320 | 42.119 | 3941.73 | 240 | 5602.5 | 5362.5 | 9.75 | 87.4285 | 5496.4 | 0 | 106.1 | 0 |  | 62.066 | 5362.5
27 | 500 | 0 | 500 | 0 | 0 | 3 | 500 | 50 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 85.4 | 10160 | 41.831 | 3604.77 | 840 | 5715 | 4875 | 9.75 | 86.7234 | 5396 | 0 | 319 | 0 |  | 56.4236 | 4875
28 | 0 | 540 | 540 | 0 | 0 | 4 | 540 | 54 | 0 | 11.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85.4 | 10160 | 41.7 | 3451.5 | 0 | 5400 | 5400 | 10 | 84.5553 | 5305.8 | 0 | 94.2 | 0 |  | 62.5 | 5400
29 | 590 | 0 | 590 | 0 | 0 | 4 | 590 | 45 | 13.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.1 | 9440 | 41.7 | 3451.5 | -720 | 5062 | 5782 | 9.8 | 86.8815 | 4825.3 | 0 | 236.7 | 0 |  | 66.9213 | 5782
30 | 0 | 490 | 490 | 0 | 0 | 2 | 490 | 45 | 0 | 10.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85.2 | 9680 | 41.8788 | 3660.696 | 240 | 5140 | 4900 | 10 | 84.9468 | 4959.36 | 0 | 180.64 | 0 |  | 56.713 | 4900
31 | 460 | 10 | 470 | 0 | 0 | 3 | 470 | 85 | 10.15 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 85 | 9200 | 41.947 | 3740.49 | -480 | 4126 | 4606 | 9.8 | 87.0835 | 3970.35 | 0 | 155.65 | 0 |  | 53.3102 | 4606
| 8010 | 12010 | 20020 | 0 | 0 | 106 | 19914 | 110 | 166.4 | 247.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 39 |  |  | 84.9194 | 9006.4516 | 41.7843 | 3550.1499 | 360 | 204393.25 | 200595.75 | 10.0198 | 85.3335 | 199609.68 | 3437.5 | 4973.57 | 190 |  | 74.8939 | 200595.75