## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85 | 9200 | 40.45 | 1989 | -480 | 1069.3061 | 784 | 9.8 | 87.0835 | 906 | 765.3061 | 163.3061 | 0 |  | 9.0741 | 784
2 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 35 | 0 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 85 | 9200 | 40.6 | 2164.5 | 0 | 2404.8684 | 757.5 | 10.1 | 84.4969 | 2388.75 | 1647.3684 | 76.1184 | 60 |  | 8.7674 | 757.5
3 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.3 | 7520 | 40.88 | 2492.1 | -1680 | 1258.5513 | 656.5 | 10.1 | 85.8952 | 1139.6 | 2282.0513 | 178.9513 | 60 |  | 7.5984 | 656.5
4 | 0 | 145 | 145 | 0 | 0 | 4 | 145 | 35 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.95 | 9080 | 41.72 | 3474.9 | 1560 | 7011.4202 | 1515.25 | 10.45 | 81.7619 | 6840.1 | 3936.1702 | 231.3202 | 60 |  | 17.5376 | 1515.25
5 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 85 | 9200 | 41.69 | 3439.8 | 120 | 806 | 686 | 9.8 | 87.0835 | 692.85 | 0 | 113.15 | 0 |  | 7.9398 | 686
6 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 35 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 85.1 | 9440 | 41.73 | 3486.6 | 240 | 1553 | 1313 | 10.1 | 84.3008 | 1460 | 0 | 93 | 0 |  | 15.1968 | 1313
7 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 35 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.95 | 9080 | 41.2 | 2866.5 | -360 | 852 | 1212 | 10.1 | 84.5953 | 751.9 | 0 | 100.1 | 0 |  | 14.0278 | 1212
8 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.9 | 8960 | 41.32 | 3006.9 | -120 | 587 | 707 | 10.1 | 84.6939 | 532.9 | 0 | 54.1 | 0 |  | 8.1829 | 707
9 | 270 | 0 | 270 | 0 | 0 | 5 | 270 | 55 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.85 | 8840 | 41.599 | 3333.33 | -120 | 2539.5 | 2659.5 | 9.85 | 86.9448 | 2278.5 | 0 | 261 | 0 |  | 30.7812 | 2659.5
10 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 54 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85 | 9200 | 41.2 | 2866.5 | 360 | 1067 | 707 | 10.1 | 84.4969 | 817.6 | 0 | 309.4 | 60 |  | 8.1829 | 707
11 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85.05 | 9320 | 41.2 | 2866.5 | 120 | 2087.4158 | 791.25 | 10.55 | 80.7988 | 2029.4 | 1176.1658 | 58.0158 | 0 |  | 9.158 | 791.25
12 | 200 | 265 | 465 | 0 | 0 | 4 | 465 | 70 | 5.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 12 | 84.85 | 8840 | 41.577 | 3307.59 | -480 | 4216.5 | 4696.5 | 10.1 | 84.7927 | 4035.15 | 0 | 181.35 | 0 |  | 54.3576 | 4696.5
13 | 225 | 265 | 490 | 0 | 0 | 4 | 490 | 80 | 6 | 7.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.45 | 7880 | 41.54 | 3264.3 | -960 | 3964.5 | 4924.5 | 10.05 | 86.0175 | 3796.2 | 0 | 168.3 | 0 |  | 56.9965 | 4924.5
14 | 90 | 340 | 430 | 0 | 0 | 3 | 430 | 70 | 2.55 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.1 | 7040 | 41.599 | 3333.33 | -840 | 3503 | 4343 | 10.1 | 86.3032 | 3518.3 | 0 | 24.7 | 40 |  | 50.2662 | 4343
15 | 130 | 0 | 130 | 0 | 0 | 4 | 130 | 35 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.4 | 7760 | 41.56 | 3287.7 | 720 | 1987.5 | 1267.5 | 9.75 | 88.7687 | 1747.5 | 0 | 240 | 0 |  | 14.6701 | 1267.5
16 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 40 | 0 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.45 | 7880 | 41.27 | 2948.4 | 120 | 855 | 735 | 9.8 | 88.2118 | 661.2 | 0 | 193.8 | 0 |  | 8.5069 | 735
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.6 | 8240 | 41.33 | 3018.6 | 360 | 1095 | 735 | 9.8 | 87.9012 | 968.5 | 0 | 126.5 | 0 |  | 8.5069 | 735
18 | 0 | 130 | 130 | 0 | 0 | 3 | 130 | 35 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.7 | 8480 | 41.807 | 3576.69 | 240 | 1553 | 1313 | 10.1 | 85.0905 | 1241 | 0 | 312 | 0 |  | 15.1968 | 1313
19 | 105 | 0 | 105 | 0 | 0 | 4 | 105 | 54 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.7 | 8480 | 41.55 | 3276 | 0 | 1029 | 1029 | 9.8 | 87.6954 | 800.3 | 0 | 228.7 | 0 |  | 11.9097 | 1029
20 | 0 | 215 | 215 | 0 | 0 | 4 | 215 | 54 | 0 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.8 | 8720 | 41.85 | 3627 | 240 | 2368.5 | 2128.5 | 9.9 | 86.6067 | 2000.75 | 0 | 367.75 | 0 |  | 24.6354 | 2128.5
21 | 135 | 0 | 135 | 0 | 0 | 5 | 135 | 55 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.85 | 8840 | 41.67 | 3416.4 | 120 | 1537.5 | 1417.5 | 10.5 | 81.5625 | 1569.5 | 0 | 28 | 60 |  | 16.4062 | 1417.5
22 | 395 | 470 | 865 | 0 | 0 | 4 | 865 | 110 | 7.6 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84.3 | 7520 | 41.46 | 3170.7 | -1320 | 7416.5 | 8736.5 | 10.1 | 85.8952 | 7219.7 | 0 | 196.8 | 0 |  | 101.1169 | 8736.5
23 | 95 | 315 | 410 | 0 | 0 | 4 | 410 | 90 | 2 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 23 | 83.9 | 6560 | 40.656 | 2230.02 | -960 | 3181 | 4141 | 10.1 | 86.7152 | 3139 | 0 | 102 | 60 |  | 47.9282 | 4141
24 | 175 | 735 | 910 | 0 | 0 | 4 | 910 | 110 | 3.5 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 83.3 | 5120 | 41.81 | 3580.2 | -1440 | 7751 | 9191 | 10.1 | 87.975 | 7739.55 | 0 | 71.45 | 60 |  | 106.3773 | 9191
25 | 870 | 0 | 870 | 0 | 0 | 5 | 870 | 55 | 15.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.55 | 5720 | 41.9655 | 3762.135 | 600 | 9387 | 8787 | 10.1 | 87.4456 | 9396 | 0 | 51 | 60 |  | 101.7014 | 8787
26 | 170 | 465 | 635 | 0 | 0 | 3 | 635 | 110 | 3.1 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.45 | 7880 | 41.3 | 2983.5 | 2160 | 8573.5 | 6413.5 | 10.1 | 85.5917 | 8263.6 | 0 | 369.9 | 60 |  | 74.2303 | 6413.5
27 | 285 | 710 | 995 | 0 | 0 | 5 | 995 | 108 | 5.9 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.2 | 7280 | 41.602 | 3336.84 | -600 | 9350 | 9950 | 10 | 86.9597 | 9208.2 | 0 | 141.8 | 0 |  | 115.162 | 9950
28 | 180 | 625 | 805 | 0 | 0 | 4 | 805 | 110 | 3.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.65 | 8360 | 41.501 | 3218.67 | 1080 | 9210.5 | 8130.5 | 10.1 | 85.1903 | 9163.5 | 0 | 47 | 0 |  | 94.103 | 8130.5
| 3810 | 5100 | 8910 | 0 | 0 | 110 | 8800 | 110 | 82 | 110.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 |  |  | 84.5839 | 8201.4286 | 41.4156 | 3118.7395 | -1320 | 98215.0618 | 89728 | 10.0705 | 85.5726 | 94305.55 | 9807.0618 | 4489.5118 | 580 |  | 37.0899 | 89728