## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 370 | 720 | 1090 | 0 | 0 | 4 | 1090 | 100 | 7.2 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 1 | 83.75 | 6200 | 41.919 | 3707.73 | 3230 | 14402.5 | 11172.5 | 10.25 | 85.7532 | 14524.97 | 0 | 27.53 | 150 |  | 129.3113 | 11172.5
2 | 655 | 830 | 1485 | 0 | 0 | 4 | 1485 | 100 | 13 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 82.7 | 3740 | 41.659 | 3403.53 | -2460 | 12612.75 | 15072.75 | 10.15 | 88.8321 | 12633.9 | 0 | 38.85 | 60 |  | 174.4531 | 15072.75
3 | 835 | 285 | 1120 | 0 | 0 | 3 | 1120 | 109 | 16.1 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 3 | 83.9 | 6560 | 41.761 | 3522.87 | 2820 | 14020 | 11200 | 10 | 87.5823 | 13800 | 0 | 220 | 0 |  | 129.6296 | 11200
4 | 605 | 860 | 1465 | 0 | 0 | 4 | 1465 | 105 | 12.35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 82.5 | 3300 | 41.601 | 3335.67 | -3260 | 11756.25 | 15016.25 | 10.25 | 88.3999 | 11760.3 | 0 | 55.95 | 60 |  | 173.7992 | 15016.25
5 | 525 | 305 | 830 | 0 | 0 | 4 | 830 | 55 | 10.15 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 82.9 | 4180 | 41.851 | 3628.17 | 880 | 9304.5 | 8424.5 | 10.15 | 88.3978 | 9316.45 | 0 | 48.05 | 60 |  | 97.5058 | 8424.5
6 | 310 | 625 | 935 | 0 | 0 | 4 | 935 | 108 | 5.8 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84 | 6800 | 41.8315 | 3605.355 | 2620 | 12063.5 | 9443.5 | 10.1 | 86.5087 | 11929.05 | 0 | 134.45 | 0 |  | 109.2998 | 9443.5
7 | 585 | 695 | 1280 | 0 | 0 | 3 | 1280 | 110 | 11.3 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.1 | 7040 | 41.52 | 3240.9 | 240 | 13168 | 12928 | 10.1 | 86.3032 | 13193.25 | 0 | 34.75 | 60 |  | 149.6296 | 12928
8 | 105 | 135 | 240 | 0 | 0 | 4 | 240 | 70 | 2.7 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 83.8 | 6320 | 41.631 | 3370.77 | -720 | 1704 | 2424 | 10.1 | 86.9226 | 1742.4 | 0 | 21.6 | 60 |  | 28.0556 | 2424
9 | 195 | 175 | 370 | 0 | 0 | 3 | 370 | 110 | 4.1 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 9 | 83.45 | 5480 | 42.004 | 3807.18 | -840 | 3386.2473 | 3737 | 10.1 | 87.6566 | 3379.6 | 489.2473 | 66.6473 | 60 |  | 43.2523 | 3737
10 | 470 | 645 | 1115 | 0 | 0 | 3 | 1115 | 110 | 8.85 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 10 | 83.15 | 4760 | 42.052 | 3863.34 | -720 | 10541.5 | 11261.5 | 10.1 | 88.2957 | 10596.3 | 0 | 25.2 | 80 |  | 130.3414 | 11261.5
11 | 800 | 645 | 1445 | 0 | 0 | 6 | 1445 | 110 | 16.45 | 13.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 82.8 | 3960 | 41.85 | 3627 | -800 | 13939 | 14739 | 10.2 | 88.18 | 13963.5 | 0 | 35.5 | 60 |  | 170.5903 | 14739
12 | 710 | 590 | 1300 | 0 | 0 | 3 | 1300 | 105 | 14.8 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 12 | 83.1 | 4640 | 41.92 | 3708.9 | 680 | 14330 | 13650 | 10.5 | 85.0353 | 14326.35 | 0 | 63.65 | 60 |  | 157.9861 | 13650
13 | 875 | 405 | 1280 | 0 | 0 | 4 | 1280 | 109 | 17 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 13 | 83.2 | 4880 | 41.9 | 3685.5 | 240 | 13168 | 12928 | 10.1 | 88.1885 | 12826.1 | 0 | 341.9 | 0 |  | 149.6296 | 12928
14 | 5 | 510 | 515 | 0 | 0 | 4 | 515 | 100 | 0.2 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 83.5 | 5600 | 41.8 | 3568.5 | 720 | 5921.5 | 5201.5 | 10.1 | 87.551 | 5818.1 | 0 | 103.4 | 0 |  | 60.2025 | 5201.5
15 | 385 | 0 | 385 | 0 | 0 | 4 | 385 | 55 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.6 | 5840 | 41.5128 | 3232.476 | 240 | 4128.5 | 3888.5 | 10.1 | 87.3405 | 4066.1 | 0 | 122.4 | 60 |  | 45.0058 | 3888.5
16 | 0 | 395 | 395 | 0 | 0 | 3 | 395 | 54 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84 | 6800 | 41.22 | 2889.9 | 960 | 4910 | 3950 | 10 | 87.3738 | 4891 | 0 | 19 | 0 |  | 45.7176 | 3950
17 | 410 | 0 | 410 | 0 | 0 | 4 | 410 | 55 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84 | 6800 | 40.86 | 2468.7 | 0 | 4100 | 4100 | 10 | 87.3738 | 3920.1 | 0 | 189.9 | 10 |  | 47.4537 | 4100
18 | 275 | 320 | 595 | 0 | 0 | 4 | 595 | 55 | 5.8 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 83.5 | 5600 | 41.71 | 3463.2 | -1200 | 5047.5 | 6247.5 | 10.5 | 84.2157 | 5130 | 0 | 37.5 | 120 |  | 72.309 | 6247.5
19 | 385 | 0 | 385 | 0 | 0 | 3 | 385 | 50 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 83.95 | 6680 | 40.99 | 2620.8 | 1080 | 5450.0106 | 3811.5 | 9.9 | 88.3616 | 5213.6 | 558.5106 | 236.4106 | 0 |  | 44.1146 | 3811.5
20 | 255 | 85 | 340 | 0 | 0 | 3 | 340 | 50 | 5.35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 20 | 83.4 | 5360 | 41.402 | 3102.84 | -1320 | 2114 | 3434 | 10.1 | 87.7625 | 2044 | 0 | 130 | 60 |  | 39.7454 | 3434
21 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.7 | 8480 | 39.415 | 778.05 | 3120 | 4547.0426 | 693 | 9.9 | 86.8095 | 4314.3 | 734.0426 | 232.7426 | 0 |  | 8.0208 | 693
22 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 35 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 83.1 | 4640 | 40.82 | 2421.9 | -3840 | 2428.6505 | 1666.5 | 10.1 | 88.4031 | 2436 | 4602.1505 | 52.6505 | 60 |  | 19.2882 | 1666.5
23 | 290 | 30 | 320 | 0 | 0 | 3 | 320 | 50 | 6.1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 83.45 | 5480 | 41.71 | 3463.2 | 840 | 4040 | 3200 | 10 | 88.5332 | 3799.95 | 0 | 240.05 | 0 |  | 37.037 | 3200
24 | 380 | 720 | 1100 | 0 | 0 | 4 | 1100 | 108 | 8.9 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 24 | 84.1 | 7040 | 41.72 | 3474.9 | 1560 | 13055 | 11495 | 10.45 | 83.4127 | 13075.8 | 0 | 39.2 | 60 |  | 133.044 | 11495
25 | 505 | 305 | 810 | 0 | 0 | 3 | 810 | 108 | 10.9 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 83.55 | 5720 | 42.062 | 3875.04 | -1320 | 7063.5 | 8383.5 | 10.35 | 85.3334 | 7077 | 0 | 46.5 | 60 |  | 97.0312 | 8383.5
26 | 5 | 100 | 105 | 0 | 0 | 3 | 105 | 55 | 0.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83.85 | 6440 | 41.25 | 2925 | 720 | 1749 | 1029 | 9.8 | 89.4765 | 1691.2 | 0 | 57.8 | 0 |  | 11.9097 | 1029
27 | 475 | 0 | 475 | 0 | 0 | 3 | 475 | 50 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 83.85 | 6440 | 41.538 | 3261.96 | 0 | 4750 | 4750 | 10 | 87.687 | 4492.25 | 0 | 257.75 | 0 |  | 54.9769 | 4750
28 | 65 | 115 | 180 | 0 | 0 | 3 | 180 | 55 | 1.55 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 84.2 | 7280 | 41.86 | 3638.7 | 840 | 2577 | 1737 | 9.65 | 90.1137 | 2486.4 | 0 | 90.6 | 0 |  | 20.1042 | 1737
29 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 55 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 83.75 | 6200 | 41.53 | 3252.6 | -1080 | 2222.4865 | 1616 | 10.1 | 87.0267 | 2254 | 1686.4865 | 28.4865 | 60 |  | 18.7037 | 1616
30 | 85 | 135 | 220 | 0 | 0 | 4 | 220 | 70 | 2.45 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 83.9 | 6560 | 41.75 | 3510 | 360 | 2560 | 2200 | 10 | 87.5823 | 2445 | 0 | 115 | 0 |  | 25.463 | 2200
| 10790 | 9795 | 20585 | 0 | 0 | 106 | 20479 | 110 | 221.7 | 207.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 30 |  |  | 83.5917 | 5827.3333 | 41.555 | 3281.8227 | 3590 | 221060.4375 | 209400 | 10.1725 | 86.7358 | 219146.97 | 8070.4375 | 3113.4675 | 1200 |  | 80.787 | 209400