## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 54 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 83.85 | 6440 | 41.48 | 3194.1 | -120 | 3004.0106 | 1565.5 | 10.1 | 86.8188 | 2993 | 1558.5106 | 71.0106 | 60 |  | 18.1192 | 1565.5
2 | 10 | 185 | 195 | 0 | 0 | 4 | 195 | 35 | 0.1 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 83.9 | 6560 | 41.26 | 2936.7 | 120 | 2070 | 1950 | 10 | 87.5823 | 1887 | 0 | 183 | 0 |  | 22.5694 | 1950
3 | 255 | 0 | 255 | 0 | 0 | 3 | 255 | 40 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 83.9 | 6560 | 41.32 | 3006.9 | 0 | 2575.5 | 2575.5 | 10.1 | 86.7152 | 2584.2 | 0 | 11.3 | 20 |  | 29.809 | 2575.5
4 | 270 | 75 | 345 | 0 | 0 | 4 | 345 | 80 | 6.8 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.1 | 7040 | 42.06 | 3872.7 | 480 | 3930 | 3450 | 10 | 87.1663 | 3814.4 | 0 | 115.6 | 0 |  | 39.9306 | 3450
5 | 290 | 0 | 290 | 0 | 0 | 5 | 290 | 40 | 7.2 | 0 | 0 | 0 | 0 | 0 | 16.3 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 5 | 83.8 | 6320 | 41.99 | 3790.8 | -720 | 2151 | 2871 | 9.9 | 88.6787 | 1985.65 | 0 | 165.35 | 0 |  | 33.2292 | 2871
6 | 335 | 0 | 335 | 0 | 0 | 8 | 335 | 40 | 8.45 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 6 | 84.1 | 7040 | 42.042 | 3851.64 | 720 | 4103.5 | 3383.5 | 10.1 | 86.3032 | 3946.95 | 0 | 156.55 | 0 |  | 39.1609 | 3383.5
7 | 400 | 0 | 400 | 0 | 0 | 2 | 400 | 40 | 10.05 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 7 | 84.25 | 7400 | 41.72 | 3474.9 | 360 | 4400 | 4040 | 10.1 | 85.9968 | 4329.15 | 0 | 70.85 | 0 |  | 46.7593 | 4040
8 | 265 | 0 | 265 | 0 | 0 | 3 | 265 | 54 | 5.9 | 0 | 0 | 0 | 3.35 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ & ΒΛΑΒΗ ΨΥΓΕΙΩΝ Μον. ΝοΙ | 8 | 84.25 | 7400 | 41.601 | 3335.67 | 0 | 2610.25 | 2610.25 | 9.85 | 88.1795 | 2287.15 | 0 | 323.1 | 0 |  | 30.2112 | 2610.25
9 | 190 | 0 | 190 | 0 | 0 | 3 | 190 | 40 | 4.9 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 9 | 84.25 | 7400 | 41.601 | 3335.67 | 0 | 1919 | 1919 | 10.1 | 85.9968 | 1620.6 | 0 | 298.4 | 0 |  | 22.2106 | 1919
10 | 215 | 0 | 215 | 0 | 0 | 3 | 215 | 40 | 5.8 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 10 | 84.3 | 7520 | 41.95 | 3744 | 120 | 2291.5 | 2171.5 | 10.1 | 85.8952 | 2153.55 | 0 | 137.95 | 0 |  | 25.1331 | 2171.5
11 | 215 | 0 | 215 | 0 | 0 | 6 | 215 | 40 | 5.3 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 11 | 84.3 | 7520 | 41.82 | 3591.9 | 0 | 2128.5 | 2128.5 | 9.9 | 87.6304 | 2056.2 | 0 | 72.3 | 0 |  | 24.6354 | 2128.5
12 | 270 | 0 | 270 | 0 | 0 | 4 | 270 | 55 | 6.3 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 12 | 84.05 | 6920 | 41.892 | 3676.14 | -600 | 3424.8723 | 2727 | 10.1 | 86.4059 | 3197.4 | 1297.8723 | 227.4723 | 0 |  | 31.5625 | 2727
13 | 275 | 0 | 275 | 0 | 0 | 4 | 275 | 40 | 7.3 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 13 | 84.8 | 8720 | 41.631 | 3370.77 | 1800 | 5124.375 | 2777.5 | 10.1 | 84.8917 | 5110.7 | 546.875 | 73.675 | 60 |  | 32.147 | 2777.5
14 | 295 | 0 | 295 | 0 | 0 | 8 | 295 | 40 | 6.65 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 14 | 84.6 | 8240 | 41.002 | 2634.84 | -480 | 2499.5 | 2979.5 | 10.1 | 85.2903 | 2255.7 | 0 | 243.8 | 0 |  | 34.485 | 2979.5
15 | 300 | 0 | 300 | 0 | 0 | 8 | 300 | 55 | 7.65 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 15 | 84.65 | 8360 | 41.74 | 3498.3 | 120 | 3060 | 2940 | 9.8 | 87.7982 | 2929.4 | 0 | 130.6 | 0 |  | 34.0278 | 2940
16 | 325 | 0 | 325 | 0 | 0 | 8 | 325 | 55 | 7.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 16 | 84.75 | 8600 | 41.8 | 3568.5 | 240 | 3522.5 | 3282.5 | 10.1 | 84.991 | 3292.3 | 0 | 230.2 | 0 |  | 37.9919 | 3282.5
17 | 290 | 0 | 290 | 0 | 0 | 8 | 290 | 40 | 7.25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 17 | 84.7 | 8480 | 42.094 | 3912.48 | -120 | 2736.5 | 2856.5 | 9.85 | 87.2502 | 2567 | 0 | 169.5 | 0 |  | 33.0613 | 2856.5
18 | 430 | 0 | 430 | 0 | 0 | 1 | 430 | 40 | 10.65 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 18 | 84.4 | 7760 | 41.755 | 3515.85 | -720 | 3623 | 4343 | 10.1 | 85.6926 | 3646.75 | 0 | 36.25 | 60 |  | 50.2662 | 4343
19 | 250 | 0 | 250 | 0 | 0 | 1 | 250 | 40 | 6.2 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 19 | 84.6 | 8240 | 41.848 | 3624.66 | 480 | 2930 | 2450 | 9.8 | 87.9012 | 2640 | 0 | 290 | 0 |  | 28.3565 | 2450
20 | 260 | 0 | 260 | 0 | 0 | 1 | 260 | 50 | 6.2 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 20 | 84.5 | 8000 | 41.7 | 3451.5 | -240 | 2282 | 2522 | 9.7 | 89.0164 | 2032.5 | 0 | 249.5 | 0 |  | 29.1898 | 2522
21 | 260 | 0 | 260 | 0 | 0 | 1 | 260 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 21 | 84.65 | 8360 | 41.63 | 3369.6 | 360 | 2960 | 2600 | 10 | 86.0422 | 2801.05 | 0 | 158.95 | 0 |  | 30.0926 | 2600
22 | 340 | 0 | 340 | 0 | 0 | 1 | 340 | 55 | 7.6 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 0 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 22 | 84.15 | 7160 | 42 | 3802.5 | -1200 | 2234 | 3434 | 10.1 | 86.2009 | 2102.4 | 0 | 131.6 | 0 |  | 39.7454 | 3434
23 | 165 | 140 | 305 | 0 | 0 | 3 | 305 | 40 | 4.1 | 3.2 | 0 | 0 | 0 | 0 | 16.85 | 0 | 0 | 0 | 1 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 23 | 84.2 | 7280 | 41.84 | 3615.3 | 120 | 3231 | 3111 | 10.2 | 85.2546 | 3283.2 | 0 | 7.8 | 60 |  | 36.0069 | 3111
24 | 0 | 320 | 320 | 0 | 0 | 4 | 320 | 40 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.4 | 7760 | 41.62 | 3357.9 | 480 | 3712 | 3232 | 10.1 | 85.6926 | 3693.8 | 0 | 78.2 | 60 |  | 37.4074 | 3232
25 | 0 | 335 | 335 | 0 | 0 | 4 | 335 | 45 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 25 | 84.35 | 7640 | 41.79 | 3556.8 | -120 | 3230 | 3350 | 10 | 86.6517 | 3064.95 | 0 | 165.05 | 0 |  | 38.7731 | 3350
26 | 0 | 310 | 310 | 0 | 0 | 4 | 310 | 40 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.6 | 8240 | 41.94 | 3732.3 | 600 | 3731 | 3131 | 10.1 | 85.2903 | 3686.5 | 0 | 44.5 | 0 |  | 36.2384 | 3131
27 | 170 | 200 | 370 | 0 | 0 | 4 | 370 | 70 | 4.65 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 27 | 84.3 | 7520 | 42.028 | 3835.26 | -720 | 5576.5855 | 3737 | 10.1 | 85.8952 | 5587.5 | 2559.5855 | 49.0855 | 60 |  | 43.2523 | 3737
28 | 0 | 340 | 340 | 0 | 0 | 4 | 340 | 55 | 0 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.25 | 7400 | 41.62 | 3357.9 | -120 | 4361.8723 | 3434 | 10.1 | 85.9968 | 4292.4 | 1047.8723 | 69.4723 | 0 |  | 39.7454 | 3434
29 | 0 | 405 | 405 | 0 | 0 | 5 | 405 | 53 | 0 | 9.4 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 29 | 84.3 | 7520 | 41.839 | 3614.13 | 120 | 4210.5 | 4090.5 | 10.1 | 85.8952 | 4149.65 | 0 | 60.85 | 0 |  | 47.3438 | 4090.5
30 | 0 | 390 | 390 | 0 | 0 | 3 | 390 | 40 | 0 | 9.4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 30 | 84.65 | 8360 | 41.951 | 3745.17 | 840 | 4740 | 3900 | 10 | 86.0422 | 4699 | 0 | 41 | 0 |  | 45.1389 | 3900
31 | 0 | 430 | 430 | 0 | 0 | 4 | 430 | 40 | 0 | 10.6 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙΙ | 31 | 84.15 | 7160 | 41.903 | 3689.01 | -1200 | 3143 | 4343 | 10.1 | 86.2009 | 2911 | 0 | 292 | 60 |  | 50.2662 | 4343
| 6230 | 3130 | 9360 | 0 | 0 | 124 | 9236 | 80 | 153.05 | 78 | 64.4 | 0 | 3.35 | 0 | 441.15 | 0 | 0 | 0 | 42 | 19 |  |  | 84.3242 | 7578.0645 | 41.757 | 3518.19 | 600 | 101515.9658 | 93905.25 | 10.0326 | 86.4227 | 97601.05 | 7010.7158 | 4354.9158 | 440 |  | 35.0602 | 93905.25