## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 390 | 390 | 0 | 0 | 3 | 390 | 54 | 0 | 9.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 1 | 84 | 6800 | 41.801 | 3569.67 | -360 | 3579 | 3939 | 10.1 | 86.5087 | 3564 | 0 | 75 | 60 |  | 45.5903 | 3939
2 | 0 | 410 | 410 | 0 | 0 | 3 | 410 | 40 | 0 | 10.6 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 2 | 83.75 | 6200 | 41.9 | 3685.5 | -600 | 3541 | 4141 | 10.1 | 87.0267 | 3594.12 | 0 | 6.88 | 60 |  | 47.9282 | 4141
3 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 40 | 0 | 10.4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 3 | 84.2 | 7280 | 41.712 | 3465.54 | 1080 | 5196 | 4116 | 9.8 | 88.7344 | 4975.6 | 0 | 220.4 | 0 |  | 47.6389 | 4116
4 | 0 | 605 | 605 | 0 | 0 | 4 | 605 | 54 | 0 | 12.4 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 4 | 84 | 6800 | 41.852 | 3629.34 | -480 | 5842.25 | 6322.25 | 10.45 | 83.6113 | 5883.8 | 0 | 18.45 | 60 |  | 73.1742 | 6322.25
5 | 0 | 490 | 490 | 0 | 0 | 4 | 490 | 54 | 0 | 9.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 5 | 84.1 | 7040 | 41.602 | 3336.84 | 240 | 5189 | 4949 | 10.1 | 86.3032 | 5169.6 | 0 | 79.4 | 60 |  | 57.2801 | 4949
6 | 0 | 660 | 660 | 0 | 0 | 3 | 660 | 54 | 0 | 12.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 6 | 84.1 | 7040 | 41.64 | 3381.3 | 0 | 6600 | 6600 | 10 | 87.1663 | 6489.8 | 0 | 110.2 | 0 |  | 76.3889 | 6600
7 | 0 | 705 | 705 | 0 | 0 | 2 | 705 | 55 | 0 | 13.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 7 | 84.4 | 7760 | 41.761 | 3522.87 | 720 | 7840.5 | 7120.5 | 10.1 | 85.6926 | 7767.2 | 0 | 73.3 | 0 |  | 82.4132 | 7120.5
8 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 53 | 0 | 12.3 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 8 | 84.45 | 7880 | 41.751 | 3511.17 | 120 | 6533.5 | 6413.5 | 10.1 | 85.5917 | 6384.95 | 0 | 208.55 | 60 |  | 74.2303 | 6413.5
9 | 0 | 590 | 590 | 0 | 0 | 4 | 590 | 55 | 0 | 13 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 9 | 83.75 | 6200 | 42.001 | 3803.67 | -1680 | 4279 | 5959 | 10.1 | 87.0267 | 4118.4 | 0 | 220.6 | 60 |  | 68.9699 | 5959
10 | 0 | 520 | 520 | 0 | 0 | 4 | 520 | 40 | 0 | 13.2 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 10 | 84.35 | 7640 | 41.8 | 3568.5 | 1440 | 6692 | 5252 | 10.1 | 85.7938 | 6643 | 0 | 109 | 60 |  | 60.787 | 5252
11 | 0 | 540 | 540 | 0 | 0 | 2 | 540 | 55 | 0 | 11.9 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 11 | 84.4 | 7760 | 41.852 | 3629.34 | 120 | 5601 | 5481 | 10.15 | 85.2705 | 5635.6 | 0 | 25.4 | 60 |  | 63.4375 | 5481
12 | 0 | 530 | 530 | 0 | 0 | 3 | 530 | 40 | 0 | 12.1 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 12 | 84.6 | 8240 | 41.9015 | 3687.255 | 480 | 5833 | 5353 | 10.1 | 85.2903 | 5646.75 | 0 | 186.25 | 0 |  | 61.956 | 5353
13 | 0 | 630 | 630 | 0 | 0 | 4 | 630 | 55 | 0 | 13.15 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 13 | 84.7 | 8480 | 41.998 | 3800.16 | 240 | 6414 | 6174 | 9.8 | 87.6954 | 6243.1 | 0 | 170.9 | 0 |  | 71.4583 | 6174
14 | 0 | 575 | 575 | 0 | 0 | 4 | 575 | 44 | 0 | 14.65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΕΤΗΣΙΑ ΣΥΝΤΗΡΗΣΗ Μον. ΝοΙ | 14 | 84.55 | 8120 | 41.7 | 3451.5 | -360 | 5447.5 | 5807.5 | 10.1 | 85.3905 | 5445 | 0 | 62.5 | 60 |  | 67.2164 | 5807.5
15 | 445 | 110 | 555 | 0 | 0 | 4 | 555 | 100 | 10.85 | 2.4 | 0 | 0 | 1 | 0 | 0 | 0 | 2.75 | 0 | 2 | 2 | ΒΛ. ΚΥΚΛ. ΨΥΞΗΣ ΝοΙ & ΒΛ. Δ/Κ Ρ25 | 15 | 84.75 | 8600 | 41.998 | 3800.16 | 480 | 6085.5 | 5605.5 | 10.1 | 84.991 | 5942.2 | 0 | 203.3 | 60 |  | 64.8785 | 5605.5
16 | 70 | 495 | 565 | 0 | 0 | 4 | 565 | 75 | 2.1 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 16 | 84.4 | 7760 | 42 | 3802.5 | -840 | 4866.5 | 5706.5 | 10.1 | 85.6926 | 4662 | 0 | 264.5 | 60 |  | 66.0475 | 5706.5
17 | 0 | 540 | 540 | 0 | 0 | 4 | 540 | 50 | 0 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 17 | 84.5 | 8000 | 41.898 | 3683.16 | 240 | 5694 | 5454 | 10.1 | 85.491 | 5655 | 0 | 99 | 60 |  | 63.125 | 5454
18 | 250 | 315 | 565 | 0 | 0 | 4 | 565 | 45 | 5.95 | 6.95 | 0 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛ. ΚΥΚΛ. ΨΥΞΗΣ ΝοΙ (ΨΥΓΕΙΟ Νο5) | 18 | 84.5 | 8000 | 41.9 | 3685.5 | 0 | 5537 | 5537 | 9.8 | 88.108 | 5345.4 | 0 | 191.6 | 0 |  | 64.0856 | 5537
19 | 545 | 0 | 545 | 0 | 0 | 2 | 545 | 45 | 11.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.55 | 8120 | 41.998 | 3800.16 | 120 | 5570 | 5450 | 10 | 86.2444 | 5365 | 0 | 205 | 0 |  | 63.0787 | 5450
20 | 0 | 530 | 530 | 0 | 0 | 4 | 530 | 45 | 0 | 12.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.3 | 7520 | 42.057 | 3869.19 | -600 | 4753 | 5353 | 10.1 | 85.8952 | 4765.6 | 0 | 47.4 | 60 |  | 61.956 | 5353
21 | 125 | 555 | 680 | 0 | 0 | 3 | 680 | 90 | 3.2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 21 | 84.2 | 7280 | 42.056 | 3868.02 | -240 | 6628 | 6868 | 10.1 | 86.0987 | 6445.95 | 0 | 242.05 | 60 |  | 79.4907 | 6868
22 | 550 | 45 | 595 | 0 | 0 | 4 | 595 | 44 | 12.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 22 | 84.2 | 7280 | 42.048 | 3858.66 | 0 | 5831 | 5831 | 9.8 | 88.7344 | 5685 | 0 | 146 | 0 |  | 67.4884 | 5831
23 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 45 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.3 | 7520 | 42.002 | 3804.84 | 240 | 5744.5 | 5504.5 | 10.1 | 85.8952 | 5438.5 | 0 | 306 | 0 |  | 63.7095 | 5504.5
24 | 25 | 465 | 490 | 0 | 0 | 3 | 490 | 45 | 0.4 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.3 | 7520 | 41.896 | 3680.82 | 0 | 5120.5 | 5120.5 | 10.45 | 83.0183 | 4978.6 | 0 | 141.9 | 0 |  | 59.265 | 5120.5
25 | 520 | 0 | 520 | 0 | 0 | 4 | 520 | 53 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.2 | 7280 | 41.8385 | 3613.545 | -240 | 5012 | 5252 | 10.1 | 86.0987 | 4909.8 | 0 | 102.2 | 0 |  | 60.787 | 5252
26 | 10 | 545 | 555 | 0 | 0 | 4 | 555 | 50 | 0.15 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.3 | 7520 | 41.942 | 3734.64 | 240 | 5790 | 5550 | 10 | 86.7541 | 5126.3 | 0 | 663.7 | 0 |  | 64.2361 | 5550
27 | 560 | 10 | 570 | 0 | 0 | 3 | 570 | 45 | 16.15 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.6 | 8240 | 41.93 | 3720.6 | 720 | 6420 | 5700 | 10 | 86.1432 | 6157.5 | 0 | 262.5 | 0 |  | 65.9722 | 5700
28 | 0 | 155 | 155 | 0 | 0 | 4 | 155 | 45 | 0 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.6 | 8240 | 40.83 | 2433.6 | 0 | 1565.5 | 1565.5 | 10.1 | 85.2903 | 1241 | 0 | 384.5 | 60 |  | 18.1192 | 1565.5
29 | 210 | 0 | 210 | 0 | 0 | 3 | 210 | 45 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.25 | 7400 | 41.072 | 2716.74 | -840 | 2198.9487 | 2121 | 10.1 | 85.9968 | 2079.4 | 917.9487 | 119.5487 | 0 |  | 24.5486 | 2121
30 | 0 | 265 | 265 | 0 | 0 | 4 | 265 | 40 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.3 | 7520 | 41.822 | 3594.24 | 120 | 2770 | 2650 | 10 | 86.7541 | 2650.05 | 0 | 119.95 | 0 |  | 30.6713 | 2650
| 3855 | 11730 | 15585 | 0 | 0 | 105 | 15480 | 100 | 87.85 | 262.9 | 327 | 0 | 9.7 | 0 | 0 | 0 | 2.75 | 0 | 17 | 45 |  |  | 84.32 | 7568 | 41.8186 | 3590.301 | 360 | 158174.1987 | 156896.25 | 10.0671 | 86.1349 | 154008.22 | 917.9487 | 5065.9787 | 900 |  | 60.531