## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 215 | 70 | 285 | 0 | 0 | 4 | 285 | 54 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.6 | 8240 | 41.562 | 3290.04 | 720 | 3598.5 | 2878.5 | 10.1 | 85.2903 | 3270.4 | 0 | 388.1 | 60 |  | 33.316 | 2878.5
2 | 145 | 445 | 590 | 0 | 0 | 3 | 590 | 70 | 3.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.1 | 7040 | 41.872 | 3652.74 | -1200 | 4759 | 5959 | 10.1 | 86.3032 | 4780.4 | 0 | 38.6 | 60 |  | 68.9699 | 5959
3 | 480 | 90 | 570 | 0 | 0 | 3 | 570 | 89 | 10.2 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.1 | 7040 | 41.66 | 3404.7 | 0 | 5700 | 5700 | 10 | 87.1663 | 5549.25 | 0 | 150.75 | 0 |  | 65.9722 | 5700
4 | 0 | 495 | 495 | 0 | 0 | 4 | 495 | 45 | 0 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.8 | 8720 | 42.049 | 3859.83 | 1680 | 6679.5 | 4999.5 | 10.1 | 84.8917 | 6555.4 | 0 | 124.1 | 0 |  | 57.8646 | 4999.5
5 | 540 | 65 | 605 | 0 | 0 | 4 | 605 | 53 | 12.1 | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.65 | 8360 | 41.851 | 3628.17 | -360 | 5750.5 | 6110.5 | 10.1 | 85.1903 | 5563.95 | 0 | 186.55 | 0 |  | 70.7234 | 6110.5
6 | 0 | 485 | 485 | 0 | 0 | 3 | 485 | 53 | 0 | 11.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.9 | 8960 | 41.999 | 3801.33 | 600 | 5498.5 | 4898.5 | 10.1 | 84.6939 | 5368.05 | 0 | 130.45 | 0 |  | 56.6956 | 4898.5
7 | 350 | 105 | 455 | 0 | 0 | 4 | 455 | 53 | 8.2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.6 | 8240 | 41.468 | 3180.06 | -720 | 3875.5 | 4595.5 | 10.1 | 85.2903 | 3665.4 | 0 | 210.1 | 0 |  | 53.1887 | 4595.5
8 | 0 | 355 | 355 | 0 | 0 | 3 | 355 | 45 | 0 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.7 | 8480 | 41.261 | 2937.87 | 240 | 5027.6277 | 3585.5 | 10.1 | 85.0905 | 4730.4 | 1202.1277 | 297.2277 | 0 |  | 41.4988 | 3585.5
9 | 435 | 10 | 445 | 0 | 0 | 4 | 445 | 45 | 9.85 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.4 | 7760 | 41.6 | 3334.5 | -720 | 3774.5 | 4494.5 | 10.1 | 85.6926 | 3577 | 0 | 197.5 | 0 |  | 52.0197 | 4494.5
10 | 5 | 485 | 490 | 0 | 0 | 4 | 490 | 45 | 0.15 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.65 | 8360 | 41.652 | 3395.34 | 600 | 5500 | 4900 | 10 | 86.0422 | 5210.28 | 0 | 289.72 | 0 |  | 56.713 | 4900
11 | 0 | 515 | 515 | 0 | 0 | 3 | 515 | 54 | 0 | 12.05 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Αποκατάσταση βλάβης υδραυλ. Κυκλ. Υδροληψίας | 11 | 84.85 | 8840 | 41.853 | 3630.51 | 480 | 5681.5 | 5201.5 | 10.1 | 84.7927 | 5498.1 | 0 | 183.4 | 0 |  | 60.2025 | 5201.5
12 | 475 | 0 | 475 | 0 | 0 | 4 | 475 | 45 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 0 | 2 | 0 | Αποκατάσταση βλάβης υδραυλ. Κυκλ. Υδροληψίας | 12 | 84.8 | 8720 | 41.84 | 3615.3 | -120 | 4630 | 4750 | 10 | 85.7407 | 4241.3 | 0 | 388.7 | 0 |  | 54.9769 | 4750
13 | 260 | 265 | 525 | 0 | 0 | 3 | 525 | 55 | 5.7 | 5.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 13 | 84.7 | 8480 | 41.829 | 3602.43 | -240 | 5062.5 | 5302.5 | 10.1 | 85.0905 | 5078.85 | 0 | 43.65 | 60 |  | 61.3715 | 5302.5
14 | 385 | 220 | 605 | 0 | 0 | 3 | 605 | 45 | 9.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84.6 | 8240 | 41.788 | 3554.46 | -240 | 5749.5 | 5989.5 | 9.9 | 87.0133 | 5439 | 0 | 310.5 | 0 |  | 69.3229 | 5989.5
15 | 470 | 30 | 500 | 0 | 0 | 4 | 500 | 45 | 10.5 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.75 | 8600 | 41.6 | 3334.5 | 360 | 5260 | 4900 | 9.8 | 87.5928 | 4950.6 | 0 | 309.4 | 0 |  | 56.713 | 4900
16 | 5 | 560 | 565 | 0 | 0 | 4 | 565 | 53 | 0.1 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000 | 41.847 | 3623.49 | -600 | 5106.5 | 5706.5 | 10.1 | 85.491 | 5058.5 | 0 | 108 | 60 |  | 66.0475 | 5706.5
17 | 225 | 360 | 585 | 0 | 0 | 3 | 585 | 55 | 5.05 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 17 | 84.9 | 8960 | 41.866 | 3645.72 | 960 | 6751.5 | 5791.5 | 9.9 | 86.4048 | 6681.75 | 0 | 69.75 | 0 |  | 67.0312 | 5791.5
18 | 35 | 753 | 788 | 0 | 0 | 4 | 788 | 55 | 1 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 85.25 | 9800 | 41.8 | 3568.5 | 840 | 8720 | 7880 | 10 | 84.8486 | 8493.75 | 0 | 226.25 | 0 |  | 91.2037 | 7880
19 | 305 | 435 | 740 | 0 | 0 | 4 | 740 | 108 | 6.15 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 19 | 85 | 9200 | 41.983 | 3782.61 | -600 | 6689 | 7289 | 9.85 | 86.6415 | 6445.4 | 0 | 243.6 | 0 |  | 84.3634 | 7289
20 | 25 | 645 | 670 | 0 | 0 | 3 | 670 | 83 | 0.8 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.9 | 8960 | 41.9 | 3685.5 | -240 | 6527 | 6767 | 10.1 | 84.6939 | 6615.6 | 0 | 31.4 | 120 |  | 78.3218 | 6767
21 | 625 | 35 | 660 | 0 | 0 | 0 | 660 | 90 | 12.8 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 21 | 84.25 | 7400 | 41.662 | 3407.04 | -1560 | 5040 | 6600 | 10 | 86.8568 | 4812.7 | 0 | 227.3 | 0 |  | 76.3889 | 6600
22 | 32 | 615 | 647 | 0 | 0 | 8 | 647 | 53 | 0.9 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.25 | 7400 | 41.85 | 3627 | 0 | 6534.7 | 6534.7 | 10.1 | 85.9968 | 6449.3 | 0 | 145.4 | 60 |  | 75.6331 | 6534.7
23 | 698 | 20 | 718 | 0 | 0 | 0 | 718 | 53 | 15.1 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.2 | 7280 | 41.859 | 3637.53 | -120 | 7131.8 | 7251.8 | 10.1 | 86.0987 | 7027.2 | 0 | 164.6 | 60 |  | 83.9329 | 7251.8
24 | 0 | 645 | 645 | 0 | 0 | 0 | 645 | 55 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.25 | 7400 | 42.08 | 3896.1 | 120 | 6666.75 | 6546.75 | 10.15 | 85.5732 | 6664 | 0 | 62.75 | 60 |  | 75.7726 | 6546.75
25 | 705 | 130 | 835 | 0 | 0 | 4 | 835 | 110 | 14.6 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 25 | 84.3 | 7520 | 42.05 | 3861 | 120 | 8553.5 | 8433.5 | 10.1 | 85.8952 | 8288 | 0 | 265.5 | 0 |  | 97.61 | 8433.5
26 | 0 | 620 | 620 | 0 | 0 | 9 | 620 | 55 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.3 | 7520 | 42 | 3802.5 | 0 | 6262 | 6262 | 10.1 | 85.8952 | 6285.3 | 0 | 36.7 | 60 |  | 72.4769 | 6262
27 | 655 | 110 | 765 | 0 | 0 | 4 | 765 | 90 | 13.9 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 83.5 | 5600 | 42.05 | 3861 | -1920 | 5959.5 | 7879.5 | 10.3 | 85.851 | 6000.6 | 0 | 18.9 | 60 |  | 91.1979 | 7879.5
28 | 130 | 650 | 780 | 0 | 0 | 4 | 780 | 109 | 3 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 28 | 83.3 | 5120 | 42.052 | 3863.34 | -480 | 7398 | 7878 | 10.1 | 87.975 | 7363.59 | 0 | 94.41 | 60 |  | 91.1806 | 7878
29 | 500 | 85 | 585 | 6 | 0 | 0 | 585 | 53 | 10.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.1 | 7040 | 41.8 | 3568.5 | 1920 | 7828.5 | 5908.5 | 10.1 | 86.3032 | 7665 | 0 | 163.5 | 0 |  | 68.3854 | 5908.5
30 | 123 | 685 | 808 | 0 | 0 | 6 | 808 | 80 | 3.1 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 83.5 | 5600 | 41.999 | 3801.33 | -1440 | 6720.8 | 8160.8 | 10.1 | 87.551 | 6775.56 | 0 | 5.24 | 60 |  | 94.4537 | 8160.8
31 | 562 | 108 | 670 | 0 | 0 | 4 | 670 | 90 | 11 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 31 | 84 | 6800 | 41.902 | 3687.84 | 1200 | 7967 | 6767 | 10.1 | 86.5087 | 7865 | 0 | 162 | 60 |  | 78.3218 | 6767
| 8385 | 10091 | 18476 | 6 | 0 | 110 | 18220.2 | 110 | 183.6 | 218 | 0 | 0 | 4 | 0 | 0 | 0 | 6.7 | 0 | 36 | 38 |  |  | 84.4419 | 7860.6452 | 41.8253 | 3598.0897 | -720 | 186403.6777 | 185921.55 | 10.0629 | 85.9238 | 181969.63 | 1202.1277 | 5274.0477 | 840 |  | 69.4152 | 185921.55