## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 55 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.25 | 7400 | 41.805 | 3574.35 | 600 | 7316.5 | 6716.5 | 10.1 | 85.9968 | 7356.12 | 0 | 20.38 | 60 |  | 77.7373 | 6716.5
2 | 267 | 368 | 635 | 0 | 0 | 4 | 635 | 54 | 5.4 | 7.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.8 | 6320 | 41.788 | 3554.46 | -1080 | 5587.5 | 6667.5 | 10.5 | 83.6113 | 5555.3 | 0 | 92.2 | 60 |  | 77.1701 | 6667.5
3 | 648 | 67 | 715 | 0 | 0 | 4 | 715 | 106 | 12.75 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.15 | 7160 | 41.798 | 3566.16 | 840 | 8061.5 | 7221.5 | 10.1 | 86.2009 | 8043.8 | 0 | 17.7 | 0 |  | 83.5822 | 7221.5
4 | 0 | 502 | 502 | 0 | 0 | 3 | 502 | 45 | 0 | 11.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.3 | 7520 | 41.41 | 3112.2 | 360 | 5430.2 | 5070.2 | 10.1 | 85.8952 | 5415 | 0 | 75.2 | 60 |  | 58.6829 | 5070.2
5 | 535 | 6 | 541 | 0 | 0 | 4 | 541 | 45 | 12.25 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480 | 42.049 | 3859.83 | 960 | 6900.2905 | 5464.1 | 10.1 | 85.0905 | 6898.7 | 476.1905 | 61.5905 | 60 |  | 63.2419 | 5464.1
6 | 13 | 571 | 584 | 0 | 0 | 3 | 584 | 53 | 0.4 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.45 | 7880 | 41.77 | 3533.4 | -600 | 5298.4 | 5898.4 | 10.1 | 85.5917 | 5100 | 0 | 198.4 | 0 |  | 68.2685 | 5898.4
7 | 505 | 90 | 595 | 0 | 0 | 4 | 595 | 79 | 11.5 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 7 | 84.15 | 7160 | 41.64 | 3381.3 | -720 | 5289.5 | 6009.5 | 10.1 | 86.2009 | 5299.8 | 0 | 19.7 | 30 |  | 69.5544 | 6009.5
8 | 0 | 485 | 485 | 0 | 0 | 3 | 485 | 45 | 0 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.1 | 7040 | 41.952 | 3746.34 | -120 | 4778.5 | 4898.5 | 10.1 | 86.3032 | 4708.5 | 0 | 130 | 60 |  | 56.6956 | 4898.5
9 | 485 | 0 | 485 | 0 | 0 | 4 | 485 | 45 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 41.798 | 3566.16 | 480 | 5330 | 4850 | 10 | 86.7541 | 5224.6 | 0 | 105.4 | 0 |  | 56.1343 | 4850
10 | 0 | 508 | 508 | 0 | 0 | 4 | 508 | 45 | 0 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.3 | 7520 | 41.76 | 3521.7 | 0 | 5080 | 5080 | 10 | 86.7541 | 5050.95 | 0 | 29.05 | 0 |  | 58.7963 | 5080
11 | 485 | 0 | 485 | 0 | 0 | 3 | 485 | 45 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.45 | 7880 | 41.842 | 3617.64 | 360 | 5210 | 4850 | 10 | 86.4476 | 5110 | 0 | 100 | 0 |  | 56.1343 | 4850
12 | 15 | 485 | 500 | 0 | 0 | 4 | 500 | 45 | 0.4 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 83.9 | 6560 | 41.809 | 3579.03 | -1320 | 3680 | 5000 | 10 | 87.5823 | 3503.2 | 0 | 176.8 | 0 |  | 57.8704 | 5000
13 | 517 | 0 | 517 | 0 | 0 | 3 | 517 | 45 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 83.9 | 6560 | 41.698 | 3449.16 | 0 | 5221.7 | 5221.7 | 10.1 | 86.7152 | 5168.4 | 0 | 113.3 | 60 |  | 60.4363 | 5221.7
14 | 0 | 490 | 490 | 0 | 0 | 4 | 490 | 45 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84 | 6800 | 41.4 | 3100.5 | 240 | 5189 | 4949 | 10.1 | 86.5087 | 5145 | 0 | 44 | 0 |  | 57.2801 | 4949
15 | 471 | 5 | 476 | 0 | 0 | 3 | 476 | 45 | 10.9 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.55 | 5720 | 41.22 | 2889.9 | -1080 | 3821.8 | 4901.8 | 10.2979 | 85.7652 | 3810 | 0 | 11.8 | 0 |  | 56.7338 | 4901.8
16 | 0 | 532 | 532 | 0 | 0 | 4 | 532 | 45 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 83.6 | 5840 | 41.33 | 3018.6 | 120 | 5440 | 5320 | 10 | 88.2139 | 5436 | 0 | 4 | 0 |  | 61.5741 | 5320
17 | 528 | 5 | 533 | 0 | 0 | 3 | 533 | 55 | 11.9 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 83.7 | 6080 | 41.31 | 2995.2 | 240 | 5570 | 5330 | 10 | 88.0024 | 5343.6 | 0 | 226.4 | 0 |  | 61.6898 | 5330
18 | 7 | 573 | 580 | 0 | 0 | 4 | 580 | 50 | 0.2 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.7 | 8480 | 41.668 | 3414.06 | 2400 | 8113 | 5713 | 9.85 | 87.2502 | 7905.3 | 0 | 207.7 | 0 |  | 66.1227 | 5713
19 | 569 | 49 | 618 | 0 | 0 | 4 | 618 | 55 | 12.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.95 | 9080 | 41.839 | 3614.13 | 600 | 6656.4 | 6056.4 | 9.8 | 87.1849 | 6508.1 | 0 | 148.3 | 0 |  | 70.0972 | 6056.4
20 | 39 | 651 | 690 | 0 | 0 | 3 | 690 | 55 | 1.1 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.65 | 8360 | 41.902 | 3687.84 | -720 | 6249 | 6969 | 10.1 | 85.1903 | 6250.55 | 0 | 28.45 | 30 |  | 80.6597 | 6969
21 | 601 | 230 | 831 | 0 | 0 | 4 | 831 | 109 | 11.8 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.5 | 8000 | 41.901 | 3686.67 | -360 | 7950 | 8310 | 10 | 86.3459 | 7912.5 | 0 | 37.5 | 0 |  | 96.1806 | 8310
22 | 250 | 675 | 925 | 0 | 0 | 4 | 925 | 109 | 5.7 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.9 | 8960 | 41.902 | 3687.84 | 960 | 10302.5 | 9342.5 | 10.1 | 84.6939 | 10209.15 | 0 | 93.35 | 0 |  | 108.1308 | 9342.5
23 | 670 | 210 | 880 | 0 | 0 | 3 | 880 | 90 | 14.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480 | 41.95 | 3744 | -480 | 8408 | 8888 | 10.1 | 85.0905 | 8321.65 | 0 | 146.35 | 60 |  | 102.8704 | 8888
24 | 185 | 580 | 765 | 0 | 0 | 4 | 765 | 90 | 3.9 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 24 | 84.8 | 8720 | 41.902 | 3687.84 | 240 | 7890 | 7650 | 10 | 85.7407 | 7844.94 | 0 | 45.06 | 0 |  | 88.5417 | 7650
25 | 540 | 0 | 540 | 0 | 0 | 3 | 540 | 45 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.7 | 8480 | 41.702 | 3453.84 | -240 | 5160 | 5400 | 10 | 85.9415 | 5043.65 | 0 | 116.35 | 0 |  | 62.5 | 5400
26 | 45 | 480 | 525 | 0 | 0 | 4 | 525 | 46 | 1.2 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.65 | 8360 | 41.949 | 3742.83 | -120 | 5182.5 | 5302.5 | 10.1 | 85.1903 | 4995 | 0 | 187.5 | 0 |  | 61.3715 | 5302.5
27 | 107 | 380 | 487 | 0 | 0 | 0 | 487 | 90 | 2.2 | 8.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 27 | 84.9 | 8960 | 41.809 | 3579.03 | 600 | 5470 | 4870 | 10 | 85.5408 | 5365.5 | 0 | 104.5 | 0 |  | 56.3657 | 4870
28 | 0 | 500 | 500 | 0 | 0 | 0 | 500 | 45 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.8 | 8720 | 41.331 | 3019.77 | -240 | 4760 | 5000 | 10 | 85.7407 | 4498.2 | 0 | 261.8 | 0 |  | 57.8704 | 5000
29 | 363 | 140 | 503 | 0 | 0 | 10 | 503 | 90 | 8.6 | 3.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 29 | 84.8 | 8720 | 41.901 | 3686.67 | 0 | 5080.3 | 5080.3 | 10.1 | 84.8917 | 4945.25 | 0 | 135.05 | 0 |  | 58.7998 | 5080.3
30 | 0 | 595 | 595 | 0 | 0 | 4 | 595 | 45 | 0 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 85 | 9200 | 42.05 | 3861 | 480 | 6489.5 | 6009.5 | 10.1 | 84.4969 | 6193.8 | 0 | 295.7 | 0 |  | 69.5544 | 6009.5
31 | 570 | 0 | 570 | 0 | 0 | 3 | 570 | 53 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.8 | 8720 | 41.799 | 3567.33 | -480 | 5277 | 5757 | 10.1 | 84.8917 | 5161.1 | 0 | 175.9 | 60 |  | 66.6319 | 5757
| 9080 | 9177 | 18257 | 0 | 0 | 110 | 18147 | 109 | 198.3 | 201.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 36 |  |  | 84.4016 | 7763.871 | 41.7414 | 3499.9606 | 1920 | 186193.0905 | 183796.9 | 10.0672 | 85.9685 | 183323.66 | 476.1905 | 3409.4305 | 540 |  | 68.6219 | 183796.9