## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.85 | 8840 | 41.702 | 3453.84 | 120 | 6634.5 | 6514.5 | 10.1 | 84.7927 | 6576.05 | 0 | 58.45 | 0 |  | 75.3993 | 6514.5
2 | 0 | 510 | 510 | 0 | 0 | 4 | 510 | 55 | 0 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.85 | 8840 | 41.752 | 3512.34 | 0 | 4998 | 4998 | 9.8 | 87.3884 | 4952.8 | 0 | 45.2 | 0 |  | 57.8472 | 4998
3 | 745 | 5 | 750 | 0 | 0 | 3 | 750 | 53 | 14.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.8 | 8720 | 41.87 | 3650.4 | -120 | 7455 | 7575 | 10.1 | 84.8917 | 7343.8 | 0 | 171.2 | 60 |  | 87.6736 | 7575
4 | 0 | 740 | 740 | 0 | 0 | 4 | 740 | 55 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 85.05 | 9320 | 41.978 | 3776.76 | 600 | 7815 | 7215 | 9.75 | 87.4285 | 7725.65 | 0 | 89.35 | 0 |  | 83.5069 | 7215
5 | 227 | 475 | 702 | 0 | 0 | 3 | 702 | 106 | 4.65 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 5 | 84 | 6800 | 41.999 | 3801.33 | -2520 | 4570.2 | 7090.2 | 10.1 | 86.5087 | 4572 | 0 | 58.2 | 60 |  | 82.0625 | 7090.2
6 | 0 | 600 | 600 | 0 | 0 | 4 | 600 | 55 | 0 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.4 | 7760 | 41.649 | 3391.83 | 960 | 7080 | 6120 | 10.2 | 84.8525 | 7142.65 | 0 | 27.35 | 90 |  | 70.8333 | 6120
7 | 595 | 0 | 595 | 0 | 0 | 3 | 595 | 54 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.25 | 7400 | 41.679 | 3426.93 | -360 | 5530.5 | 5890.5 | 9.9 | 87.7341 | 5550 | 0 | 40.5 | 60 |  | 68.1771 | 5890.5
8 | 0 | 535 | 535 | 0 | 0 | 4 | 535 | 54 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.1 | 7040 | 41.669 | 3415.23 | -360 | 5043.5 | 5403.5 | 10.1 | 86.3032 | 5090.7 | 0 | 12.8 | 60 |  | 62.5405 | 5403.5
9 | 424 | 117 | 541 | 0 | 0 | 4 | 541 | 89 | 9.3 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.15 | 7160 | 41.827 | 3600.09 | 120 | 5530 | 5410 | 10 | 87.0629 | 5433.08 | 0 | 96.92 | 0 |  | 62.6157 | 5410
10 | 90 | 610 | 700 | 0 | 0 | 2 | 700 | 108 | 1.85 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 84.4 | 7760 | 41.758 | 3519.36 | 600 | 7670 | 7070 | 10.1 | 85.6926 | 7504.4 | 0 | 165.6 | 0 |  | 81.8287 | 7070
11 | 626 | 0 | 626 | 0 | 0 | 3 | 626 | 54 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.2 | 7280 | 41.439 | 3146.13 | -480 | 5780 | 6260 | 10 | 86.9597 | 5571.3 | 0 | 208.7 | 0 |  | 72.4537 | 6260
12 | 0 | 573 | 573 | 0 | 0 | 4 | 573 | 54 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.2 | 7280 | 41.891 | 3674.97 | 0 | 5787.3 | 5787.3 | 10.1 | 86.0987 | 5690.6 | 0 | 96.7 | 0 |  | 66.9826 | 5787.3
13 | 558 | 70 | 628 | 0 | 0 | 3 | 628 | 110 | 11.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 13 | 84.7 | 8480 | 41.841 | 3616.47 | 1200 | 7480 | 6280 | 10 | 85.9415 | 7443.45 | 0 | 36.55 | 0 |  | 72.6852 | 6280
14 | 105 | 570 | 675 | 0 | 0 | 4 | 675 | 90 | 2.9 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.3 | 7520 | 41.631 | 3370.77 | -960 | 5857.5 | 6817.5 | 10.1 | 85.8952 | 5740.35 | 0 | 117.15 | 0 |  | 78.9062 | 6817.5
15 | 490 | 0 | 490 | 0 | 0 | 3 | 490 | 55 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.15 | 7160 | 41.27 | 2948.4 | -360 | 4589 | 4949 | 10.1 | 86.2009 | 4569.8 | 0 | 79.2 | 60 |  | 57.2801 | 4949
16 | 0 | 455 | 455 | 0 | 0 | 4 | 455 | 54 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000 | 41.901 | 3686.67 | 840 | 5435.5 | 4595.5 | 10.1 | 85.491 | 5267.15 | 0 | 168.35 | 0 |  | 53.1887 | 4595.5
17 | 225 | 355 | 580 | 0 | 0 | 3 | 580 | 108 | 4.5 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 17 | 84.15 | 7160 | 41.65 | 3393 | -840 | 5018 | 5858 | 10.1 | 86.2009 | 4792.2 | 0 | 225.8 | 0 |  | 67.8009 | 5858
18 | 0 | 425 | 425 | 0 | 0 | 3 | 425 | 55 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.3 | 7520 | 41.681 | 3429.27 | 360 | 4652.5 | 4292.5 | 10.1 | 85.8952 | 4612.5 | 0 | 40 | 0 |  | 49.6817 | 4292.5
19 | 472 | 0 | 472 | 0 | 0 | 4 | 472 | 54 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.05 | 6920 | 41.58 | 3311.1 | -600 | 4120 | 4720 | 10 | 87.2699 | 4054.35 | 0 | 65.65 | 0 |  | 54.6296 | 4720
20 | 0 | 468 | 468 | 0 | 0 | 3 | 468 | 55 | 0 | 7.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.7 | 6080 | 41.707 | 3459.69 | -840 | 3886.8 | 4726.8 | 10.1 | 87.1311 | 3927.4 | 0 | 19.4 | 60 |  | 54.7083 | 4726.8
21 | 434 | 0 | 434 | 0 | 0 | 4 | 434 | 55 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.6999 | 3451.383 | 1440 | 5736.6 | 4296.6 | 9.9 | 87.6304 | 5602.1 | 0 | 134.5 | 0 |  | 49.7292 | 4296.6
22 | 0 | 482 | 482 | 0 | 0 | 3 | 482 | 55 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.2 | 7280 | 41.829 | 3602.43 | -240 | 4628.2 | 4868.2 | 10.1 | 86.0987 | 4658.35 | 0 | 29.85 | 60 |  | 56.3449 | 4868.2
23 | 335 | 95 | 430 | 0 | 0 | 4 | 430 | 110 | 7.8 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.1 | 7040 | 41.86 | 3638.7 | -240 | 4103 | 4343 | 10.1 | 86.3032 | 4146.4 | 0 | 16.6 | 60 |  | 50.2662 | 4343
24 | 0 | 442 | 442 | 0 | 0 | 3 | 442 | 55 | 0 | 9.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.25 | 7400 | 41.989 | 3789.63 | 360 | 4868.4 | 4508.4 | 10.2 | 85.1537 | 4679.3 | 0 | 189.1 | 0 |  | 52.1806 | 4508.4
25 | 219 | 0 | 219 | 0 | 0 | 3 | 219 | 40 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.35 | 7640 | 40.98 | 2609.1 | 240 | 2397.15 | 2157.15 | 9.85 | 87.9713 | 2102.4 | 0 | 354.75 | 60 |  | 24.967 | 2157.15
26 | 0 | 298 | 298 | 0 | 0 | 4 | 298 | 40 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.5 | 8000 | 41.36 | 3053.7 | 360 | 3310.2 | 2950.2 | 9.9 | 87.2181 | 3196.05 | 0 | 114.15 | 0 |  | 34.1458 | 2950.2
27 | 335 | 0 | 335 | 0 | 0 | 3 | 335 | 54 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84 | 6800 | 41.85 | 3627 | -1200 | 2183.5 | 3383.5 | 10.1 | 86.5087 | 2196.75 | 0 | 46.75 | 60 |  | 39.1609 | 3383.5
28 | 0 | 250 | 250 | 0 | 0 | 4 | 250 | 40 | 0 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.1 | 7040 | 41.85 | 3627 | 240 | 2765 | 2525 | 10.1 | 86.3032 | 2664.5 | 0 | 100.5 | 0 |  | 29.2245 | 2525
29 | 290 | 0 | 290 | 0 | 0 | 3 | 290 | 40 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84 | 6800 | 41.655 | 3398.85 | -240 | 2689 | 2929 | 10.1 | 86.5087 | 2752.5 | 0 | 16.5 | 80 |  | 33.9005 | 2929
30 | 0 | 210 | 210 | 0 | 0 | 3 | 210 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.55 | 8120 | 41.149 | 2806.83 | 1320 | 3378 | 2058 | 9.8 | 88.0045 | 2997.35 | 0 | 380.65 | 0 |  | 23.8194 | 2058
| 6815 | 8285 | 15100 | 0 | 0 | 102 | 14998 | 110 | 146 | 172.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 35 |  |  | 84.315 | 7556 | 41.6899 | 3439.6401 | -600 | 150992.35 | 151592.35 | 10.0392 | 86.3845 | 148555.93 | 0 | 3206.42 | 770 |  | 58.4847 | 151592.35