## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 35 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.3 | 7520 | 40.9 | 2515.5 | -480 | 580.5 | 1060.5 | 10.1 | 85.8952 | 503.7 | 0 | 76.8 | 0 |  | 12.2743 | 1060.5
2 | 0 | 115 | 115 | 0 | 0 | 3 | 115 | 40 | 0 | 3.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.85 | 8840 | 41.037 | 2675.79 | 1320 | 2447 | 1127 | 9.8 | 87.3884 | 2317.85 | 0 | 129.15 | 0 |  | 13.044 | 1127
3 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 35 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85 | 9200 | 41.252 | 2927.34 | 360 | 1521.5 | 1161.5 | 10.1 | 84.4969 | 1390.8 | 0 | 130.7 | 0 |  | 13.4433 | 1161.5
4 | 0 | 205 | 205 | 0 | 0 | 3 | 205 | 55 | 0 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.65 | 8360 | 40.962 | 2588.04 | -840 | 3018.0648 | 2070.5 | 10.1 | 85.1903 | 2962.5 | 1787.5648 | 55.5648 | 0 |  | 23.9641 | 2070.5
5 | 235 | 0 | 235 | 0 | 0 | 3 | 235 | 55 | 5.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.55 | 8120 | 40.67 | 2246.4 | -240 | 2204 | 2444 | 10.4 | 82.9273 | 2197.05 | 0 | 66.95 | 60 |  | 28.287 | 2444
6 | 0 | 77 | 77 | 0 | 0 | 3 | 77 | 55 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.6 | 8240 | 40.48 | 2024.1 | 120 | 874.6 | 754.6 | 9.8 | 87.9012 | 724.8 | 0 | 149.8 | 0 |  | 8.7338 | 754.6
7 | 210 | 0 | 210 | 0 | 0 | 4 | 210 | 55 | 4.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.7 | 8480 | 40.401 | 1931.67 | 240 | 2319 | 2079 | 9.9 | 86.8095 | 2166.85 | 0 | 152.15 | 0 |  | 24.0625 | 2079
8 | 130 | 155 | 285 | 0 | 0 | 3 | 285 | 55 | 2.3 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 84.5 | 8000 | 41.299 | 2982.33 | -480 | 2398.5 | 2878.5 | 10.1 | 85.491 | 2339.3 | 0 | 59.2 | 0 |  | 33.316 | 2878.5
9 | 0 | 73 | 73 | 0 | 0 | 4 | 73 | 40 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 9 | 84.7 | 8480 | 40.05 | 1521 | 480 | 1195.4 | 715.4 | 9.8 | 87.6954 | 875.8 | 0 | 319.6 | 0 |  | 8.2801 | 715.4
10 | 0 | 227 | 227 | 0 | 0 | 3 | 227 | 54 | 0 | 5.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.65 | 8360 | 40.498 | 2045.16 | -120 | 2172.7 | 2292.7 | 10.1 | 85.1903 | 1983.2 | 0 | 189.5 | 0 |  | 26.5359 | 2292.7
11 | 193 | 0 | 193 | 0 | 0 | 4 | 193 | 50 | 4.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.5 | 8000 | 40.582 | 2143.44 | -360 | 1589.3 | 1949.3 | 10.1 | 85.491 | 1522.5 | 0 | 66.8 | 0 |  | 22.5613 | 1949.3
12 | 0 | 93 | 93 | 0 | 0 | 3 | 93 | 35 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.6 | 8240 | 40.371 | 1896.57 | 240 | 1151.4 | 911.4 | 9.8 | 87.9012 | 1011.7 | 0 | 139.7 | 0 |  | 10.5486 | 911.4
13 | 117 | 0 | 117 | 0 | 0 | 4 | 117 | 55 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.45 | 7880 | 40.827 | 2430.09 | -360 | 821.7 | 1181.7 | 10.1 | 85.5917 | 871.2 | 0 | 10.5 | 60 |  | 13.6771 | 1181.7
14 | 275 | 257 | 532 | 0 | 0 | 4 | 532 | 90 | 6.9 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 14 | 84.55 | 8120 | 40.62 | 2187.9 | 240 | 5560 | 5320 | 10 | 86.2444 | 5519.68 | 0 | 40.32 | 0 |  | 61.5741 | 5320
15 | 80 | 0 | 80 | 0 | 0 | 3 | 80 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.6 | 8240 | 40.743 | 2331.81 | 120 | 912 | 792 | 9.9 | 87.0133 | 787.5 | 0 | 124.5 | 0 |  | 9.1667 | 792
16 | 125 | 0 | 125 | 0 | 0 | 3 | 125 | 40 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 16 | 84.5 | 8000 | 40.903 | 2519.01 | -240 | 1022.5 | 1262.5 | 10.1 | 85.491 | 847.5 | 0 | 175 | 0 |  | 14.6123 | 1262.5
17 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 54 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.6 | 8240 | 41.102 | 2751.84 | 240 | 2259.25 | 2019.25 | 9.85 | 87.455 | 2138.9 | 0 | 120.35 | 0 |  | 23.3709 | 2019.25
18 | 160 | 413 | 573 | 0 | 0 | 5 | 573 | 71 | 4.3 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 85.1 | 9440 | 40.832 | 2435.94 | 1200 | 6987.3 | 5787.3 | 10.1 | 84.3008 | 6965.75 | 0 | 21.55 | 0 |  | 66.9826 | 5787.3
19 | 510 | 175 | 685 | 0 | 0 | 4 | 685 | 108 | 11.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 19 | 84.7 | 8480 | 40.901 | 2516.67 | -960 | 5958.5 | 6918.5 | 10.1 | 85.0905 | 5630.1 | 0 | 328.4 | 0 |  | 80.0752 | 6918.5
20 | 0 | 285 | 285 | 0 | 0 | 4 | 285 | 40 | 0 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.9 | 8960 | 40.891 | 2504.97 | 480 | 3358.5 | 2878.5 | 10.1 | 84.6939 | 3285 | 0 | 133.5 | 60 |  | 33.316 | 2878.5
21 | 230 | 0 | 230 | 0 | 0 | 3 | 230 | 54 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.8 | 8720 | 40.682 | 2260.44 | -240 | 2083 | 2323 | 10.1 | 84.8917 | 1949.1 | 0 | 133.9 | 0 |  | 26.8866 | 2323
22 | 0 | 455 | 455 | 0 | 0 | 4 | 455 | 55 | 0 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 85.1 | 9440 | 40.692 | 2272.14 | 720 | 5224.5 | 4504.5 | 9.9 | 86.0039 | 5043.4 | 0 | 181.1 | 0 |  | 52.1354 | 4504.5
23 | 200 | 135 | 335 | 0 | 0 | 8 | 335 | 55 | 4.8 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.5 | 8000 | 40.47 | 2012.4 | -1440 | 1943.5 | 3383.5 | 10.1 | 85.491 | 1890.7 | 0 | 52.8 | 0 |  | 39.1609 | 3383.5
24 | 0 | 570 | 570 | 0 | 0 | 4 | 570 | 55 | 0 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.65 | 8360 | 40.551 | 2107.17 | 360 | 6060 | 5700 | 10 | 86.0422 | 6029.8 | 0 | 30.2 | 0 |  | 65.9722 | 5700
25 | 203 | 0 | 203 | 0 | 0 | 4 | 203 | 55 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.8 | 8720 | 40.63 | 2199.6 | 360 | 2349.4 | 1989.4 | 9.8 | 87.4905 | 2159.3 | 0 | 190.1 | 0 |  | 23.0255 | 1989.4
26 | 47 | 500 | 547 | 0 | 0 | 4 | 547 | 70 | 1.35 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 26 | 84.5 | 8000 | 40.45 | 1989 | -720 | 4804.7 | 5524.7 | 10.1 | 85.491 | 4745 | 0 | 59.7 | 0 |  | 63.9433 | 5524.7
27 | 482 | 154 | 636 | 0 | 0 | 3 | 636 | 108 | 11.15 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 27 | 84.15 | 7160 | 40.651 | 2224.17 | -840 | 5456.4 | 6296.4 | 9.9 | 87.9423 | 5475 | 0 | 41.4 | 60 |  | 72.875 | 6296.4
28 | 0 | 420 | 420 | 0 | 0 | 4 | 420 | 54 | 0 | 9.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.2 | 7280 | 40.501 | 2048.67 | 120 | 4362 | 4242 | 10.1 | 86.0987 | 4254.25 | 0 | 107.75 | 0 |  | 49.0972 | 4242
29 | 400 | 88 | 488 | 0 | 0 | 4 | 488 | 70 | 9.4 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 29 | 84.5 | 8000 | 40.561 | 2118.87 | 720 | 5648.8 | 4928.8 | 10.1 | 85.491 | 5628.3 | 0 | 80.5 | 60 |  | 57.0463 | 4928.8
30 | 285 | 405 | 690 | 0 | 0 | 5 | 690 | 110 | 6.3 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.45 | 7880 | 40.468 | 2010.06 | -120 | 6849 | 6969 | 10.1 | 85.5917 | 6907.5 | 0 | 1.5 | 60 |  | 80.6597 | 6969
| 4307 | 4802 | 9109 | 0 | 0 | 114 | 8995 | 110 | 100.4 | 111.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 29 |  |  | 84.6217 | 8292 | 40.6992 | 2280.603 | -120 | 93133.0148 | 91465.45 | 10.0412 | 85.746 | 90124.03 | 1787.5648 | 3368.9848 | 360 |  | 35.2876