## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 335 | 175 | 510 | 0 | 0 | 5 | 510 | 110 | 7.4 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.85 | 8840 | 40.493 | 2039.31 | 960 | 6111 | 5151 | 10.1 | 84.7927 | 6037.5 | 0 | 73.5 | 0 |  | 59.6181 | 5151
2 | 134 | 0 | 134 | 0 | 0 | 5 | 134 | 55 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 2 | 84.7 | 8480 | 40.14 | 1626.3 | -360 | 953.2 | 1313.2 | 9.8 | 87.6954 | 717.25 | 0 | 235.95 | 0 |  | 15.1991 | 1313.2
3 | 289 | 0 | 289 | 0 | 0 | 4 | 289 | 55 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.4 | 7760 | 40.501 | 2048.67 | -720 | 2198.9 | 2918.9 | 10.1 | 85.6926 | 2146.2 | 0 | 52.7 | 0 |  | 33.7836 | 2918.9
4 | 515 | 352 | 867 | 0 | 0 | 4 | 867 | 108 | 10.6 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 4 | 84.35 | 7640 | 40.75 | 2340 | -120 | 8636.7 | 8756.7 | 10.1 | 85.7938 | 8665.65 | 0 | 31.05 | 60 |  | 101.3507 | 8756.7
5 | 175 | 0 | 175 | 0 | 0 | 5 | 175 | 40 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.5 | 8000 | 40.48 | 2024.1 | 360 | 2127.5 | 1767.5 | 10.1 | 85.491 | 1907.6 | 0 | 219.9 | 0 |  | 20.4572 | 1767.5
6 | 157 | 135 | 292 | 0 | 0 | 4 | 292 | 70 | 4.15 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 6 | 84.2 | 7280 | 41.249 | 2923.83 | -720 | 2229.2 | 2949.2 | 10.1 | 86.0987 | 2226.5 | 0 | 62.7 | 60 |  | 34.1343 | 2949.2
7 | 186 | 0 | 186 | 0 | 0 | 5 | 186 | 40 | 4.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.4 | 7760 | 41.531 | 3253.77 | 480 | 2358.6 | 1878.6 | 10.1 | 85.6926 | 2295.2 | 0 | 93.4 | 30 |  | 21.7431 | 1878.6
8 | 0 | 236 | 236 | 0 | 0 | 4 | 236 | 40 | 0 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.45 | 7880 | 41.942 | 3734.64 | 120 | 2503.6 | 2383.6 | 10.1 | 85.5917 | 2477.6 | 0 | 26 | 0 |  | 27.588 | 2383.6
9 | 247 | 0 | 247 | 0 | 0 | 5 | 247 | 40 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 41.53 | 3252.6 | -360 | 2110 | 2470 | 10 | 86.7541 | 2064.6 | 0 | 45.4 | 0 |  | 28.588 | 2470
10 | 0 | 401 | 401 | 0 | 0 | 4 | 401 | 55 | 0 | 10.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.2 | 7280 | 41.32 | 3006.9 | -240 | 3729.9 | 3969.9 | 9.9 | 87.8381 | 3774 | 0 | 15.9 | 60 |  | 45.9479 | 3969.9
11 | 595 | 340 | 935 | 0 | 0 | 5 | 935 | 110 | 12.2 | 6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 11 | 84.55 | 8120 | 41.68 | 3428.1 | 840 | 10283.5 | 9443.5 | 10.1 | 85.3905 | 10300.3 | 0 | 43.2 | 60 |  | 109.2998 | 9443.5
12 | 95 | 334 | 429 | 0 | 0 | 5 | 429 | 110 | 1.9 | 7.5 | 0 | 0 | 1.1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | ΒΛΑΒΗ ΣΥΓΧΡΟΝΙΣΤΗ | 12 | 84.6 | 8240 | 40.6 | 2164.5 | 120 | 4452.9 | 4332.9 | 10.1 | 85.2903 | 4248.6 | 0 | 204.3 | 0 |  | 50.1493 | 4332.9
13 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 55 | 0 | 14.4 | 0 | 0 | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ΒΛΑΒΗ ΣΥΓΧΡΟΝΙΣΤΗ | 13 | 83.4 | 5360 | 41.201 | 2867.67 | -2880 | 4188.5 | 7068.5 | 10.55 | 84.019 | 4210.3 | 0 | 38.2 | 60 |  | 81.8113 | 7068.5
14 | 95 | 385 | 480 | 0 | 0 | 5 | 480 | 70 | 2.4 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 83.95 | 6680 | 41.352 | 3044.34 | 1320 | 6168 | 4848 | 10.1 | 86.6118 | 6149.4 | 0 | 18.6 | 0 |  | 56.1111 | 4848
15 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 40 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 83.8 | 6320 | 41.35 | 3042 | -360 | 1306.5 | 1666.5 | 10.1 | 86.9226 | 1260 | 0 | 46.5 | 0 |  | 19.2882 | 1666.5
16 | 0 | 127 | 127 | 0 | 0 | 5 | 127 | 40 | 0 | 3.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83.9 | 6560 | 41.2 | 2866.5 | 240 | 1522.7 | 1282.7 | 10.1 | 86.7152 | 1411.2 | 0 | 111.5 | 0 |  | 14.8461 | 1282.7
17 | 255 | 0 | 255 | 0 | 0 | 5 | 255 | 45 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.1 | 7040 | 41.252 | 2927.34 | 480 | 3055.5 | 2575.5 | 10.1 | 86.3032 | 3065.3 | 0 | 50.2 | 60 |  | 29.809 | 2575.5
18 | 0 | 138 | 138 | 0 | 0 | 5 | 138 | 35 | 0 | 3.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.4 | 7760 | 40.96 | 2585.7 | 720 | 2113.8 | 1393.8 | 10.1 | 85.6926 | 1740 | 0 | 373.8 | 0 |  | 16.1319 | 1393.8
19 | 250 | 0 | 250 | 0 | 0 | 4 | 250 | 40 | 7.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.1 | 7040 | 40.729 | 2315.43 | -720 | 1780 | 2500 | 10 | 87.1663 | 1795.45 | 0 | 44.55 | 60 |  | 28.9352 | 2500
20 | 140 | 292 | 432 | 0 | 0 | 5 | 432 | 108 | 3.1 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 20 | 84.4 | 7760 | 41.57 | 3299.4 | 720 | 5083.2 | 4363.2 | 10.1 | 85.6926 | 5157.8 | 0 | 25.4 | 100 |  | 50.5 | 4363.2
21 | 225 | 0 | 225 | 0 | 0 | 4 | 225 | 35 | 6.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.0249 | 2661.633 | -240 | 2010 | 2250 | 10 | 86.7541 | 1990.6 | 0 | 79.4 | 60 |  | 26.0417 | 2250
22 | 0 | 123 | 123 | 0 | 0 | 5 | 123 | 35 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.45 | 7880 | 40.357 | 1880.19 | 360 | 1577.7 | 1217.7 | 9.9 | 87.3208 | 1298.6 | 0 | 279.1 | 0 |  | 14.0938 | 1217.7
23 | 270 | 130 | 400 | 0 | 0 | 5 | 400 | 85 | 5.65 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.7 | 8480 | 41.4 | 3100.5 | 600 | 4560 | 3960 | 9.9 | 86.8095 | 4477 | 0 | 83 | 0 |  | 45.8333 | 3960
24 | 0 | 123 | 123 | 0 | 0 | 4 | 123 | 45 | 0 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.65 | 8360 | 40.9289 | 2549.313 | -120 | 2455.7447 | 1230 | 10 | 86.0422 | 2423.6 | 1345.7447 | 92.1447 | 60 |  | 14.2361 | 1230
25 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.2 | 7280 | 40.659 | 2233.53 | -1080 | 4547.1489 | 808 | 10.1 | 86.0987 | 4526 | 4819.1489 | 81.1489 | 60 |  | 9.3519 | 808
26 | 0 | 137 | 137 | 0 | 0 | 5 | 137 | 35 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.35 | 7640 | 40.366 | 1890.72 | 360 | 1702.6 | 1342.6 | 9.8 | 88.4201 | 1638.35 | 0 | 64.25 | 0 |  | 15.5394 | 1342.6
27 | 230 | 0 | 230 | 0 | 0 | 5 | 230 | 35 | 6.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.35 | 7640 | 41.02 | 2655.9 | 0 | 2323 | 2323 | 10.1 | 85.7938 | 2117 | 0 | 206 | 0 |  | 26.8866 | 2323
28 | 110 | 300 | 410 | 0 | 0 | 5 | 410 | 70 | 3.3 | 7.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 28 | 84.8 | 8720 | 41.801 | 3569.67 | 1080 | 5303 | 4223 | 10.3 | 83.2434 | 5343.25 | 0 | 19.75 | 60 |  | 48.8773 | 4223
29 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 35 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.4 | 7760 | 40.98 | 2609.1 | -960 | 1539 | 2499 | 9.8 | 88.3158 | 1449.6 | 0 | 89.4 | 0 |  | 28.9236 | 2499
30 | 136 | 171 | 307 | 0 | 0 | 5 | 307 | 55 | 3.3 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 30 | 84.05 | 6920 | 41.55 | 3276 | -840 | 2260.7 | 3100.7 | 10.1 | 86.4059 | 2073.2 | 0 | 187.5 | 0 |  | 35.8877 | 3100.7
31 | 191 | 0 | 191 | 0 | 0 | 5 | 191 | 35 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.6 | 8240 | 41 | 2632.5 | 1320 | 3249.1 | 1929.1 | 10.1 | 85.2903 | 3182.8 | 0 | 66.3 | 0 |  | 22.3275 | 1929.1
| 5130 | 4569 | 9699 | 0 | 0 | 143 | 9556 | 110 | 124.8 | 109.8 | 0 | 0 | 2.25 | 0 | 0 | 0 | 0 | 0 | 37 | 27 |  |  | 84.3355 | 7605.1613 | 41.0618 | 2704.8437 | 360 | 104441.1936 | 97916.3 | 10.0955 | 85.8614 | 102170.45 | 6164.8936 | 3060.7436 | 790 |  | 36.5578 | 97916.3