## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 83 | 0 | 83 | 0 | 0 | 4 | 83 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.1 | 7040 | 40.75 | 2340 | -1200 | 2919.55 | 838.3 | 10.1 | 86.3032 | 2920 | 3281.25 | 59.55 | 60 |  | 9.7025 | 838.3
2 | 0 | 400 | 400 | 0 | 0 | 5 | 400 | 54 | 0 | 8.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.8 | 8720 | 41.682 | 3430.44 | 1680 | 5720 | 4040 | 10.1 | 84.8917 | 5664.8 | 0 | 115.2 | 60 |  | 46.7593 | 4040
3 | 575 | 0 | 575 | 0 | 0 | 3 | 575 | 45 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.5 | 8000 | 41.24 | 2913.3 | -720 | 5087.5 | 5807.5 | 10.1 | 85.491 | 5043.4 | 0 | 104.1 | 60 |  | 67.2164 | 5807.5
4 | 573 | 651 | 1224 | 0 | 0 | 7 | 1224 | 110 | 11.1 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.6 | 8240 | 41.615 | 3352.05 | 240 | 13153.2 | 12913.2 | 10.55 | 81.6523 | 13129.75 | 0 | 83.45 | 60 |  | 149.4583 | 12913.2
5 | 251 | 178 | 429 | 0 | 0 | 4 | 429 | 70 | 6.2 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 5 | 84.4 | 7760 | 41.646 | 3388.32 | -480 | 8573.9526 | 4332.9 | 10.1 | 85.6926 | 8548.3 | 4721.0526 | 85.6526 | 60 |  | 50.1493 | 4332.9
6 | 0 | 195 | 195 | 0 | 0 | 5 | 195 | 45 | 0 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 85.05 | 9320 | 40.81 | 2410.2 | 1560 | 5891.2021 | 1969.5 | 10.1 | 84.3988 | 5964.1 | 2361.7021 | 27.1021 | 100 |  | 22.7951 | 1969.5
7 | 196 | 0 | 196 | 0 | 0 | 3 | 196 | 35 | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 85.2 | 9680 | 40.495 | 2041.65 | 360 | 6600.2383 | 1979.6 | 10.1 | 84.1057 | 6453.2 | 4260.6383 | 207.0383 | 60 |  | 22.912 | 1979.6
8 | 635 | 660 | 1295 | 0 | 0 | 4 | 1295 | 110 | 12 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 85.1 | 9440 | 41.851 | 3628.17 | -240 | 19416.7287 | 13273.75 | 10.25 | 83.0672 | 19432.71 | 6382.9787 | 44.0187 | 60 |  | 153.6314 | 13273.75
9 | 590 | 435 | 1025 | 0 | 0 | 5 | 1025 | 110 | 13.3 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 9 | 84.25 | 7400 | 41.201 | 2867.67 | -2040 | 14185.5159 | 10352.5 | 10.1 | 85.9968 | 14217 | 5873.0159 | 28.5159 | 60 |  | 119.8206 | 10352.5
10 | 100 | 375 | 475 | 0 | 0 | 5 | 475 | 108 | 2.3 | 8.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 10 | 85.3 | 9920 | 40.902 | 2517.84 | 2520 | 10782.7394 | 4821.25 | 10.15 | 83.4981 | 10774.8 | 3441.4894 | 67.9394 | 60 |  | 55.8015 | 4821.25
11 | 805 | 497 | 1302 | 0 | 0 | 5 | 1302 | 108 | 15.8 | 9.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 11 | 84.25 | 7400 | 41.218 | 2887.56 | -2520 | 12417.434 | 13150.2 | 10.1 | 85.9968 | 12427.2 | 1787.234 | 50.234 | 60 |  | 152.2014 | 13150.2
12 | 408 | 345 | 753 | 0 | 0 | 4 | 753 | 108 | 8 | 7.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 12 | 84 | 6800 | 41.38 | 3077.1 | -600 | 7005.3 | 7605.3 | 10.1 | 86.5087 | 7047.04 | 0 | 18.26 | 60 |  | 88.0243 | 7605.3
13 | 339 | 56 | 395 | 0 | 0 | 5 | 395 | 110 | 6.9 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1 | 1 |  | 13 | 85.15 | 9560 | 41.68 | 3428.1 | 2760 | 6591.5 | 3831.5 | 9.7 | 87.6755 | 6508.1 | 0 | 143.4 | 60 |  | 44.3461 | 3831.5
14 | 702 | 662 | 1364 | 0 | 0 | 5 | 1364 | 110 | 13.5 | 13.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 85 | 9200 | 41.762 | 3524.04 | -360 | 18939.8968 | 13912.8 | 10.2 | 83.6685 | 18958.75 | 5387.0968 | 41.1468 | 60 |  | 161.0278 | 13912.8
15 | 421 | 265 | 686 | 0 | 0 | 5 | 686 | 70 | 11.25 | 7.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 15 | 85.4 | 10160 | 41.6315 | 3371.355 | 960 | 12731.5319 | 6928.6 | 10.1 | 83.7181 | 12744.9 | 4842.9319 | 46.6319 | 60 |  | 80.1921 | 6928.6
16 | 500 | 600 | 1100 | 0 | 0 | 5 | 1100 | 110 | 10.85 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 16 | 85.1 | 9440 | 42.095 | 3913.65 | -720 | 17671.9149 | 11110 | 10.1 | 84.3008 | 17546.1 | 7281.9149 | 185.8149 | 60 |  | 128.588 | 11110
17 | 572 | 253 | 825 | 0 | 0 | 5 | 825 | 110 | 14.3 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 |  | 17 | 85.1 | 9440 | 41.302 | 2985.84 | 0 | 14929.2742 | 8332.5 | 10.1 | 84.3008 | 14960.1 | 6596.7742 | 69.1742 | 100 |  | 96.441 | 8332.5
18 | 309 | 422 | 731 | 0 | 0 | 5 | 731 | 108 | 7.2 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 18 | 84.5 | 8000 | 41.35 | 3042 | -1440 | 10734.9691 | 7419.65 | 10.15 | 85.0698 | 10760.2 | 4755.3191 | 34.7691 | 60 |  | 85.8756 | 7419.65
19 | 419 | 338 | 757 | 0 | 0 | 4 | 757 | 108 | 9.2 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 19 | 84.3 | 7520 | 41.05 | 2691 | -480 | 7165.7 | 7645.7 | 10.1 | 85.8952 | 7073.7 | 0 | 152 | 60 |  | 88.4919 | 7645.7
20 | 0 | 177 | 177 | 0 | 0 | 5 | 177 | 54 | 0 | 4.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 85.15 | 9560 | 40.8 | 2398.5 | 2040 | 3810 | 1770 | 10 | 85.0452 | 3672.85 | 0 | 137.15 | 0 |  | 20.4861 | 1770
21 | 387 | 390 | 777 | 0 | 0 | 6 | 777 | 108 | 8.6 | 8.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 21 | 84.1 | 7040 | 41.46 | 3170.7 | -2520 | 9475.8481 | 7847.7 | 10.1 | 86.3032 | 9520 | 4148.1481 | 15.8481 | 60 |  | 90.8299 | 7847.7
22 | 210 | 410 | 620 | 0 | 0 | 5 | 620 | 108 | 5.6 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 |  | 22 | 84 | 6800 | 41.31 | 2995.2 | -240 | 6022 | 6262 | 10.1 | 86.5087 | 5953.5 | 0 | 68.5 | 0 |  | 72.4769 | 6262
23 | 243 | 20 | 263 | 0 | 0 | 5 | 263 | 54 | 6.25 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 23 | 84.5 | 8000 | 40.3 | 1813.5 | 1200 | 5946.7255 | 2656.3 | 10.1 | 85.491 | 5883.8 | 2090.4255 | 62.9255 | 0 |  | 30.7442 | 2656.3
24 | 175 | 110 | 285 | 0 | 0 | 6 | 285 | 55 | 4.05 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.8 | 8720 | 41.2 | 2866.5 | 720 | 3541.5 | 2821.5 | 9.9 | 86.6067 | 3145.8 | 0 | 395.7 | 0 |  | 32.6562 | 2821.5
25 | 443 | 337 | 780 | 0 | 0 | 5 | 780 | 110 | 10.4 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 25 | 83.9 | 6560 | 40.95 | 2574 | -2160 | 5718 | 7878 | 10.1 | 86.7152 | 5715.5 | 0 | 62.5 | 60 |  | 91.1806 | 7878
26 | 74 | 233 | 307 | 0 | 0 | 5 | 307 | 70 | 1.8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 84.3 | 7520 | 41.2 | 2866.5 | 960 | 4030 | 3070 | 10 | 86.7541 | 3959 | 0 | 71 | 0 |  | 35.5324 | 3070
27 | 113 | 0 | 113 | 0 | 0 | 5 | 113 | 54 | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.4 | 7760 | 40.6 | 2164.5 | 240 | 1381.3 | 1141.3 | 10.1 | 85.6926 | 1266.5 | 0 | 114.8 | 0 |  | 13.2095 | 1141.3
28 | 0 | 215 | 215 | 0 | 0 | 6 | 215 | 54 | 0 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 83.9 | 6560 | 40.751 | 2341.17 | -1200 | 971.5 | 2171.5 | 10.1 | 86.7152 | 722.7 | 0 | 248.8 | 0 |  | 25.1331 | 2171.5
29 | 120 | 0 | 120 | 0 | 0 | 5 | 120 | 35 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.2 | 7280 | 40.18 | 1673.1 | 720 | 1932 | 1212 | 10.1 | 86.0987 | 1781.2 | 0 | 150.8 | 0 |  | 14.0278 | 1212
30 | 0 | 88 | 88 | 0 | 0 | 6 | 88 | 45 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.4 | 7760 | 40.347 | 1868.49 | 480 | 1360 | 880 | 10 | 86.5495 | 1268.4 | 0 | 91.6 | 0 |  | 10.1852 | 880
31 | 285 | 0 | 285 | 0 | 0 | 5 | 285 | 40 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 84.05 | 6920 | 40.63 | 2199.6 | -840 | 2038.5 | 2878.5 | 10.1 | 86.4059 | 1955.45 | 0 | 83.05 | 0 |  | 33.316 | 2878.5
| 9528 | 8312 | 17840 | 0 | 0 | 152 | 17688 | 110 | 212.3 | 185.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 38 | 40 |  |  | 84.5742 | 8178.0645 | 41.1416 | 2798.1305 | -1320 | 246745.5217 | 180853.55 | 10.1375 | 85.026 | 245018.85 | 67211.9717 | 3066.6717 | 1340 |  | 67.523 | 180853.55