## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 130 | 0 | 130 | 0 | 0 | 5 | 130 | 35 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.25 | 7400 | 40.85 | 2457 | 360 | 1634 | 1274 | 9.8 | 88.6294 | 1547.75 | 0 | 146.25 | 60 |  | 14.7454 | 1274
2 | 0 | 130 | 130 | 0 | 0 | 5 | 130 | 35 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.25 | 7400 | 41.4 | 3100.5 | 0 | 1313 | 1313 | 10.1 | 85.9968 | 1170 | 0 | 143 | 0 |  | 15.1968 | 1313
3 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 55 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.3 | 7520 | 41.04 | 2679.3 | 120 | 920 | 800 | 10 | 86.7541 | 765 | 0 | 155 | 0 |  | 9.2593 | 800
4 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 35 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.5 | 8000 | 40.92 | 2538.9 | 480 | 1264 | 784 | 9.8 | 88.108 | 1005 | 0 | 259 | 0 |  | 9.0741 | 784
5 | 120 | 0 | 120 | 0 | 0 | 5 | 120 | 40 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.4 | 7760 | 41.22 | 2889.9 | -240 | 972 | 1212 | 10.1 | 85.6926 | 854.1 | 0 | 117.9 | 0 |  | 14.0278 | 1212
6 | 0 | 65 | 65 | 0 | 0 | 6 | 65 | 40 | 0 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.4 | 7760 | 40.88 | 2492.1 | 0 | 656.5 | 656.5 | 10.1 | 85.6926 | 735 | 0 | 21.5 | 100 |  | 7.5984 | 656.5
7 | 90 | 0 | 90 | 0 | 0 | 5 | 90 | 35 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.5 | 8000 | 41.18 | 2843.1 | 240 | 1140 | 900 | 10 | 86.3459 | 906 | 0 | 234 | 0 |  | 10.4167 | 900
8 | 0 | 95 | 95 | 0 | 0 | 5 | 95 | 35 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.4 | 7760 | 41.52 | 3240.9 | -240 | 1714.1809 | 959.5 | 10.1 | 85.6926 | 1635.2 | 994.6809 | 138.9809 | 60 |  | 11.1053 | 959.5
9 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.55 | 8120 | 41.02 | 2655.9 | 360 | 1117.5 | 757.5 | 10.1 | 85.3905 | 855 | 0 | 262.5 | 0 |  | 8.7674 | 757.5
10 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.5 | 8000 | 40.8 | 2398.5 | -120 | 1769.5833 | 650 | 10 | 86.3459 | 1676.1 | 1239.5833 | 93.4833 | 0 |  | 7.5231 | 650
11 | 100 | 0 | 100 | 0 | 0 | 5 | 100 | 35 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.55 | 8120 | 41.15 | 2808 | 120 | 1105 | 985 | 9.85 | 87.5578 | 868.25 | 0 | 236.75 | 0 |  | 11.4005 | 985
12 | 0 | 120 | 120 | 0 | 0 | 5 | 120 | 35 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84 | 6800 | 41.58 | 3311.1 | -1320 | 1524.9787 | 1212 | 10.1 | 86.5087 | 1379.7 | 1632.9787 | 205.2787 | 60 |  | 14.0278 | 1212
13 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 54 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.05 | 6920 | 41.92 | 3708.9 | 120 | 1570 | 1450 | 10 | 87.2699 | 1430.4 | 0 | 139.6 | 0 |  | 16.7824 | 1450
14 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 35 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.1 | 7040 | 41.19 | 2854.8 | 120 | 928 | 808 | 10.1 | 86.3032 | 781.1 | 0 | 146.9 | 0 |  | 9.3519 | 808
15 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 54 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 15 | 84.2 | 7280 | 40.63 | 2199.6 | 240 | 1028 | 788 | 9.85 | 88.284 | 830.5 | 0 | 197.5 | 0 |  | 9.1204 | 788
16 | 60 | 0 | 60 | 0 | 0 | 5 | 60 | 35 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 84.15 | 7160 | 40.488 | 2033.46 | -120 | 1810.4681 | 606 | 10.1 | 86.2009 | 1715.5 | 1324.4681 | 154.9681 | 60 |  | 7.0139 | 606
17 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 40 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.4 | 7760 | 40.626 | 2194.92 | 600 | 1408 | 808 | 10.1 | 85.6926 | 1153.4 | 0 | 254.6 | 0 |  | 9.3519 | 808
18 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 35 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 84.6 | 8240 | 40.599 | 2163.33 | 480 | 1280 | 800 | 10 | 86.1432 | 1278 | 0 | 32 | 30 |  | 9.2593 | 800
19 | 145 | 0 | 145 | 0 | 0 | 5 | 145 | 35 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.5 | 8000 | 41.295 | 2977.65 | -240 | 1181 | 1421 | 9.8 | 88.108 | 876 | 0 | 305 | 0 |  | 16.4468 | 1421
20 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.7 | 8480 | 40.941 | 2563.47 | 480 | 1136.5 | 656.5 | 10.1 | 85.0905 | 962 | 0 | 174.5 | 0 |  | 7.5984 | 656.5
21 | 95 | 0 | 95 | 0 | 0 | 5 | 95 | 45 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.55 | 8120 | 40.8968 | 2511.756 | -360 | 3714.617 | 931 | 9.8 | 88.0045 | 3592.5 | 3143.617 | 122.117 | 0 |  | 10.7755 | 931
22 | 0 | 198 | 198 | 0 | 0 | 5 | 198 | 54 | 0 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.1 | 7040 | 41.499 | 3216.33 | -1080 | 919.8 | 1999.8 | 10.1 | 86.3032 | 941.7 | 0 | 8.1 | 30 |  | 23.1458 | 1999.8
23 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.2 | 7280 | 40.773 | 2366.91 | 240 | 3804.7872 | 735 | 9.8 | 88.7344 | 3682.5 | 2829.7872 | 122.2872 | 0 |  | 8.5069 | 735
24 | 0 | 58 | 58 | 0 | 0 | 5 | 58 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 83.85 | 6440 | 40.241 | 1744.47 | -840 | 2431.0085 | 574.2 | 9.9 | 88.5727 | 2299.5 | 2696.8085 | 131.5085 | 0 |  | 6.6458 | 574.2
25 | 135 | 0 | 135 | 0 | 0 | 4 | 135 | 35 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.35 | 5240 | 41.52 | 3240.9 | -1200 | 3136.9043 | 1363.5 | 10.1 | 87.8686 | 3168.2 | 2973.4043 | 28.7043 | 60 |  | 15.7812 | 1363.5
26 | 0 | 199 | 199 | 0 | 0 | 4 | 199 | 55 | 0 | 4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.45 | 7880 | 40.65 | 2223 | 2640 | 4590.2 | 1950.2 | 9.8 | 88.2118 | 4432.5 | 0 | 157.7 | 0 |  | 22.5718 | 1950.2
27 | 135 | 0 | 135 | 0 | 0 | 4 | 135 | 55 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.5 | 8000 | 41.23 | 2901.6 | 120 | 1483.5 | 1363.5 | 10.1 | 85.491 | 1408.9 | 0 | 134.6 | 60 |  | 15.7812 | 1363.5
28 | 425 | 560 | 985 | 0 | 0 | 4 | 985 | 70 | 11.6 | 14.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 28 | 83.3 | 5120 | 41.1 | 2749.5 | -2880 | 7167 | 10047 | 10.2 | 87.1125 | 7148.4 | 0 | 78.6 | 60 |  | 116.2847 | 10047
29 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 83.8 | 6320 | 40.3 | 1813.5 | 1200 | 4373.0769 | 650 | 10 | 87.7919 | 4049.85 | 2523.0769 | 323.2269 | 0 |  | 7.5231 | 650
30 | 0 | 95 | 95 | 0 | 0 | 4 | 95 | 45 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 83.9 | 6560 | 40.578 | 2138.76 | 240 | 1199.5 | 959.5 | 10.1 | 86.7152 | 1116.9 | 0 | 142.6 | 60 |  | 11.1053 | 959.5
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 45 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.1 | 7040 | 40.67 | 2246.4 | 480 | 3858.0128 | 757.5 | 10.1 | 86.3032 | 3744.9 | 2620.5128 | 173.1128 | 60 |  | 8.7674 | 757.5
| 2030 | 1970 | 4000 | 0 | 0 | 148 | 3852 | 70 | 51.85 | 51.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 |  |  | 84.2387 | 7372.9032 | 40.9905 | 2621.4341 | 0 | 62151.1178 | 40172.2 | 10.043 | 86.5076 | 58009.85 | 21978.9178 | 4841.2678 | 700 |  | 14.9986 | 40172.2