## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 45 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 1 | 84.55 | 8120 | 40.71 | 2293.2 | 1080 | 6316.2872 | 656.5 | 10.1 | 85.3905 | 6248.8 | 4579.7872 | 127.4872 | 60 |  | 7.5984 | 656.5
2 | 0 | 165 | 165 | 0 | 0 | 3 | 165 | 55 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.65 | 8360 | 41.49 | 3205.8 | 240 | 1865.25 | 1625.25 | 9.85 | 87.3525 | 1755 | 0 | 110.25 | 0 |  | 18.8108 | 1625.25
3 | 205 | 0 | 205 | 0 | 0 | 4 | 205 | 55 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.6 | 8240 | 41.902 | 3687.84 | -120 | 1899.25 | 2019.25 | 9.85 | 87.455 | 1664.4 | 0 | 234.85 | 0 |  | 23.3709 | 2019.25
4 | 0 | 160 | 160 | 0 | 0 | 4 | 160 | 54 | 0 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.7 | 8480 | 40.999 | 2631.33 | 240 | 1824 | 1584 | 9.9 | 86.8095 | 1762.5 | 0 | 61.5 | 0 |  | 18.3333 | 1584
5 | 235 | 0 | 235 | 0 | 0 | 4 | 235 | 55 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.15 | 7160 | 40.873 | 2483.91 | -1320 | 1494.9894 | 2373.5 | 10.1 | 86.2009 | 1416.2 | 441.4894 | 78.7894 | 0 |  | 27.4711 | 2373.5
6 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 40 | 0 | 3.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.1 | 7040 | 40.94 | 2562.3 | -120 | 1322 | 1442 | 10.3 | 84.6274 | 1292.1 | 0 | 89.9 | 60 |  | 16.6898 | 1442
7 | 145 | 0 | 145 | 0 | 0 | 4 | 145 | 35 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.1 | 7040 | 41.148 | 2805.66 | 0 | 1544.25 | 1544.25 | 10.65 | 81.8463 | 1537.25 | 0 | 67 | 60 |  | 17.8733 | 1544.25
8 | 101 | 59 | 160 | 0 | 0 | 4 | 160 | 54 | 1.9 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 8 | 83.9 | 6560 | 40.608 | 2173.86 | -480 | 1136 | 1616 | 10.1 | 86.7152 | 880.4 | 0 | 255.6 | 0 |  | 18.7037 | 1616
9 | 89 | 0 | 89 | 0 | 0 | 3 | 89 | 45 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.15 | 7160 | 40.487 | 2032.29 | 600 | 1498.9 | 898.9 | 10.1 | 86.2009 | 1401.6 | 0 | 157.3 | 60 |  | 10.4039 | 898.9
10 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 54 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.25 | 7400 | 40.38 | 1907.1 | 240 | 1153.5 | 913.5 | 10.15 | 85.5732 | 1029.3 | 0 | 124.2 | 0 |  | 10.5729 | 913.5
11 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.4 | 7760 | 40.4919 | 2038.023 | 360 | 1319.5 | 959.5 | 10.1 | 85.6926 | 1153.4 | 0 | 166.1 | 0 |  | 11.1053 | 959.5
12 | 0 | 81 | 81 | 0 | 0 | 4 | 81 | 35 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 84.3 | 7520 | 40.6058 | 2171.286 | -240 | 602.4 | 842.4 | 10.4 | 83.4174 | 666 | 0 | 16.4 | 80 |  | 9.75 | 842.4
13 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 54 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.4 | 7760 | 41.11 | 2761.2 | 240 | 1654 | 1414 | 10.1 | 85.6926 | 1562.2 | 0 | 91.8 | 0 |  | 16.3657 | 1414
14 | 0 | 105 | 105 | 0 | 0 | 4 | 105 | 54 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.7 | 8480 | 41.091 | 2738.97 | 720 | 1754.25 | 1034.25 | 9.85 | 87.2502 | 1402.5 | 0 | 351.75 | 0 |  | 11.9705 | 1034.25
15 | 170 | 0 | 170 | 0 | 0 | 4 | 170 | 35 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.35 | 7640 | 41.195 | 2860.65 | -840 | 911 | 1751 | 10.3 | 84.1279 | 952 | 0 | 19 | 60 |  | 20.2662 | 1751
16 | 80 | 165 | 245 | 0 | 0 | 4 | 245 | 70 | 2.1 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 16 | 84.5 | 8000 | 41.825 | 3597.75 | 360 | 2810 | 2450 | 10 | 86.3459 | 2682 | 0 | 128 | 0 |  | 28.3565 | 2450
17 | 110 | 5 | 115 | 0 | 0 | 3 | 115 | 35 | 2.6 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480 | 40.75 | 2340 | 480 | 1607 | 1127 | 9.8 | 87.6954 | 1490.4 | 0 | 116.6 | 0 |  | 13.044 | 1127
18 | 0 | 160 | 160 | 0 | 0 | 5 | 160 | 35 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.3 | 7520 | 41.288 | 2969.46 | -960 | 720 | 1680 | 10.5 | 82.623 | 686 | 0 | 94 | 60 |  | 19.4444 | 1680
19 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.45 | 7880 | 41 | 2632.5 | 360 | 1152 | 792 | 9.9 | 87.3208 | 981.5 | 0 | 170.5 | 0 |  | 9.1667 | 792
20 | 0 | 60 | 60 | 0 | 0 | 5 | 60 | 35 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.6 | 8240 | 40.34 | 1860.3 | 360 | 951 | 591 | 9.85 | 87.455 | 896.8 | 0 | 54.2 | 0 |  | 6.8403 | 591
21 | 105 | 0 | 105 | 0 | 0 | 5 | 105 | 35 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.6 | 8240 | 39.981 | 1440.27 | 0 | 1081.5 | 1081.5 | 10.3 | 83.6342 | 1015.2 | 0 | 66.3 | 0 |  | 12.5174 | 1081.5
22 | 0 | 115 | 115 | 0 | 0 | 5 | 115 | 55 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.7 | 8480 | 40.406 | 1937.52 | 240 | 1378.5 | 1138.5 | 9.9 | 86.8095 | 1212.75 | 0 | 165.75 | 0 |  | 13.1771 | 1138.5
23 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 55 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.5 | 8000 | 40.793 | 2390.31 | -480 | 727.5 | 1207.5 | 10.5 | 82.2342 | 658 | 0 | 69.5 | 0 |  | 13.9757 | 1207.5
24 | 0 | 60 | 60 | 0 | 0 | 5 | 60 | 35 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.3 | 7520 | 40.19 | 1684.8 | -480 | 1097.3617 | 588 | 9.8 | 88.5246 | 1117.5 | 989.3617 | 39.8617 | 60 |  | 6.8056 | 588
25 | 77 | 0 | 77 | 0 | 0 | 5 | 77 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.5 | 8000 | 40.9 | 2515.5 | 480 | 2874.7213 | 777.7 | 10.1 | 85.491 | 2708.3 | 1617.0213 | 166.4213 | 0 |  | 9.0012 | 777.7
26 | 0 | 35 | 35 | 0 | 0 | 5 | 35 | 45 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85.2 | 9680 | 40.581 | 2142.27 | 1680 | 3540.0561 | 344.75 | 9.85 | 86.2404 | 3480.55 | 1515.3061 | 59.5061 | 0 |  | 3.9902 | 344.75
27 | 96 | 0 | 96 | 0 | 0 | 4 | 96 | 45 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.85 | 8840 | 40.748 | 2337.66 | -840 | 2597.6851 | 969.6 | 10.1 | 84.7927 | 2430.9 | 2468.0851 | 166.7851 | 0 |  | 11.2222 | 969.6
28 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 83.75 | 6200 | 40.68 | 2258.1 | -2640 | 979.6579 | 656.5 | 10.1 | 87.0267 | 934.4 | 2963.1579 | 45.2579 | 0 |  | 7.5984 | 656.5
29 | 72 | 0 | 72 | 0 | 0 | 5 | 72 | 35 | 1.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 82.7 | 3740 | 40.65 | 2223 | -2460 | 1246.998 | 727.2 | 10.1 | 89.2719 | 1162.7 | 2979.798 | 84.298 | 0 |  | 8.4167 | 727.2
30 | 0 | 65 | 65 | 0 | 0 | 5 | 65 | 35 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.25 | 7400 | 40.605 | 2170.35 | 3660 | 5104.2701 | 640.25 | 9.85 | 88.1795 | 5028.75 | 804.0201 | 75.5201 | 0 |  | 7.4103 | 640.25
| 1915 | 1595 | 3510 | 0 | 0 | 129 | 3381 | 70 | 47.95 | 39.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 18 |  |  | 84.3733 | 7698 | 40.8256 | 2428.4403 | 360 | 54163.8268 | 35445.8 | 10.0985 | 85.7591 | 51209.4 | 18358.0268 | 3454.4268 | 500 |  | 13.6751 | 35445.8