## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 592 | 0 | 592 | 0 | 0 | 3 | 592 | 54 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 84.6 | 8240 | 41.041 | 2680.47 | 1560 | 7480 | 5920 | 10 | 86.1432 | 7365 | 0 | 115 | 0 |  | 68.5185 | 5920
2 | 35 | 580 | 615 | 0 | 0 | 3 | 615 | 70 | 1 | 12.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.6 | 8240 | 41.251 | 2926.17 | 0 | 6150 | 6150 | 10 | 86.1432 | 6075.4 | 0 | 74.6 | 0 |  | 71.1806 | 6150
3 | 613 | 0 | 613 | 0 | 0 | 3 | 613 | 45 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.75 | 8600 | 41.2 | 2866.5 | 360 | 6490 | 6130 | 10 | 85.8409 | 6274.05 | 0 | 215.95 | 0 |  | 70.9491 | 6130
4 | 5 | 585 | 590 | 0 | 0 | 3 | 590 | 50 | 0.2 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.85 | 8840 | 41.05 | 2691 | 240 | 6788.7436 | 5959 | 10.1 | 84.7927 | 6576.05 | 589.7436 | 212.6936 | 0 |  | 68.9699 | 5959
5 | 590 | 155 | 745 | 0 | 0 | 4 | 745 | 90 | 13.4 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 84.5 | 8000 | 42.08 | 3896.1 | -840 | 6759 | 7599 | 10.2 | 84.6528 | 6615 | 0 | 144 | 0 |  | 87.9514 | 7599
6 | 0 | 705 | 705 | 0 | 0 | 3 | 705 | 50 | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.5 | 8000 | 42.1 | 3919.5 | 0 | 7120.5 | 7120.5 | 10.1 | 85.491 | 6997.2 | 0 | 183.3 | 60 |  | 82.4132 | 7120.5
7 | 310 | 385 | 695 | 0 | 0 | 3 | 695 | 55 | 5.8 | 8.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 85 | 9200 | 42.1 | 3919.5 | 1200 | 8219.5 | 7019.5 | 10.1 | 84.4969 | 8205.2 | 0 | 74.3 | 60 |  | 81.2442 | 7019.5
8 | 180 | 640 | 820 | 0 | 0 | 3 | 820 | 90 | 4.65 | 14.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 8 | 84.6 | 8240 | 41.83 | 3603.6 | -960 | 7322 | 8282 | 10.1 | 85.2903 | 7318.15 | 0 | 63.85 | 60 |  | 95.8565 | 8282
9 | 700 | 0 | 700 | 0 | 0 | 4 | 700 | 55 | 13.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 85 | 9200 | 42.1 | 3919.5 | 960 | 8030 | 7070 | 10.1 | 84.4969 | 7744.4 | 0 | 285.6 | 0 |  | 81.8287 | 7070
10 | 0 | 730 | 730 | 0 | 0 | 2 | 730 | 55 | 0 | 14.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 83.5 | 5600 | 42.049 | 3859.83 | -3600 | 4028.5 | 7628.5 | 10.45 | 84.6187 | 4102.6 | 0 | 25.9 | 100 |  | 88.2928 | 7628.5
11 | 440 | 0 | 440 | 0 | 0 | 3 | 440 | 55 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.65 | 8360 | 41.5 | 3217.5 | 2760 | 7160 | 4400 | 10 | 86.0422 | 7080 | 0 | 140 | 60 |  | 50.9259 | 4400
12 | 225 | 370 | 595 | 0 | 0 | 3 | 595 | 54 | 4.5 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 12 | 84.7 | 8480 | 41.9 | 3685.5 | 120 | 6070 | 5950 | 10 | 85.9415 | 5874.8 | 0 | 195.2 | 0 |  | 68.8657 | 5950
13 | 455 | 0 | 455 | 0 | 0 | 4 | 455 | 45 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 13 | 84.9 | 8960 | 41.9 | 3685.5 | 480 | 5030 | 4550 | 10 | 85.5408 | 4757.6 | 0 | 272.4 | 0 |  | 52.662 | 4550
14 | 135 | 205 | 340 | 0 | 0 | 3 | 340 | 45 | 3.2 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 14 | 84 | 6800 | 41.9 | 3685.5 | -2160 | 4889.7895 | 3434 | 10.1 | 86.5087 | 4599 | 3615.7895 | 350.7895 | 60 |  | 39.7454 | 3434
15 | 490 | 0 | 490 | 0 | 0 | 4 | 490 | 45 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.2 | 7280 | 41.9 | 3685.5 | 480 | 5551.5 | 5071.5 | 10.35 | 84.019 | 5562.6 | 0 | 48.9 | 60 |  | 58.6979 | 5071.5
16 | 0 | 305 | 305 | 0 | 0 | 4 | 305 | 45 | 0 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.3 | 7520 | 41.42 | 3123.9 | 240 | 3396.75 | 3156.75 | 10.35 | 83.8204 | 3226.6 | 0 | 230.15 | 60 |  | 36.5365 | 3156.75
17 | 290 | 0 | 290 | 0 | 0 | 3 | 290 | 45 | 6.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.5 | 8000 | 41.531 | 3253.77 | 480 | 5597.7755 | 2929 | 10.1 | 85.491 | 5616.6 | 2188.7755 | 41.1755 | 60 |  | 33.9005 | 2929
18 | 0 | 315 | 315 | 0 | 0 | 3 | 315 | 45 | 0 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.5 | 8000 | 41.621 | 3359.07 | 0 | 3181.5 | 3181.5 | 10.1 | 85.491 | 3217.5 | 0 | 24 | 60 |  | 36.8229 | 3181.5
19 | 115 | 180 | 295 | 0 | 0 | 4 | 295 | 54 | 2.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 19 | 84.65 | 8360 | 41.42 | 3123.9 | 360 | 3339.5 | 2979.5 | 10.1 | 85.1903 | 3066 | 0 | 273.5 | 0 |  | 34.485 | 2979.5
20 | 0 | 325 | 325 | 0 | 0 | 3 | 325 | 45 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.35 | 7640 | 41.12 | 2772.9 | -720 | 2692.5 | 3412.5 | 10.5 | 82.5254 | 2671.8 | 0 | 80.7 | 60 |  | 39.4965 | 3412.5
21 | 335 | 90 | 425 | 0 | 0 | 4 | 425 | 99 | 7.6 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.7 | 8480 | 41.461 | 3171.87 | 840 | 4962.5 | 4122.5 | 9.7 | 88.5994 | 4827.15 | 0 | 135.35 | 0 |  | 47.7141 | 4122.5
22 | 0 | 485 | 485 | 0 | 0 | 4 | 485 | 54 | 0 | 9.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.8 | 8720 | 41.96 | 3755.7 | 240 | 5090 | 4850 | 10 | 85.7407 | 4693.9 | 0 | 396.1 | 0 |  | 56.1343 | 4850
23 | 495 | 0 | 495 | 0 | 0 | 3 | 495 | 50 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 85 | 9200 | 41.97 | 3767.4 | 480 | 5430 | 4950 | 10 | 85.3419 | 5201.95 | 0 | 228.05 | 0 |  | 57.2917 | 4950
24 | 0 | 563 | 563 | 0 | 0 | 4 | 563 | 50 | 0 | 11.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 85.15 | 9560 | 42.04 | 3849.3 | 360 | 5990 | 5630 | 10 | 85.0452 | 5646.8 | 0 | 343.2 | 0 |  | 65.162 | 5630
25 | 570 | 0 | 570 | 0 | 0 | 3 | 570 | 45 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.7 | 8480 | 41.75 | 3510 | -1080 | 4620 | 5700 | 10 | 85.9415 | 4455.1 | 0 | 164.9 | 0 |  | 65.9722 | 5700
26 | 0 | 622 | 622 | 0 | 0 | 3 | 622 | 50 | 0 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.5 | 8000 | 41.71 | 3463.2 | -480 | 5740 | 6220 | 10 | 86.3459 | 5609.65 | 0 | 130.35 | 0 |  | 71.9907 | 6220
27 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 52 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.8 | 8720 | 41.7 | 3451.5 | 720 | 7170 | 6450 | 10 | 85.7407 | 7044.8 | 0 | 125.2 | 0 |  | 74.6528 | 6450
28 | 0 | 685 | 685 | 0 | 0 | 4 | 685 | 50 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 84.4 | 7760 | 41.79 | 3556.8 | -960 | 5787.25 | 6747.25 | 9.85 | 87.8675 | 5692.4 | 0 | 94.85 | 0 |  | 78.0932 | 6747.25
29 | 700 | 0 | 700 | 0 | 0 | 3 | 700 | 50 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 84.8 | 8720 | 41.93 | 3720.6 | 960 | 8030 | 7070 | 10.1 | 84.8917 | 7666.05 | 0 | 363.95 | 0 |  | 81.8287 | 7070
30 | 245 | 630 | 875 | 0 | 0 | 3 | 875 | 85 | 5.6 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.75 | 8600 | 40.97 | 2597.4 | -120 | 8717.5 | 8837.5 | 10.1 | 84.991 | 8617.5 | 0 | 100 | 0 |  | 102.2859 | 8837.5
31 | 665 | 0 | 665 | 0 | 0 | 3 | 665 | 50 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 85.2 | 9680 | 41.821 | 3593.07 | 1080 | 7796.5 | 6716.5 | 10.1 | 84.1057 | 7466.6 | 0 | 389.9 | 60 |  | 77.7373 | 6716.5
| 8830 | 8555 | 17385 | 0 | 0 | 102 | 17283 | 99 | 188.2 | 181.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 32 |  |  | 84.6274 | 8305.8065 | 41.6811 | 3429.421 | 3000 | 184631.3086 | 175237 | 10.0798 | 85.4064 | 179867.45 | 6394.3086 | 5523.8586 | 760 |  | 65.426 | 175237