## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 900 | 325 | 1225 | 0 | 0 | 3 | 1225 | 107 | 17.3 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 1 | 83.8 | 6320 | 42.011 | 3815.37 | -3360 | 9012.5 | 12372.5 | 10.1 | 86.9226 | 9030.45 | 0 | 42.05 | 60 |  | 143.2002 | 12372.5
2 | 215 | 645 | 860 | 0 | 0 | 4 | 860 | 110 | 4.4 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 2 | 84.4 | 7760 | 41.8 | 3568.5 | 1440 | 10151.8 | 8711.8 | 10.13 | 85.4388 | 10179 | 0 | 32.8 | 60 |  | 100.831 | 8711.8
3 | 655 | 0 | 655 | 0 | 0 | 3 | 655 | 50 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 84.9 | 8960 | 41.69 | 3439.8 | 1200 | 7750 | 6550 | 10 | 85.5408 | 7497.15 | 0 | 252.85 | 0 |  | 75.8102 | 6550
4 | 310 | 370 | 680 | 0 | 0 | 3 | 680 | 50 | 6.4 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 4 | 84.5 | 8000 | 41.73 | 3486.6 | -960 | 5840 | 6800 | 10 | 86.3459 | 5722.9 | 0 | 117.1 | 0 |  | 78.7037 | 6800
5 | 415 | 250 | 665 | 0 | 0 | 3 | 665 | 105 | 8.4 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 5 | 85.25 | 9800 | 41.85 | 3627 | 1800 | 8516.5 | 6716.5 | 10.1 | 84.0085 | 8280 | 0 | 236.5 | 0 |  | 77.7373 | 6716.5
6 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 50 | 0 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 85 | 9200 | 42.1 | 3919.5 | -600 | 6167 | 6767 | 10.1 | 84.4969 | 5907.85 | 0 | 259.15 | 0 |  | 78.3218 | 6767
7 | 635 | 0 | 635 | 0 | 0 | 3 | 635 | 50 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.9 | 8960 | 41.85 | 3627 | -240 | 6173.5 | 6413.5 | 10.1 | 84.6939 | 6118 | 0 | 55.5 | 0 |  | 74.2303 | 6413.5
8 | 0 | 650 | 650 | 0 | 0 | 3 | 650 | 50 | 0 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 85.05 | 9320 | 41.9 | 3685.5 | 360 | 6860 | 6500 | 10 | 85.2427 | 6578.25 | 0 | 281.75 | 0 |  | 75.2315 | 6500
9 | 675 | 0 | 675 | 0 | 0 | 3 | 675 | 50 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.95 | 9080 | 41.95 | 3744 | -240 | 6577.5 | 6817.5 | 10.1 | 84.5953 | 6278 | 0 | 299.5 | 0 |  | 78.9062 | 6817.5
10 | 0 | 670 | 670 | 0 | 0 | 4 | 670 | 50 | 0 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.9 | 8960 | 42.07 | 3884.4 | -120 | 6647 | 6767 | 10.1 | 84.6939 | 6304.8 | 0 | 342.2 | 0 |  | 78.3218 | 6767
11 | 415 | 280 | 695 | 0 | 0 | 3 | 695 | 55 | 8.4 | 5.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 85.05 | 9320 | 42.05 | 3861 | 360 | 7379.5 | 7019.5 | 10.1 | 84.3988 | 7151.6 | 0 | 227.9 | 0 |  | 81.2442 | 7019.5
12 | 0 | 610 | 610 | 0 | 0 | 3 | 610 | 50 | 0 | 12.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 12 | 85.2 | 9680 | 41.7 | 3451.5 | 360 | 6460 | 6100 | 10 | 84.9468 | 6287.8 | 0 | 172.2 | 0 |  | 70.6019 | 6100
13 | 725 | 0 | 725 | 0 | 0 | 4 | 725 | 55 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.1 | 9440 | 41.7 | 3451.5 | -240 | 7082.5 | 7322.5 | 10.1 | 84.3008 | 7029 | 0 | 113.5 | 60 |  | 84.7512 | 7322.5
14 | 115 | 655 | 770 | 0 | 0 | 3 | 770 | 90 | 3.3 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 14 | 84.8 | 8720 | 42.1 | 3919.5 | -720 | 7057 | 7777 | 10.1 | 84.8917 | 6906.15 | 0 | 150.85 | 0 |  | 90.0116 | 7777
15 | 670 | 15 | 685 | 0 | 0 | 3 | 685 | 100 | 13.8 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.1 | 7040 | 42.1 | 3919.5 | -1680 | 6077.6923 | 6850 | 10 | 87.1663 | 5934.8 | 907.6923 | 142.8923 | 0 |  | 79.2824 | 6850
16 | 0 | 680 | 680 | 0 | 0 | 4 | 680 | 55 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000 | 41.85 | 3627 | 960 | 7828 | 6868 | 10.1 | 85.491 | 7695 | 0 | 193 | 60 |  | 79.4907 | 6868
17 | 600 | 0 | 600 | 0 | 0 | 3 | 600 | 55 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 85 | 9200 | 41.65 | 3393 | 1200 | 7260 | 6060 | 10.1 | 84.4969 | 7227 | 0 | 93 | 60 |  | 70.1389 | 6060
18 | 160 | 630 | 790 | 0 | 0 | 3 | 790 | 108 | 3.8 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.5 | 8000 | 41.9 | 3685.5 | -1200 | 6779 | 7979 | 10.1 | 85.491 | 6794.91 | 0 | 44.09 | 60 |  | 92.3495 | 7979
19 | 555 | 0 | 555 | 0 | 0 | 3 | 555 | 54 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 84.8 | 8720 | 41.2 | 2866.5 | 720 | 6159 | 5439 | 9.8 | 87.4905 | 6030 | 0 | 129 | 0 |  | 62.9514 | 5439
20 | 0 | 535 | 535 | 0 | 0 | 4 | 535 | 45 | 0 | 12.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.8 | 8720 | 40.8801 | 2492.217 | 0 | 5403.5 | 5403.5 | 10.1 | 84.8917 | 5350.2 | 0 | 113.3 | 60 |  | 62.5405 | 5403.5
21 | 605 | 60 | 665 | 0 | 0 | 3 | 665 | 108 | 13.1 | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 21 | 84.3 | 7520 | 41.7202 | 3475.0872 | -1200 | 5616.25 | 6816.25 | 10.25 | 84.6382 | 5638.8 | 0 | 37.45 | 60 |  | 78.8918 | 6816.25
22 | 0 | 545 | 545 | 0 | 0 | 3 | 545 | 40 | 0 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.4 | 7760 | 41.85 | 3627 | 240 | 5744.5 | 5504.5 | 10.1 | 85.6926 | 5752.4 | 0 | 52.1 | 60 |  | 63.7095 | 5504.5
23 | 235 | 290 | 525 | 0 | 0 | 3 | 525 | 54 | 5.05 | 6.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 23 | 84.25 | 7400 | 41.53 | 3252.6 | -360 | 4890 | 5250 | 10 | 86.8568 | 4770 | 0 | 120 | 0 |  | 60.7639 | 5250
24 | 0 | 555 | 555 | 0 | 0 | 3 | 555 | 54 | 0 | 12.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.55 | 8120 | 41.66 | 3404.7 | 720 | 6381 | 5661 | 10.2 | 84.5534 | 6332.5 | 0 | 108.5 | 60 |  | 65.5208 | 5661
25 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 54 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 85 | 9200 | 41.6005 | 3335.085 | 1080 | 6584.5 | 5504.5 | 10.1 | 84.4969 | 6482.8 | 0 | 101.7 | 0 |  | 63.7095 | 5504.5
26 | 0 | 635 | 635 | 0 | 0 | 3 | 635 | 55 | 0 | 12.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.65 | 8360 | 42.0802 | 3896.334 | -840 | 5637 | 6477 | 10.2 | 84.3551 | 5613.7 | 0 | 83.3 | 60 |  | 74.9653 | 6477
27 | 520 | 0 | 520 | 0 | 0 | 3 | 520 | 55 | 11.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 84.75 | 8600 | 41.76 | 3521.7 | 240 | 5336 | 5096 | 9.8 | 87.5928 | 5153.8 | 0 | 182.2 | 0 |  | 58.9815 | 5096
28 | 0 | 485 | 485 | 0 | 0 | 3 | 485 | 45 | 0 | 12.05 | 0 | 0 | 0 | 2.33 | 0 | 0 | 0 | 2.33 | 0 | 3 | ΒΛΑΒΗ Κ.Γ. ΜΕΤΑΦΟΡΑΣ Μ.Τ. ΔΕΔΔΗΕ | 28 | 85.075 | 9380 | 41.46 | 3170.7 | 780 | 5533 | 4753 | 9.8 | 86.9319 | 5416.8 | 0 | 116.2 | 0 |  | 55.0116 | 4753
29 | 505 | 0 | 505 | 0 | 0 | 3 | 505 | 40 | 12.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.2 | 9680 | 41.2401 | 2913.417 | 300 | 5299.5 | 4999.5 | 9.9 | 85.8048 | 4898.3 | 0 | 401.2 | 0 |  | 57.8646 | 4999.5
30 | 85 | 495 | 580 | 0 | 0 | 3 | 580 | 110 | 2.1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.9 | 8960 | 41.63 | 3369.6 | -720 | 5080 | 5800 | 10 | 85.5408 | 4943.2 | 0 | 136.8 | 0 |  | 67.1296 | 5800
31 | 490 | 0 | 490 | 0 | 0 | 3 | 490 | 45 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 31 | 85.05 | 9320 | 41.6 | 3334.5 | 360 | 5260 | 4900 | 10 | 85.2427 | 5115 | 0 | 145 | 0 |  | 56.713 | 4900
| 10030 | 10050 | 20080 | 0 | 0 | 100 | 19980 | 110 | 216.3 | 213.3 | 0 | 0 | 0 | 2.33 | 0 | 0 | 0 | 2.33 | 34 | 35 |  |  | 84.7621 | 8629.0323 | 41.7488 | 3508.5681 | -360 | 202543.7423 | 201996.05 | 10.0596 | 85.3085 | 198420.16 | 907.6923 | 4783.5823 | 660 |  | 75.4167 | 201996.05