## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 200 | 85 | 285 | 0 | 0 | 3 | 285 | 110 | 4.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 1 | 84.9 | 8960 | 41.84 | 3615.3 | 0 | 3312.1735 | 2878.5 | 10.1 | 84.6939 | 3176.8 | 433.6735 | 135.3735 | 0 |  | 33.316 | 2878.5
2 | 0 | 175 | 175 | 0 | 0 | 2 | 175 | 45 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.05 | 9320 | 41.52 | 3240.9 | 360 | 2127.5 | 1767.5 | 10.1 | 84.3988 | 2121.55 | 0 | 35.95 | 30 |  | 20.4572 | 1767.5
3 | 175 | 0 | 175 | 0 | 0 | 3 | 175 | 45 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 3 | 85.1 | 9440 | 41.19 | 2854.8 | 120 | 3011.8523 | 1767.5 | 10.1 | 84.3008 | 2810.5 | 1124.3523 | 201.3523 | 0 |  | 20.4572 | 1767.5
4 | 0 | 370 | 370 | 0 | 0 | 3 | 370 | 55 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.5 | 8000 | 41.48 | 3194.1 | -1440 | 2445 | 3885 | 10.5 | 82.2342 | 2256.45 | 0 | 248.55 | 60 |  | 44.9653 | 3885
5 | 160 | 0 | 160 | 0 | 0 | 3 | 160 | 45 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.6 | 8240 | 41 | 2632.5 | 240 | 1840 | 1600 | 10 | 86.1432 | 1638.35 | 0 | 201.65 | 0 |  | 18.5185 | 1600
6 | 0 | 200 | 200 | 0 | 0 | 3 | 200 | 55 | 0 | 4.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.75 | 8600 | 41.03 | 2667.6 | 360 | 2380 | 2020 | 10.1 | 84.991 | 2272.55 | 0 | 167.45 | 60 |  | 23.3796 | 2020
7 | 295 | 0 | 295 | 0 | 0 | 2 | 295 | 54 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 84.4 | 7760 | 41.77 | 3533.4 | -840 | 2139.5 | 2979.5 | 10.1 | 85.6926 | 1992.9 | 0 | 176.6 | 30 |  | 34.485 | 2979.5
8 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 40 | 0 | 4.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.5 | 8000 | 41.17 | 2831.4 | 240 | 1856 | 1616 | 10.1 | 85.491 | 1597.5 | 0 | 258.5 | 0 |  | 18.7037 | 1616
9 | 205 | 0 | 205 | 0 | 0 | 3 | 205 | 45 | 5.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 9 | 84.3 | 7520 | 41.38 | 3077.1 | -480 | 1549.5 | 2029.5 | 9.9 | 87.6304 | 1457.15 | 0 | 152.35 | 60 |  | 23.4896 | 2029.5
10 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 40 | 0 | 4.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 10 | 84.08 | 6992 | 41.77 | 3533.4 | -528 | 1795 | 2323 | 10.1 | 86.3443 | 1562.2 | 0 | 232.8 | 0 |  | 26.8866 | 2323
11 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 54 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.05 | 6920 | 41.59 | 3322.8 | -72 | 1457.75 | 1529.75 | 10.55 | 82.7203 | 1569.5 | 0 | 8.25 | 120 |  | 17.7054 | 1529.75
12 | 0 | 135 | 135 | 0 | 0 | 3 | 135 | 55 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.55 | 8120 | 41.29 | 2971.8 | 1200 | 2563.5 | 1363.5 | 10.1 | 85.3905 | 2452.8 | 0 | 170.7 | 60 |  | 15.7812 | 1363.5
13 | 140 | 0 | 140 | 0 | 0 | 3 | 140 | 40 | 3.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.8 | 8720 | 40.96 | 2585.7 | 600 | 1972 | 1372 | 9.8 | 87.4905 | 1824 | 0 | 148 | 0 |  | 15.8796 | 1372
14 | 0 | 120 | 120 | 0 | 0 | 3 | 120 | 55 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.9 | 8960 | 40.57 | 2129.4 | 240 | 1440 | 1200 | 10 | 85.5408 | 1298.6 | 0 | 141.4 | 0 |  | 13.8889 | 1200
15 | 220 | 0 | 220 | 0 | 0 | 3 | 220 | 55 | 4.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 84.95 | 9080 | 41 | 2632.5 | 120 | 2276 | 2156 | 9.8 | 87.1849 | 2112.8 | 0 | 163.2 | 0 |  | 24.9537 | 2156
16 | 0 | 165 | 165 | 0 | 0 | 2 | 165 | 55 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 85 | 9200 | 41.2 | 2866.5 | 120 | 1786.5 | 1666.5 | 10.1 | 84.4969 | 1565.6 | 0 | 220.9 | 0 |  | 19.2882 | 1666.5
17 | 145 | 0 | 145 | 0 | 0 | 3 | 145 | 45 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 85 | 9200 | 41.05 | 2691 | 0 | 1464.5 | 1464.5 | 10.1 | 84.4969 | 1406 | 0 | 58.5 | 0 |  | 16.9502 | 1464.5
18 | 90 | 165 | 255 | 0 | 0 | 3 | 255 | 108 | 1.7 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 18 | 84.7 | 8480 | 41.5 | 3217.5 | -720 | 1830 | 2550 | 10 | 85.9415 | 1577.95 | 0 | 252.05 | 0 |  | 29.5139 | 2550
19 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 45 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.75 | 8600 | 41.08 | 2726.1 | 120 | 1332 | 1212 | 10.1 | 84.991 | 1170.25 | 0 | 161.75 | 0 |  | 14.0278 | 1212
20 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 45 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.95 | 9080 | 40.57 | 2129.4 | 480 | 2044.6282 | 959.5 | 10.1 | 84.5953 | 1947.9 | 605.1282 | 156.7282 | 60 |  | 11.1053 | 959.5
21 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 45 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 85 | 9200 | 40.11 | 1591.2 | 120 | 1130 | 1010 | 10.1 | 84.4969 | 941.7 | 0 | 248.3 | 60 |  | 11.6898 | 1010
22 | 0 | 100 | 100 | 0 | 0 | 2 | 100 | 40 | 0 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85 | 9200 | 39.77 | 1193.4 | 0 | 3298.5106 | 990 | 9.9 | 86.2039 | 3060 | 2308.5106 | 238.5106 | 0 |  | 11.4583 | 990
23 | 90 | 0 | 90 | 0 | 0 | 2 | 90 | 35 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 85.05 | 9320 | 39.54 | 924.3 | 120 | 1697.1702 | 891 | 9.9 | 86.1038 | 1628 | 686.1702 | 69.1702 | 0 |  | 10.3125 | 891
24 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 55 | 0 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.15 | 9560 | 39.8 | 1228.5 | 240 | 1626 | 1386 | 9.9 | 85.9042 | 1568.8 | 0 | 57.2 | 0 |  | 16.0417 | 1386
25 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 35 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.22 | 9750 | 39.75 | 1170 | 190 | 1328.5 | 1138.5 | 9.9 | 85.7651 | 1154.4 | 0 | 174.1 | 0 |  | 13.1771 | 1138.5
26 | 70 | 135 | 205 | 0 | 0 | 3 | 205 | 390 | 2 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 26 | 85 | 9200 | 40.7 | 2281.5 | -550 | 2208.2234 | 2029.5 | 9.9 | 86.2039 | 2049.8 | 728.7234 | 158.4234 | 0 |  | 23.4896 | 2029.5
27 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 54 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.9 | 8960 | 41.5 | 3217.5 | -240 | 1591.5 | 1831.5 | 9.9 | 86.4048 | 1480 | 0 | 111.5 | 0 |  | 21.1979 | 1831.5
28 | 0 | 110 | 110 | 0 | 0 | 3 | 110 | 55 | 0 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 85.05 | 9320 | 41.65 | 3393 | 360 | 1449 | 1089 | 9.9 | 86.1038 | 1346.8 | 0 | 102.2 | 0 |  | 12.6042 | 1089
29 | 185 | 0 | 185 | 0 | 0 | 3 | 185 | 50 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 85 | 9200 | 41.78 | 3545.1 | -120 | 1711.5 | 1831.5 | 9.9 | 86.2039 | 1552.5 | 0 | 159 | 0 |  | 21.1979 | 1831.5
30 | 0 | 155 | 155 | 0 | 0 | 3 | 155 | 50 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.95 | 9080 | 41.87 | 3650.4 | -120 | 1414.5 | 1534.5 | 9.9 | 86.3043 | 1228.4 | 0 | 186.1 | 0 |  | 17.7604 | 1534.5
31 | 115 | 0 | 115 | 0 | 0 | 3 | 115 | 35 | 3.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 85.1 | 9440 | 41.84 | 3615.3 | 360 | 1498.5 | 1138.5 | 9.9 | 86.0039 | 1372.5 | 0 | 126 | 0 |  | 13.1771 | 1138.5
| 2755 | 2540 | 5295 | 0 | 0 | 89 | 5206 | 390 | 63.55 | 57.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 19 |  |  | 84.8145 | 8755.5484 | 41.0732 | 2718.1742 | 480 | 59576.8083 | 53210.25 | 10.0492 | 85.2924 | 55194.25 | 5886.5583 | 4922.5583 | 540 |  | 19.8664 | 53210.25