## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 105 | 0 | 105 | 0 | 0 | 3 | 105 | 35 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 85.15 | 9560 | 41.76 | 3521.7 | 120 | 1180.5 | 1060.5 | 10.1 | 84.2032 | 1041.9 | 0 | 138.6 | 0 |  | 12.2743 | 1060.5
2 | 0 | 145 | 145 | 0 | 0 | 2 | 145 | 54 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 85.18 | 9632 | 41.75 | 3510 | 72 | 1624.5213 | 1435.5 | 9.9 | 85.8446 | 1449.6 | 117.0213 | 174.9213 | 0 |  | 16.6146 | 1435.5
3 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 85.03 | 9272 | 41.58 | 3311.1 | -360 | 836.6915 | 643.5 | 9.9 | 86.1438 | 747.45 | 553.1915 | 89.2415 | 0 |  | 7.4479 | 643.5
4 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.56 | 8144 | 41.5 | 3217.5 | -1128 | 4568.3617 | 707 | 10.1 | 85.3704 | 4321.6 | 4989.3617 | 246.7617 | 0 |  | 8.1829 | 707
5 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.85 | 8840 | 41.3 | 2983.5 | 696 | 1346 | 650 | 10 | 85.6406 | 1073.1 | 0 | 272.9 | 0 |  | 7.5231 | 650
6 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.9 | 8960 | 41.06 | 2702.7 | 120 | 776.5 | 656.5 | 10.1 | 84.6939 | 795.2 | 0 | 41.3 | 60 |  | 7.5984 | 656.5
7 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 40 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.7 | 8480 | 41 | 2632.5 | -480 | 1319.383 | 693 | 9.9 | 86.8095 | 1110 | 1106.383 | 209.383 | 0 |  | 8.0208 | 693
8 | 0 | 95 | 95 | 0 | 0 | 3 | 95 | 40 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.9 | 8960 | 40.99 | 2620.8 | 480 | 1420.5 | 940.5 | 9.9 | 86.4048 | 1327.5 | 0 | 93 | 0 |  | 10.8854 | 940.5
9 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 35 | 1.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85.1 | 9440 | 40.8 | 2398.5 | 480 | 1173 | 693 | 9.9 | 86.0039 | 930 | 0 | 243 | 0 |  | 8.0208 | 693
10 | 0 | 160 | 160 | 0 | 0 | 3 | 160 | 55 | 0 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.58 | 8192 | 41.37 | 3065.4 | -1248 | 2133.9149 | 1600 | 10 | 86.1837 | 2070 | 1781.9149 | 123.9149 | 60 |  | 18.5185 | 1600
11 | 120 | 0 | 120 | 0 | 0 | 3 | 120 | 35 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 84.9 | 8960 | 41.52 | 3240.9 | 768 | 1980 | 1212 | 10.1 | 84.6939 | 1957.5 | 0 | 82.5 | 60 |  | 14.0278 | 1212
12 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.95 | 9080 | 41.25 | 2925 | 120 | 813 | 693 | 9.9 | 86.3043 | 780 | 0 | 93 | 60 |  | 8.0208 | 693
13 | 70 | 0 | 70 | 0 | 0 | 3 | 70 | 54 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.67 | 8408 | 41.05 | 2691 | -672 | 1241.5128 | 693 | 9.9 | 86.8706 | 900 | 1220.5128 | 341.5128 | 0 |  | 8.0208 | 693
14 | 0 | 80 | 80 | 0 | 0 | 3 | 80 | 35 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 84.75 | 8600 | 41 | 2632.5 | 192 | 992 | 800 | 10 | 85.8409 | 817.5 | 0 | 174.5 | 0 |  | 9.2593 | 800
15 | 70 | 0 | 70 | 0 | 0 | 2 | 70 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.85 | 8840 | 40.9 | 2515.5 | 240 | 947 | 707 | 10.1 | 84.7927 | 730 | 0 | 277 | 60 |  | 8.1829 | 707
16 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.95 | 9080 | 40.74 | 2328.3 | 240 | 896.5 | 656.5 | 10.1 | 84.5953 | 810.3 | 0 | 146.2 | 60 |  | 7.5984 | 656.5
17 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 83.8 | 6320 | 40.56 | 2117.7 | -2760 | 806.0745 | 656.5 | 10.1 | 86.9226 | 798 | 2909.5745 | 68.0745 | 60 |  | 7.5984 | 656.5
18 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 18 | 83.9 | 6560 | 40.39 | 1918.8 | 240 | 896.5 | 656.5 | 10.1 | 86.7152 | 661.5 | 0 | 235 | 0 |  | 7.5984 | 656.5
19 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84 | 6800 | 40.25 | 1755 | 240 | 896.5 | 656.5 | 10.1 | 86.5087 | 845.25 | 0 | 81.25 | 30 |  | 7.5984 | 656.5
20 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.2 | 7280 | 40.2 | 1696.5 | 480 | 1130 | 650 | 10 | 86.9597 | 765 | 0 | 365 | 0 |  | 7.5231 | 650
21 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.9 | 8960 | 40.22 | 1719.9 | 1680 | 5933.3586 | 656.5 | 10.1 | 84.6939 | 5735 | 3596.8586 | 258.3586 | 60 |  | 7.5984 | 656.5
22 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 85 | 9200 | 40.2 | 1696.5 | 240 | 896.5 | 656.5 | 10.1 | 84.4969 | 759.2 | 0 | 197.3 | 60 |  | 7.5984 | 656.5
23 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 23 | 85.15 | 9560 | 40.16 | 1649.7 | 360 | 1067 | 707 | 10.1 | 84.2032 | 853.15 | 0 | 243.85 | 30 |  | 8.1829 | 707
24 | 0 | 55 | 55 | 0 | 0 | 3 | 55 | 40 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.05 | 9320 | 40.07 | 1544.4 | -240 | 2294.2234 | 555.5 | 10.1 | 84.3988 | 2175.4 | 1978.7234 | 178.8234 | 60 |  | 6.4294 | 555.5
25 | 155 | 0 | 155 | 0 | 0 | 3 | 155 | 55 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 85.1 | 9440 | 41 | 2632.5 | 120 | 1654.5 | 1534.5 | 9.9 | 86.0039 | 854.1 | 0 | 800.4 | 0 |  | 17.7604 | 1534.5
26 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 26 | 85.05 | 9320 | 41.05 | 2691 | -120 | 1631.2368 | 656.5 | 10.1 | 84.3988 | 1284.8 | 1094.7368 | 406.4368 | 60 |  | 7.5984 | 656.5
27 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 85.1 | 9440 | 41.06 | 2702.7 | 120 | 776.5 | 656.5 | 10.1 | 84.3008 | 693.5 | 0 | 143 | 60 |  | 7.5984 | 656.5
28 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 28 | 84.5 | 8000 | 41.15 | 2808 | -1440 | 1819.2895 | 643.5 | 9.9 | 87.2181 | 1547.6 | 2615.7895 | 271.6895 | 0 |  | 7.4479 | 643.5
29 | 90 | 0 | 90 | 0 | 0 | 4 | 90 | 35 | 2.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.7 | 8480 | 41.55 | 3276 | 480 | 2315.3158 | 909 | 10.1 | 85.0905 | 2124.3 | 926.3158 | 191.0158 | 0 |  | 10.5208 | 909
30 | 0 | 215 | 215 | 0 | 0 | 3 | 215 | 40 | 0 | 5.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 30 | 84.45 | 7880 | 41.68 | 3428.1 | -600 | 2225.7553 | 2171.5 | 10.1 | 85.5917 | 2102.4 | 654.2553 | 183.3553 | 60 |  | 25.1331 | 2171.5
| 1270 | 1285 | 2555 | 0 | 0 | 88 | 2467 | 55 | 34.15 | 32.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 |  |  | 84.764 | 8633.6 | 40.9703 | 2597.79 | -1560 | 47592.1391 | 25607.5 | 10.0225 | 85.6201 | 42060.85 | 23544.6391 | 6371.2891 | 840 |  | 9.8794 | 25607.5