## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.4 | 7760 | 41.13 | 2784.6 | 480 | 2287.5417 | 656.5 | 10.1 | 85.6926 | 2100 | 1151.0417 | 247.5417 | 60 |  | 7.5984 | 656.5
2 | 35 | 70 | 105 | 0 | 0 | 4 | 105 | 54 | 0.95 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 2 | 83.7 | 6080 | 41.4 | 3100.5 | -1680 | 1785.7632 | 1060.5 | 10.1 | 87.1311 | 1844.85 | 2405.2632 | 20.9132 | 80 |  | 12.2743 | 1060.5
3 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.05 | 6920 | 41.4 | 3100.5 | 840 | 1477 | 637 | 9.8 | 89.0509 | 1283.5 | 0 | 193.5 | 0 |  | 7.3727 | 637
4 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 4 | 84.2 | 7280 | 41.38 | 3077.1 | 360 | 1016.5 | 656.5 | 10.1 | 86.0987 | 868.25 | 0 | 148.25 | 0 |  | 7.5984 | 656.5
5 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84 | 6800 | 41.34 | 3030.3 | -480 | 739 | 656.5 | 10.1 | 86.5087 | 671.6 | 562.5 | 127.4 | 60 |  | 7.5984 | 656.5
6 | 0 | 200 | 200 | 0 | 0 | 4 | 200 | 40 | 0 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 83.7 | 6080 | 41.65 | 3393 | -720 | 1300 | 2020 | 10.1 | 87.1311 | 1299.4 | 0 | 60.6 | 60 |  | 23.3796 | 2020
7 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 7 | 83.9 | 6560 | 41.5 | 3217.5 | 480 | 1136.5 | 656.5 | 10.1 | 86.7152 | 934.4 | 0 | 262.1 | 60 |  | 7.5984 | 656.5
8 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 40 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.8 | 8720 | 41.59 | 3322.8 | 2160 | 3544.5306 | 808 | 10.1 | 84.8917 | 3276.7 | 576.5306 | 267.8306 | 0 |  | 9.3519 | 808
9 | 80 | 0 | 80 | 0 | 0 | 5 | 80 | 35 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 85.05 | 9320 | 41.7 | 3451.5 | 600 | 1408 | 808 | 10.1 | 84.3988 | 1296 | 0 | 172 | 60 |  | 9.3519 | 808
10 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 85.1 | 9440 | 41.88 | 3662.1 | 120 | 1029 | 909 | 10.1 | 84.3008 | 883.3 | 0 | 205.7 | 60 |  | 10.5208 | 909
11 | 140 | 0 | 140 | 0 | 0 | 4 | 140 | 35 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 11 | 85 | 9200 | 41.8 | 3568.5 | -240 | 1118 | 1358 | 9.7 | 87.9813 | 921.1 | 0 | 196.9 | 0 |  | 15.7176 | 1358
12 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 85.1 | 9440 | 41.65 | 3393 | 240 | 940 | 700 | 10 | 85.1439 | 862.5 | 0 | 77.5 | 0 |  | 8.1019 | 700
13 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 40 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 13 | 85 | 9200 | 41.85 | 3627 | -240 | 1060 | 1300 | 10 | 85.3419 | 928.65 | 0 | 131.35 | 0 |  | 15.0463 | 1300
14 | 145 | 65 | 210 | 0 | 0 | 4 | 210 | 55 | 3.1 | 1.7 | 0 | 0 | 4.25 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | ΒΛΑΒΗ Δ/Κ Ρ15 | 14 | 84.55 | 8120 | 41.66 | 3404.7 | -1080 | 2180.8964 | 2121 | 10.1 | 85.3905 | 2065.9 | 1139.8964 | 114.9964 | 0 |  | 24.5486 | 2121
15 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.65 | 8360 | 41.61 | 3346.2 | 240 | 2168.2949 | 656.5 | 10.1 | 85.1903 | 2085 | 1271.7949 | 143.2949 | 60 |  | 7.5984 | 656.5
16 | 0 | 75 | 75 | 0 | 0 | 4 | 75 | 40 | 0 | 2.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 84.5 | 8000 | 41.65 | 3393 | -360 | 818.5714 | 750 | 10 | 86.3459 | 747.45 | 428.5714 | 71.1214 | 0 |  | 8.6806 | 750
17 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 40 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.3 | 7520 | 41.63 | 3369.6 | -480 | 1176.5 | 656.5 | 10.1 | 85.8952 | 1146.1 | 1000 | 90.4 | 60 |  | 7.5984 | 656.5
18 | 0 | 115 | 115 | 0 | 0 | 4 | 115 | 54 | 0 | 2.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.3 | 7520 | 41.57 | 3299.4 | 0 | 2920.8333 | 1150 | 10 | 86.7541 | 2725.55 | 1770.8333 | 195.2833 | 0 |  | 13.3102 | 1150
19 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.9 | 0 | 0 | 0 | 4.3 | 0 | 0 | 0 | 2.8 | 0 | 1 | 0 | ΑΠΟΚΑΤΑΣΤΑΣΗ ΒΛΑΒΗΣ Απ/Ζ 16 & 26 | 19 | 84.7 | 8480 | 41.56 | 3287.7 | 960 | 1736.2917 | 656.5 | 10.1 | 85.0905 | 1702.5 | 119.7917 | 33.7917 | 0 |  | 7.5984 | 656.5
20 | 0 | 170 | 170 | 0 | 0 | 4 | 170 | 35 | 0 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.9 | 8960 | 41.52 | 3240.9 | 480 | 2940.6383 | 1700 | 10 | 85.5408 | 2759.4 | 760.6383 | 181.2383 | 0 |  | 19.6759 | 1700
21 | 165 | 0 | 165 | 0 | 0 | 5 | 165 | 35 | 4.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 21 | 84.3 | 7520 | 41.7 | 3451.5 | -1440 | 1907.4359 | 1650 | 10 | 86.7541 | 1800 | 1697.4359 | 107.4359 | 0 |  | 19.0972 | 1650
22 | 0 | 80 | 80 | 0 | 0 | 4 | 80 | 35 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.25 | 7400 | 41.6 | 3334.5 | -120 | 1278.383 | 792 | 9.9 | 87.7341 | 1191.4 | 606.383 | 86.983 | 0 |  | 9.1667 | 792
23 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.4 | 7760 | 41.78 | 3545.1 | 360 | 1110 | 750 | 10 | 86.5495 | 996.6 | 0 | 113.4 | 0 |  | 8.6806 | 750
24 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 36 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 84.55 | 8120 | 41.68 | 3428.1 | 360 | 1210 | 850 | 10 | 86.2444 | 1125 | 0 | 85 | 0 |  | 9.838 | 850
25 | 75 | 0 | 75 | 0 | 0 | 5 | 75 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 84.72 | 8528 | 41.76 | 3521.7 | 408 | 1150.5 | 742.5 | 9.9 | 86.7689 | 969.4 | 0 | 181.1 | 0 |  | 8.5938 | 742.5
26 | 0 | 60 | 60 | 0 | 0 | 3 | 60 | 40 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 84.8 | 8720 | 41.7 | 3451.5 | 192 | 798 | 606 | 10.1 | 84.8917 | 781.1 | 0 | 76.9 | 60 |  | 7.0139 | 606
27 | 165 | 0 | 165 | 0 | 0 | 4 | 165 | 55 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.9 | 8960 | 41.14 | 2796.3 | 240 | 2943.734 | 1666.5 | 10.1 | 84.6939 | 2762.25 | 1037.234 | 241.484 | 60 |  | 19.2882 | 1666.5
28 | 0 | 110 | 110 | 0 | 0 | 4 | 110 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84 | 6800 | 41.45 | 3159 | -2160 | 1655.736 | 1100 | 10 | 87.3738 | 1422.95 | 2715.736 | 232.786 | 0 |  | 12.7315 | 1100
29 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.2 | 7280 | 41.65 | 3393 | 480 | 2719.9924 | 940.5 | 9.9 | 87.8381 | 2715.6 | 1299.4924 | 34.3924 | 30 |  | 10.8854 | 940.5
30 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 84.285 | 7484 | 41.65 | 3393 | 204 | 1833.9043 | 656.5 | 10.1 | 85.9257 | 1759.3 | 973.4043 | 134.6043 | 60 |  | 7.5984 | 656.5
31 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 84.245 | 7388 | 41.78 | 3545.1 | -96 | 854 | 950 | 10 | 86.8671 | 540.2 | 0 | 313.8 | 0 |  | 10.9954 | 950
| 1460 | 1595 | 3055 | 0 | 0 | 126 | 2929 | 55 | 37.8 | 39.3 | 0 | 0 | 8.55 | 0 | 0 | 0 | 2.8 | 0 | 17 | 21 |  |  | 84.4694 | 7926.4516 | 41.5923 | 3325.4419 | 108 | 50245.547 | 30621 | 10.0232 | 86.2078 | 46465.95 | 19516.547 | 4549.597 | 770 |  | 11.4326 | 30621