## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.58 | 8190 | 41.85 | 3627 | 802 | 1544.5 | 742.5 | 9.9 | 87.0542 | 1430.8 | 0 | 113.7 | 0 |  | 8.5938 | 742.5
2 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 84.73 | 8552 | 41.82 | 3591.9 | 362 | 1531.5417 | 643.5 | 9.9 | 86.7486 | 1401.6 | 526.0417 | 129.9417 | 0 |  | 7.4479 | 643.5
3 | 80 | 0 | 80 | 0 | 0 | 4 | 80 | 35 | 2.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84.9 | 8960 | 41.9 | 3685.5 | 408 | 1200 | 792 | 9.9 | 86.4048 | 1110 | 0 | 90 | 0 |  | 9.1667 | 792
4 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 4 | 84.9 | 8960 | 41.2 | 2866.5 | 0 | 757.5 | 757.5 | 10.1 | 84.6939 | 754.8 | 0 | 62.7 | 60 |  | 8.7674 | 757.5
5 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 35 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.6 | 8240 | 41.36 | 3053.7 | -720 | 3618.9583 | 990 | 9.9 | 87.0133 | 3358 | 3348.9583 | 260.9583 | 0 |  | 11.4583 | 990
6 | 0 | 105 | 105 | 0 | 0 | 4 | 105 | 35 | 0 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.6 | 8240 | 41.62 | 3357.9 | 0 | 1050 | 1050 | 10 | 86.1432 | 940.8 | 0 | 109.2 | 0 |  | 12.1528 | 1050
7 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 7 | 84.85 | 8840 | 41.6 | 3334.5 | 600 | 1250 | 650 | 10 | 85.6406 | 1036.35 | 0 | 213.65 | 0 |  | 7.5231 | 650
8 | 0 | 185 | 185 | 0 | 0 | 5 | 185 | 36 | 0 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.8 | 8720 | 41.68 | 3428.1 | -120 | 1748.5 | 1868.5 | 10.1 | 84.8917 | 1679 | 0 | 129.5 | 60 |  | 21.6262 | 1868.5
9 | 135 | 0 | 135 | 0 | 0 | 5 | 135 | 36 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 9 | 84.8 | 8720 | 41.7 | 3451.5 | 0 | 1363.5 | 1363.5 | 10.1 | 84.8917 | 1241 | 0 | 182.5 | 60 |  | 15.7812 | 1363.5
10 | 0 | 140 | 140 | 0 | 0 | 4 | 140 | 35 | 0 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 10 | 84.55 | 8120 | 41.15 | 2808 | -600 | 814 | 1414 | 10.1 | 85.3905 | 824.9 | 0 | 49.1 | 60 |  | 16.3657 | 1414
11 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 35 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.5 | 8000 | 41.81 | 3580.2 | -120 | 2398.9119 | 1550 | 10 | 86.3459 | 2131.5 | 968.9119 | 267.4119 | 0 |  | 17.9398 | 1550
12 | 0 | 90 | 90 | 0 | 0 | 3 | 90 | 55 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84 | 6800 | 41.15 | 2808 | -1200 | 1492.3118 | 945 | 10.5 | 83.2132 | 1512 | 1747.3118 | 40.3118 | 60 |  | 10.9375 | 945
13 | 100 | 0 | 100 | 0 | 0 | 4 | 100 | 35 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 84.2 | 7280 | 41.19 | 2854.8 | 480 | 1490.2564 | 1000 | 10 | 86.9597 | 1277.5 | 10.2564 | 212.7564 | 0 |  | 11.5741 | 1000
14 | 0 | 480 | 480 | 0 | 0 | 4 | 480 | 55 | 0 | 9.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 84.2 | 7280 | 41.81 | 3580.2 | 0 | 6015.5676 | 4848 | 10.1 | 86.0987 | 5810 | 1167.5676 | 265.5676 | 60 |  | 56.1111 | 4848
15 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 15 | 84.85 | 8840 | 41.15 | 2808 | 1560 | 4456.1538 | 650 | 10 | 85.6406 | 4170 | 2246.1538 | 286.1538 | 0 |  | 7.5231 | 650
16 | 75 | 0 | 75 | 0 | 0 | 4 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 16 | 85.3 | 9920 | 41 | 2632.5 | 1080 | 5009.375 | 757.5 | 10.1 | 83.9115 | 4964 | 3171.875 | 75.375 | 30 |  | 8.7674 | 757.5
17 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 54 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 17 | 84.7 | 8480 | 40.9 | 2515.5 | -1440 | 5192.9787 | 750 | 10 | 85.9415 | 5066.2 | 5882.9787 | 126.7787 | 0 |  | 8.6806 | 750
18 | 65 | 100 | 165 | 0 | 0 | 4 | 165 | 65 | 1.9 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 18 | 84.5 | 8000 | 41.28 | 2960.1 | -480 | 1186.5 | 1666.5 | 10.1 | 85.491 | 1071 | 0 | 175.5 | 60 |  | 19.2882 | 1666.5
19 | 95 | 0 | 95 | 0 | 0 | 4 | 95 | 35 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 84.8 | 8720 | 41.23 | 2901.6 | 720 | 1679.5 | 959.5 | 10.1 | 84.8917 | 1727.25 | 0 | 12.25 | 60 |  | 11.1053 | 959.5
20 | 0 | 135 | 135 | 0 | 0 | 3 | 135 | 55 | 0 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 84.85 | 8840 | 41.39 | 3088.8 | 120 | 1483.5 | 1363.5 | 10.1 | 84.7927 | 1334.8 | 0 | 208.7 | 60 |  | 15.7812 | 1363.5
21 | 115 | 0 | 115 | 0 | 0 | 4 | 115 | 35 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 84.5 | 8000 | 41.67 | 3416.4 | -840 | 1560.8617 | 1161.5 | 10.1 | 85.491 | 1562.2 | 1239.3617 | 58.6617 | 60 |  | 13.4433 | 1161.5
22 | 50 | 115 | 165 | 0 | 0 | 5 | 165 | 55 | 1.15 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 22 | 84.6 | 8240 | 41.1 | 2749.5 | 240 | 1906.5 | 1666.5 | 10.1 | 85.2903 | 1832.3 | 0 | 74.2 | 0 |  | 19.2882 | 1666.5
23 | 155 | 0 | 155 | 0 | 0 | 4 | 155 | 55 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 23 | 84.6 | 8240 | 41.7 | 3451.5 | 0 | 2011.8511 | 1581 | 10.2 | 84.4541 | 2051.3 | 430.8511 | 20.5511 | 60 |  | 18.2986 | 1581
24 | 80 | 105 | 185 | 0 | 0 | 3 | 185 | 35 | 2.15 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 24 | 84.55 | 8120 | 41.64 | 3381.3 | -120 | 2386.7979 | 1868.5 | 10.1 | 85.3905 | 2248.4 | 638.2979 | 198.3979 | 60 |  | 21.6262 | 1868.5
25 | 180 | 105 | 285 | 0 | 0 | 4 | 285 | 70 | 5.05 | 2.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 25 | 85 | 9200 | 41.95 | 3744 | 1080 | 7255.9359 | 2878.5 | 10.1 | 84.4969 | 7241.6 | 3297.4359 | 34.3359 | 20 |  | 33.316 | 2878.5
26 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 83 | 4400 | 41.17 | 2831.4 | -4800 | 2852.0135 | 738.5 | 10.55 | 84.8387 | 2905 | 6913.5135 | 27.0135 | 80 |  | 8.5475 | 738.5
27 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 55 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 83.97 | 6728 | 40.96 | 2585.7 | 2328 | 5422.2876 | 757.5 | 10.1 | 86.5706 | 5183 | 2336.7876 | 239.2876 | 0 |  | 8.7674 | 757.5
28 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 35 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.27 | 7448 | 41 | 2632.5 | 720 | 1665 | 945 | 10.5 | 82.6816 | 1711.2 | 0 | 53.8 | 100 |  | 10.9375 | 945
29 | 240 | 0 | 240 | 0 | 0 | 4 | 240 | 55 | 4.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 29 | 84.3 | 7520 | 41.73 | 3486.6 | 72 | 3027.9149 | 2424 | 10.1 | 85.8952 | 2916 | 531.9149 | 171.9149 | 60 |  | 28.0556 | 2424
| 2055 | 1785 | 3840 | 0 | 0 | 112 | 3728 | 70 | 50.8 | 43.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 18 |  |  | 84.5517 | 8124.069 | 41.4383 | 3145.2828 | 132 | 73372.7178 | 38782.5 | 10.0996 | 85.3904 | 70492.5 | 34458.2178 | 3890.2178 | 1010 |  | 15.4783 | 38782.5