## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 100 | 0 | 100 | 0 | 0 | 3 | 100 | 55 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 84.65 | 8360 | 41.8 | 3568.5 | 840 | 1850 | 1010 | 10.1 | 85.1903 | 1868.8 | 0 | 41.2 | 60 |  | 11.6898 | 1010
2 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 2 | 83.85 | 6440 | 41.83 | 3603.6 | -1920 | 2476.0135 | 682.5 | 10.5 | 83.5114 | 2408 | 3713.5135 | 168.0135 | 100 |  | 7.8993 | 682.5
3 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 3 | 84 | 6800 | 41.86 | 3638.7 | 360 | 5037.7766 | 656.5 | 10.1 | 86.5087 | 5168.4 | 4021.2766 | 19.3766 | 150 |  | 7.5984 | 656.5
4 | 0 | 230 | 230 | 0 | 0 | 3 | 230 | 55 | 0 | 4.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.25 | 7400 | 41.78 | 3545.1 | 600 | 2923 | 2323 | 10.1 | 85.9968 | 2863 | 0 | 120 | 60 |  | 26.8866 | 2323
5 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 54 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 5 | 84.9 | 8960 | 41.67 | 3416.4 | 1560 | 2260 | 700 | 10 | 85.5408 | 2057.2 | 0 | 202.8 | 0 |  | 8.1019 | 700
6 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 35 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 6 | 84.9 | 8960 | 41.67 | 3416.4 | 0 | 656.5 | 656.5 | 10.1 | 84.6939 | 617.4 | 0 | 99.1 | 60 |  | 7.5984 | 656.5
7 | 85 | 35 | 120 | 0 | 0 | 4 | 120 | 35 | 2.3 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 7 | 84.6 | 8240 | 41.69 | 3439.8 | -720 | 3029.234 | 1212 | 10.1 | 85.2903 | 3000.3 | 2537.234 | 88.934 | 60 |  | 14.0278 | 1212
8 | 0 | 75 | 75 | 0 | 0 | 3 | 75 | 35 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 8 | 84.1 | 7040 | 41.54 | 3264.3 | -1200 | 5924.5213 | 757.5 | 10.1 | 86.3032 | 5858 | 6367.0213 | 126.5213 | 60 |  | 8.7674 | 757.5
9 | 175 | 45 | 220 | 0 | 0 | 4 | 220 | 70 | 4.5 | 2.1 | 0 | 8.25 | 0 | 0 | 0 | 8.25 | 0 | 0 | 2 | 1 | ΣΥΝΤΗΡΗΣΗ Δ/Κ Ρ10 | 9 | 84.65 | 8360 | 41.6 | 3334.5 | 1320 | 4142 | 2222 | 10.1 | 85.1903 | 3850 | 600 | 292 | 0 |  | 25.7176 | 2222
10 | 0 | 65 | 65 | 0 | 0 | 3 | 65 | 35 | 0 | 1.9 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 2.2 | 0 | 1 | ΒΛΑΒΗ Δ/Κ Ρ60 Υ/Σ ΡΑΧΙΑΣ | 10 | 84.95 | 9080 | 41.32 | 3006.9 | 720 | 1413.734 | 656.5 | 10.1 | 84.5953 | 1379.7 | 37.234 | 34.034 | 0 |  | 7.5984 | 656.5
11 | 155 | 20 | 175 | 0 | 0 | 4 | 175 | 55 | 3.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 11 | 84.9 | 8960 | 42 | 3802.5 | -120 | 1647.5 | 1767.5 | 10.1 | 84.6939 | 1659 | 0 | 48.5 | 60 |  | 20.4572 | 1767.5
12 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 40 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 12 | 84.76 | 8624 | 41.05 | 2691 | -336 | 980.0745 | 656.5 | 10.1 | 84.9711 | 980 | 659.5745 | 60.0745 | 60 |  | 7.5984 | 656.5
13 | 65 | 0 | 65 | 0 | 0 | 3 | 65 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 13 | 85 | 9200 | 40.85 | 2457 | 576 | 1700.9211 | 656.5 | 10.1 | 84.4969 | 1558.2 | 468.4211 | 142.7211 | 0 |  | 7.5984 | 656.5
14 | 0 | 130 | 130 | 0 | 0 | 4 | 130 | 36 | 0 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 14 | 85 | 9200 | 41.3 | 2983.5 | 0 | 1313 | 1313 | 10.1 | 84.4969 | 1219.1 | 0 | 93.9 | 0 |  | 15.1968 | 1313
15 | 255 | 0 | 255 | 0 | 0 | 4 | 255 | 55 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 15 | 85.4 | 10160 | 41.3 | 2983.5 | 960 | 4608.7984 | 2575.5 | 10.1 | 83.7181 | 4518.7 | 1073.2984 | 90.0984 | 0 |  | 29.809 | 2575.5
16 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 36 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 16 | 83 | 4400 | 41.32 | 3006.9 | -5760 | 5526.7872 | 707 | 10.1 | 88.6187 | 5436 | 10579.7872 | 150.7872 | 60 |  | 8.1829 | 707
17 | 285 | 0 | 285 | 0 | 0 | 4 | 285 | 55 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.7 | 8480 | 41.68 | 3428.1 | 4080 | 6987 | 2907 | 10.2 | 84.2563 | 6967.25 | 0 | 79.75 | 60 |  | 33.6458 | 2907
18 | 0 | 125 | 125 | 0 | 0 | 3 | 125 | 55 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 83.85 | 6440 | 41.76 | 3521.7 | -2040 | 1296.9681 | 1262.5 | 10.1 | 86.8188 | 1320.6 | 2074.4681 | 36.3681 | 60 |  | 14.6123 | 1262.5
19 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 35 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 19 | 83.9 | 6560 | 41.65 | 3393 | 120 | 3524.9167 | 707 | 10.1 | 86.7152 | 3379.9 | 2697.9167 | 205.0167 | 60 |  | 8.1829 | 707
20 | 0 | 70 | 70 | 0 | 0 | 3 | 70 | 35 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 20 | 84.1 | 7040 | 41.72 | 3474.9 | 480 | 1187 | 707 | 10.1 | 86.3032 | 1173 | 0 | 74 | 60 |  | 8.1829 | 707
21 | 70 | 0 | 70 | 0 | 0 | 4 | 70 | 55 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 21 | 83.65 | 5960 | 41.79 | 3556.8 | -1080 | 2006.6791 | 707 | 10.1 | 87.2357 | 2044.5 | 2379.6791 | 22.1791 | 60 |  | 8.1829 | 707
22 | 0 | 90 | 90 | 0 | 0 | 4 | 90 | 55 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 22 | 84.45 | 7880 | 41.05 | 2691 | 1920 | 2829 | 909 | 10.1 | 85.5917 | 2817.8 | 0 | 71.2 | 60 |  | 10.5208 | 909
23 | 195 | 0 | 195 | 0 | 0 | 3 | 195 | 55 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.15 | 7160 | 41.05 | 2691 | -720 | 1808.6398 | 1969.5 | 10.1 | 86.2009 | 1792 | 559.1398 | 76.6398 | 60 |  | 22.7951 | 1969.5
24 | 0 | 80 | 80 | 0 | 0 | 5 | 80 | 40 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 24 | 85.35 | 10040 | 41 | 2632.5 | 2880 | 5579.1917 | 808 | 10.1 | 83.8147 | 5285.2 | 1891.1917 | 293.9917 | 0 |  | 9.3519 | 808
25 | 65 | 0 | 65 | 0 | 0 | 4 | 65 | 36 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 25 | 83.6 | 5840 | 40.99 | 2620.8 | -4200 | 6107.0376 | 656.5 | 10.1 | 87.3405 | 5978 | 9650.5376 | 189.0376 | 60 |  | 7.5984 | 656.5
26 | 0 | 65 | 65 | 0 | 0 | 4 | 65 | 36 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 26 | 85 | 9200 | 40.88 | 2492.1 | 3360 | 8084.9211 | 656.5 | 10.1 | 84.4969 | 7935.1 | 4068.4211 | 209.8211 | 60 |  | 7.5984 | 656.5
27 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 55 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 27 | 84.15 | 7160 | 41.01 | 2644.2 | -2040 | 5997.9233 | 757.5 | 10.1 | 86.2009 | 5929 | 7280.4233 | 128.9233 | 60 |  | 8.7674 | 757.5
28 | 0 | 70 | 70 | 0 | 0 | 4 | 70 | 55 | 0 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 28 | 84.4 | 7760 | 41.05 | 2691 | 600 | 1307 | 707 | 10.1 | 85.6926 | 1253 | 0 | 114 | 60 |  | 8.1829 | 707
29 | 0 | 145 | 145 | 0 | 0 | 3 | 145 | 55 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 29 | 84.75 | 8600 | 41.65 | 3393 | 840 | 3879.6295 | 1464.5 | 10.1 | 84.991 | 3700 | 1575.1295 | 179.6295 | 0 |  | 16.9502 | 1464.5
30 | 0 | 85 | 85 | 0 | 0 | 4 | 85 | 40 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 30 | 85.4 | 10160 | 41.49 | 3205.8 | 1560 | 2410 | 850 | 10 | 84.5553 | 2249.9 | 0 | 160.1 | 0 |  | 9.838 | 850
31 | 75 | 0 | 75 | 0 | 0 | 3 | 75 | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 31 | 83.35 | 5240 | 41.48 | 3194.1 | -4920 | 3713.8441 | 757.5 | 10.1 | 87.8686 | 3712.2 | 7876.3441 | 61.6441 | 60 |  | 8.7674 | 757.5
| 1805 | 1595 | 3400 | 0 | 0 | 113 | 3287 | 70 | 40.7 | 38.7 | 0 | 8.25 | 0 | 2.2 | 0 | 8.25 | 0 | 2.2 | 19 | 22 |  |  | 84.4423 | 7861.4194 | 41.4461 | 3154.471 | -2280 | 102209.6116 | 34379 | 10.1115 | 85.5102 | 99979.25 | 70110.6116 | 3680.3616 | 1450 |  | 12.8356 | 34379