## Sheet1
Public Power Corporation
Aliakmonas River Complex | [17 empty] | Month |  |  |  | Aliakmonas River Complex | [11 empty] | Month
HPP Asomata | [10 empty] | Monthly Production Report | [6 empty] | Peak |  | MW |  | HPP Asomata | [6 empty] | Monthly Hydrological Report
Date |  | Production |  |  | Auxiliaries Consumptions |  | Net Production | Peak | Hours of Operation |  |  |  |  | Downtime |  |  |  |  | Number of Starts |  |  | Date | Asomata Reservoir |  | Regulating lake |  | Water saved in lake | Catchment water inflow | Production Water Consumption | Specific Consumption | Turbine Efficiency | HPP Sfikia Water |  | Lake natural inflow |  |  | Regulating lake
|  | MWh |  |  | MWh | [17 empty] | Water Level | Water Comtent | Water Level | Water Content | [5 empty] | Production | Pumped upstream |  | Losses
[11 empty] | Unit I |  |  |  |  | Unit II | [19 empty] | B | Water flow | Total Water
| Unit | Unit | HPP | Unit | Unit | Grid |  |  | Unit | Unit | Maintenance |  | Failure |  | Maintenance |  | Failure |  | Unit |  | Comments |  | m | m3 x 1000 | m | m3 x 1000 |  |  | m3 x 1000 | q=ε/energyproduced | nt=36697/(q*H) | m3 x 1000 | m3 x 1000 | m3 x 1000 | m3 x 1000 |  | m3/s | m3 x 1000
| I | II |  | I | II |  | MWh | MW | I | II | Plant | Outside | Plant | Outside | Plant | Outside | Plant | Outside | I | II |  |  | 85 | 9.2 | 41.71 | 3.197 | α=δ(level) | β=γ+α+ε | γ |  |  | δ | ε | στ=β-δ | ζ=στ-κ+α |  | ζ | η=ζχ86,400
1 | 480 | 0 | 480 | 0 | 0 | 4 | 480 | 54 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 1 | 85.1 | 9440 | 41.92 | 3708.9 | 600 | 6126.7565 | 4848 | 10.1 | 84.3008 | 5749.8 | 678.7565 | 376.9565 | 0 |  | 56.1111 | 4848
2 | 0 | 585 | 585 | 0 | 0 | 3 | 585 | 55 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 84.75 | 8600 | 41.92 | 3708.9 | -840 | 5068.5 | 5908.5 | 10.1 | 84.991 | 5095.4 | 0 | 33.1 | 60 |  | 68.3854 | 5908.5
3 | 490 | 75 | 565 | 0 | 0 | 3 | 565 | 70 | 10.1 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 |  | 3 | 84.85 | 8840 | 41.67 | 3416.4 | 240 | 5946.5 | 5706.5 | 10.1 | 84.7927 | 5565.6 | 0 | 380.9 | 0 |  | 66.0475 | 5706.5
4 | 0 | 575 | 575 | 0 | 0 | 4 | 575 | 55 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4 | 84.65 | 8360 | 42.1 | 3919.5 | -480 | 5327.5 | 5807.5 | 10.1 | 85.1903 | 5234.1 | 0 | 153.4 | 60 |  | 67.2164 | 5807.5
5 | 510 | 0 | 510 | 0 | 0 | 3 | 510 | 50 | 10.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 5 | 84.7 | 8480 | 42.1 | 3919.5 | 120 | 5271 | 5151 | 10.1 | 85.0905 | 5115 | 0 | 156 | 0 |  | 59.6181 | 5151
6 | 0 | 675 | 675 | 0 | 0 | 4 | 675 | 54 | 0 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 6 | 84.6 | 8240 | 41.85 | 3627 | -240 | 8659.5513 | 6817.5 | 10.1 | 85.2903 | 8369.4 | 2082.0513 | 290.1513 | 0 |  | 78.9062 | 6817.5
7 | 520 | 0 | 520 | 0 | 0 | 4 | 520 | 54 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 7 | 83.5 | 5600 | 42.07 | 3884.4 | -2640 | 5460.3146 | 5252 | 10.1 | 87.551 | 5188.4 | 2848.3146 | 331.9146 | 60 |  | 60.787 | 5252
8 | 30 | 550 | 580 | 0 | 0 | 3 | 580 | 54 | 0.5 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 8 | 84.2 | 7280 | 42.02 | 3825.9 | 1680 | 7538 | 5858 | 10.1 | 86.0987 | 7540.75 | 0 | 57.25 | 60 |  | 67.8009 | 5858
9 | 535 | 0 | 535 | 0 | 0 | 3 | 535 | 54 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 84.1 | 7040 | 42.11 | 3931.2 | -240 | 5828.8255 | 5478.4 | 10.24 | 85.1233 | 5621 | 590.4255 | 207.8255 | 0 |  | 63.4074 | 5478.4
10 | 0 | 495 | 495 | 0 | 0 | 4 | 495 | 50 | 0 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 84.75 | 8600 | 42.02 | 3825.9 | 1560 | 6717.9 | 5157.9 | 10.42 | 82.3809 | 6351 | 0 | 366.9 | 0 |  | 59.6979 | 5157.9
11 | 525 | 0 | 525 | 0 | 0 | 3 | 525 | 50 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 11 | 84.87 | 8888 | 42 | 3802.5 | 288 | 5590.5 | 5302.5 | 10.1 | 84.7531 | 5358.15 | 0 | 232.35 | 0 |  | 61.3715 | 5302.5
12 | 0 | 520 | 520 | 0 | 0 | 3 | 520 | 54 | 0 | 10.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 12 | 84.8 | 8720 | 41.88 | 3662.1 | -168 | 5136 | 5304 | 10.2 | 84.0595 | 4909.8 | 0 | 226.2 | 0 |  | 61.3889 | 5304
13 | 555 | 0 | 555 | 0 | 0 | 4 | 555 | 55 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 13 | 85.05 | 9320 | 41.98 | 3779.1 | 600 | 6205.5 | 5605.5 | 10.1 | 84.3988 | 6000.6 | 0 | 204.9 | 0 |  | 64.8785 | 5605.5
14 | 0 | 540 | 540 | 0 | 0 | 3 | 540 | 50 | 0 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 14 | 85.3 | 9920 | 41.95 | 3744 | 600 | 6000 | 5400 | 10 | 84.7506 | 5721.1 | 0 | 278.9 | 0 |  | 62.5 | 5400
15 | 545 | 170 | 715 | 0 | 0 | 4 | 715 | 100 | 10.9 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 |  | 15 | 84.6 | 8240 | 41.81 | 3580.2 | -1680 | 5541.5 | 7221.5 | 10.1 | 85.2903 | 5569.9 | 0 | 11.6 | 40 |  | 83.5822 | 7221.5
16 | 0 | 590 | 590 | 0 | 0 | 3 | 590 | 55 | 0 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 16 | 84.5 | 8000 | 42 | 3802.5 | -240 | 5984.5 | 6224.5 | 10.55 | 81.8444 | 5884.45 | 0 | 100.05 | 0 |  | 72.0428 | 6224.5
17 | 560 | 0 | 560 | 0 | 0 | 4 | 560 | 50 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 17 | 84.65 | 8360 | 42.05 | 3861 | 360 | 6016 | 5656 | 10.1 | 85.1903 | 6041.95 | 0 | 34.05 | 60 |  | 65.463 | 5656
18 | 0 | 630 | 630 | 0 | 0 | 3 | 630 | 55 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 18 | 84.6 | 8240 | 41.75 | 3510 | -120 | 6243 | 6363 | 10.1 | 85.2903 | 5959.5 | 0 | 283.5 | 0 |  | 73.6458 | 6363
19 | 570 | 0 | 570 | 0 | 0 | 4 | 570 | 55 | 11.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 19 | 83.9 | 6560 | 41.82 | 3591.9 | -1680 | 6034.4468 | 5757 | 10.1 | 86.7152 | 5803.5 | 1957.4468 | 230.9468 | 0 |  | 66.6319 | 5757
20 | 0 | 600 | 600 | 0 | 0 | 3 | 600 | 55 | 0 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 20 | 83.9 | 6560 | 41.9 | 3685.5 | 0 | 6060 | 6060 | 10.1 | 86.7152 | 6027 | 0 | 63 | 30 |  | 70.1389 | 6060
21 | 570 | 0 | 570 | 0 | 0 | 4 | 570 | 55 | 11.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 21 | 84.15 | 7160 | 42.04 | 3849.3 | 600 | 6357 | 5757 | 10.1 | 86.2009 | 6276.4 | 0 | 80.6 | 0 |  | 66.6319 | 5757
22 | 0 | 610 | 610 | 0 | 0 | 3 | 610 | 55 | 0 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 22 | 84.15 | 7160 | 42.01 | 3814.2 | 0 | 6161 | 6161 | 10.1 | 86.2009 | 6127.55 | 0 | 93.45 | 60 |  | 71.3079 | 6161
23 | 630 | 0 | 630 | 0 | 0 | 4 | 630 | 50 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 23 | 84.3 | 7520 | 42.1 | 3919.5 | 360 | 6723 | 6363 | 10.1 | 85.8952 | 6504.3 | 0 | 218.7 | 0 |  | 73.6458 | 6363
24 | 0 | 595 | 595 | 0 | 0 | 3 | 595 | 55 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 24 | 84.58 | 8192 | 41.97 | 3767.4 | 672 | 6681.5 | 6009.5 | 10.1 | 85.3304 | 6482.4 | 0 | 199.1 | 0 |  | 69.5544 | 6009.5
25 | 610 | 0 | 610 | 0 | 0 | 4 | 610 | 50 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 25 | 84.75 | 8600 | 42.08 | 3896.1 | 408 | 6569 | 6161 | 10.1 | 84.991 | 6349.2 | 0 | 219.8 | 0 |  | 71.3079 | 6161
26 | 0 | 550 | 550 | 0 | 0 | 3 | 550 | 50 | 0 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 26 | 84.95 | 9080 | 41.97 | 3767.4 | 480 | 5980 | 5500 | 10 | 85.4412 | 5805 | 0 | 175 | 0 |  | 63.6574 | 5500
27 | 545 | 0 | 545 | 0 | 0 | 4 | 545 | 55 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 27 | 85.1 | 9440 | 41.57 | 3299.4 | 360 | 5810 | 5450 | 10 | 85.1439 | 5600.7 | 0 | 209.3 | 0 |  | 63.0787 | 5450
28 | 0 | 635 | 635 | 0 | 0 | 4 | 635 | 55 | 0 | 12.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 28 | 85 | 9200 | 42.1 | 3919.5 | -240 | 6046.5 | 6286.5 | 9.9 | 86.2039 | 5723.2 | 0 | 323.3 | 0 |  | 72.7604 | 6286.5
29 | 645 | 0 | 645 | 0 | 0 | 3 | 645 | 55 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  | 29 | 85.1 | 9440 | 41.84 | 3615.3 | 240 | 6754.5 | 6514.5 | 10.1 | 84.3008 | 6663.8 | 0 | 90.7 | 0 |  | 75.3993 | 6514.5
30 | 120 | 670 | 790 | 0 | 0 | 3 | 790 | 70 | 3.1 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 30 | 84.35 | 7640 | 42.1 | 3919.5 | -1800 | 6179 | 7979 | 10.1 | 85.7938 | 5914.3 | 0 | 324.7 | 60 |  | 92.3495 | 7979
| 8440 | 9065 | 17505 | 0 | 0 | 104 | 17401 | 100 | 174.2 | 183.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 28 |  |  | 84.5933 | 8224 | 41.9567 | 3751.8 | -1200 | 184017.7947 | 177060.8 | 10.1149 | 85.1782 | 178553.25 | 8156.9947 | 5954.5447 | 490 |  | 68.3105 | 177060.8